## Bryansk
[9 empty] | table 1 | [12 empty] | table 2
No. | Name of supply center, voltage class | Current deficit | [8 empty] | Note | No. | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Supply Center, MVA |  |  |  |  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load of Supply Center, MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Supply Center, MVA
|  |  | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | MVA | Min | [11 empty] | MVA | Min
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | SS 110/10 kV Lopandino | 6.3 | 0.715 | 6.3 | 1 day and night | 6.3 | 0 | 6.3 | 5.585 | 5.585 | available | 1 | SS 110/10 kV Lopandino | 6.3 | 0.0075 | 0.7225 | 6.3 | 1 day and night | 6.3 | 0 | 6.3 | 5.5775 | 5.5775 | available
2 | SS 110/35/10 kV Nerussa | 16 | 4.21 | 16 | 1 day and night | 16 | 0 | 16 | 11.79 | 11.79 | available | 2 | SS 110/35/10 kV Nerussa | 16 | 0.0508 | 4.2608 | 16 | 1 day and night | 16 | 0 | 16 | 11.7392 | 11.7392 | available
| Nom. capacity MV, MVA | 16 | 2.607 | 16 | 1 day and night | 16 | 0 | 16 | 13.393 |  |  |  | Nom. capacity MV, MVA | 16 |  | 2.607 | 16 | 1 day and night | 16 | 0 | 16 | 13.393
| Nom. capacity LV, MVA | 16 | 1.603 | 16 | 1 day and night | 16 | 0 | 16 | 14.397 |  |  |  | Nom. capacity LV, MVA | 16 | 0.0508 | 1.6538 | 16 | 1 day and night | 16 | 0 | 16 | 14.3462
3 | SS 110/6 kV Svenskaya | 6.3 | 1.217 | 6.3 | 1 day and night | 6.3 | 0 | 6.3 | 5.083 | 5.083 | available | 3 | SS 110/6 kV Svenskaya | 6.3 | 0.22538 | 1.4424 | 6.3 | 1 day and night | 6.3 | 0 | 6.3 | 4.8576 | 4.8576 | available
4 | SS 110/10 kV Khmelevskaya | 6.3 | 0.345 | 6.3 | 1 day and night | 6.3 | 0 | 6.3 | 5.955 | 5.955 | available | 4 | SS 110/10 kV Khmelevskaya | 6.3 | 2.9429 | 3.2879 | 6.3 | 1 day and night | 6.3 | 0 | 6.3 | 3.0121 | 3.0121 | available
5 | SS 110/6 kV Energoremont | 10 | 7.042 | 4.3 | 1 day and night | 4.3 | 0 | 4.3 | -2.742 | -2.742 | unavailable | 5 | SS 110/6 kV Energoremont | 10 | 1.7354 | 8.7774 | 4.3 | 1 day and night | 4.3 | 0 | 4.3 | -4.4774 | -4.4774 | unavailable
6 | SS 110/6 kV Naytopovichi 8NA | 10 | 0.529 | 10 | 1 day and night | 10 | 0 | 10 | 9.471 | 9.471 | available | 6 | SS 110/6 kV Naytopovichi 8NA | 10 | 0.68313 | 1.2121 | 10 | 1 day and night | 10 | 0 | 10 | 8.7879 | 8.7879 | available
7 | SS 110/10 kV Glybochka | 2.5 | 0.233 | 2.5 | 1 day and night | 2.5 | 0 | 2.5 | 2.267 | 2.267 | available | 7 | SS 110/10 kV Glybochka | 2.5 | 0.3515 | 0.5845 | 2.5 | 1 day and night | 2.5 | 0 | 2.5 | 1.9155 | 1.9155 | available
8 | SS 110/10 kV Desyatukha | 6.3 | 1.001 | 6.3 | 1 day and night | 6.3 | 0 | 6.3 | 5.299 | 5.299 | available | 8 | SS 110/10 kV Desyatukha | 6.3 | 0.028258 | 1.0293 | 6.3 | 1 day and night | 6.3 | 0 | 6.3 | 5.2707 | 5.2707 | available
9 | SS 110/35/10 kV Ivaytenki | 6.3 | 0.999 | 6.3 | 1 day and night | 6.3 | 0 | 6.3 | 5.301 | 5.301 | available | 9 | SS 110/35/10 kV Ivaytenki | 6.3 | 0.28374 | 1.2827 | 6.3 | 1 day and night | 6.3 | 0 | 6.3 | 5.0173 | 5.0173 | available
| Nom. capacity MV, MVA | 6.3 | 0.212 | 6.3 | 1 day and night | 6.3 | 0 | 6.3 | 6.088 |  |  |  | Nom. capacity MV, MVA | 6.3 |  | 0.212 | 6.3 | 1 day and night | 6.3 | 0 | 6.3 | 6.088
| Nom. capacity LV, MVA | 6.3 | 0.787 | 6.3 | 1 day and night | 6.3 | 0 | 6.3 | 5.513 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.28374 | 1.0707 | 6.3 | 1 day and night | 6.3 | 0 | 6.3 | 5.2293
10 | SS 110/35/10 kV Lugovaya | 16 | 6.056 | 16 | 1 day and night | 16 | 0 | 16 | 9.944 | 9.944 | available | 10 | SS 110/35/10 kV Lugovaya | 16 | 0.0718 | 6.1278 | 16 | 1 day and night | 16 | 0 | 16 | 9.8722 | 9.8722 | available
| Nom. capacity MV, MVA | 16 | 5.227 | 16 | 1 day and night | 16 | 0 | 16 | 10.773 |  |  |  | Nom. capacity MV, MVA | 16 |  | 5.227 | 16 | 1 day and night | 16 | 0 | 16 | 10.773
| Nom. capacity LV, MVA | 16 | 0.829 | 16 | 1 day and night | 16 | 0 | 16 | 15.171 |  |  |  | Nom. capacity LV, MVA | 16 | 0.0718 | 0.9008 | 16 | 1 day and night | 16 | 0 | 16 | 15.0992
11 | SS 110/35/10 kV Plyuskovo | 6.3 | 1.729 | 6.3 | 1 day and night | 6.3 | 0 | 6.3 | 4.571 | 4.571 | available | 11 | SS 110/35/10 kV Plyuskovo | 6.3 | 1.4138 | 3.1428 | 6.3 | 1 day and night | 6.3 | 0 | 6.3 | 3.1572 | 3.1572 | available
| Nom. capacity MV, MVA | 6.3 | 0.822 | 6.3 | 1 day and night | 6.3 | 0 | 6.3 | 5.478 |  |  |  | Nom. capacity MV, MVA | 6.3 |  | 0.822 | 6.3 | 1 day and night | 6.3 | 0 | 6.3 | 5.478
| Nom. capacity LV, MVA | 6.3 | 0.907 | 6.3 | 1 day and night | 6.3 | 0 | 6.3 | 5.393 |  |  |  | Nom. capacity LV, MVA | 6.3 | 1.4138 | 2.3208 | 6.3 | 1 day and night | 6.3 | 0 | 6.3 | 3.9792
12 | SS 35/10 kV Aleshinskaya | 2.5 | 0.402 | 2.5 | 1 day and night | 2.5 | 0 | 2.5 | 2.098 | 2.098 | available | 12 | SS 35/10 kV Aleshinskaya | 2.5 | 0.0574 | 0.4594 | 2.5 | 1 day and night | 2.5 | 0 | 2.5 | 2.0406 | 2.0406 | available
13 | SS 35/10 kV Altukhovskaya | 1.6 | 0.4 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 1.2 | 1.2 | available | 13 | SS 35/10 kV Altukhovskaya | 1.6 | 0 | 0.4 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 1.2 | 1.2 | available
14 | SS 35/10 kV Domashovo | 2.5 | 0.514 | 2.5 | 1 day and night | 2.5 | 0 | 2.5 | 1.986 | 1.986 | available | 14 | SS 35/10 kV Domashovo | 2.5 | 0.896 | 1.41 | 2.5 | 1 day and night | 2.5 | 0 | 2.5 | 1.09 | 1.09 | available
15 | SS 35/6 kV Dronovskaya | 2.5 | 0.586 | 2.5 | 1 day and night | 2.5 | 0 | 2.5 | 1.914 | 1.914 | available | 15 | SS 35/6 kV Dronovskaya | 2.5 | 0.054 | 0.64 | 2.5 | 1 day and night | 2.5 | 0 | 2.5 | 1.86 | 1.86 | available
16 | SS 35/10 kV Kokorevskaya | 4 | 0.85 | 4 | 1 day and night | 4 | 0 | 4 | 3.15 | 3.15 | available | 16 | SS 35/10 kV Kokorevskaya | 4 | 0.003 | 0.853 | 4 | 1 day and night | 4 | 0 | 4 | 3.147 | 3.147 | available
17 | SS 35/6 kV Malopolpinskaya | 4 | 0.72 | 4 | 1 day and night | 4 | 0 | 4 | 3.28 | 3.28 | available | 17 | SS 35/6 kV Malopolpinskaya | 4 | 0.12648 | 0.84648 | 4 | 1 day and night | 4 | 0 | 4 | 3.1535 | 3.1535 | available
18 | SS 35/10 kV Morachevskaya | 1.6 | 0.527 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 1.073 | 1.073 | available | 18 | SS 35/10 kV Morachevskaya | 1.6 | 0.6834 | 1.2104 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 0.3896 | 0.3896 | available
19 | SS 35/10 kV Saltanovskaya | 2.5 | 0.452 | 2.5 | 1 day and night | 2.5 | 0 | 2.5 | 2.048 | 2.048 | available | 19 | SS 35/10 kV Saltanovskaya | 2.5 | 0.0385 | 0.4905 | 2.5 | 1 day and night | 2.5 | 0 | 2.5 | 2.0095 | 2.0095 | available
20 | SS 35/10 kV Svetovo | 2.5 | 0.343 | 2.5 | 1 day and night | 2.5 | 0 | 2.5 | 2.157 | 2.157 | available | 20 | SS 35/10 kV Svetovo | 2.5 | 0.0163 | 0.3593 | 2.5 | 1 day and night | 2.5 | 0 | 2.5 | 2.1407 | 2.1407 | available
21 | SS 35/10 kV Seshcha | 2.5 | 0.753 | 2.5 | 1 day and night | 2.5 | 0 | 2.5 | 1.747 | 1.747 | available | 21 | SS 35/10 kV Seshcha | 2.5 | 0.01 | 0.763 | 2.5 | 1 day and night | 2.5 | 0 | 2.5 | 1.737 | 1.737 | available
22 | SS 35/10 kV Sovkhoznaya | 4 | 0.379 | 4 | 1 day and night | 4 | 0 | 4 | 3.621 | 3.621 | available | 22 | SS 35/10 kV Sovkhoznaya | 4 | 0.0039 | 0.3829 | 4 | 1 day and night | 4 | 0 | 4 | 3.6171 | 3.6171 | available
23 | SS 35/10 kV Strachevskaya | 2.5 | 0.496 | 2.5 | 1 day and night | 2.5 | 0 | 2.5 | 2.004 | 2.004 | available | 23 | SS 35/10 kV Strachevskaya | 2.5 | 0.1497 | 0.6457 | 2.5 | 1 day and night | 2.5 | 0 | 2.5 | 1.8543 | 1.8543 | available
24 | SS 35/10 kV Strashevichi | 4 | 1.36 | 4 | 1 day and night | 4 | 0 | 4 | 2.64 | 2.64 | available | 24 | SS 35/10 kV Strashevichi | 4 | 2.1409 | 3.5009 | 4 | 1 day and night | 4 | 0 | 4 | 0.4991 | 0.4991 | available
25 | SS 35/10 kV Usozhskaya | 2.5 | 0.613 | 2.5 | 1 day and night | 2.5 | 0 | 2.5 | 1.887 | 1.887 | available | 25 | SS 35/10 kV Usozhskaya | 2.5 | 0.054 | 0.667 | 2.5 | 1 day and night | 2.5 | 0 | 2.5 | 1.833 | 1.833 | available
26 | SS 35/10 kV Kharinovskaya | 1 | 0.08 | 1 | 1 day and night | 1 | 0 | 1 | 0.92 | 0.92 | available | 26 | SS 35/10 kV Kharinovskaya | 1 | 0 | 0.08 | 1 | 1 day and night | 1 | 0 | 1 | 0.92 | 0.92 | available
27 | SS 35/10 kV Kharitonovskaya | 4 | 0.748 | 4 | 1 day and night | 4 | 0 | 4 | 3.252 | 3.252 | available | 27 | SS 35/10 kV Kharitonovskaya | 4 | 0.1295 | 0.8775 | 4 | 1 day and night | 4 | 0 | 4 | 3.1225 | 3.1225 | available
28 | SS 35/10 kV Divovka | 2.5 | 0.63 | 2.5 | 1 day and night | 2.5 | 0 | 2.5 | 1.87 | 1.87 | available | 28 | SS 35/10 kV Divovka | 2.5 | 0.2436 | 0.8736 | 2.5 | 1 day and night | 2.5 | 0 | 2.5 | 1.6264 | 1.6264 | available
29 | SS 35/10 kV Molodkovo | 1.6 | 0.225 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 1.375 | 1.375 | available | 29 | SS 35/10 kV Molodkovo | 1.6 | 0.0011 | 0.2261 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 1.3739 | 1.3739 | available
30 | SS 35/10 kV Papsuevskaya | 2.5 | 0.322 | 2.5 | 1 day and night | 2.5 | 0 | 2.5 | 2.178 | 2.178 | available | 30 | SS 35/10 kV Papsuevskaya | 2.5 | 0.0132 | 0.3352 | 2.5 | 1 day and night | 2.5 | 0 | 2.5 | 2.1648 | 2.1648 | available
31 | SS 35/10 kV Radutinskaya | 1.6 | 0.537 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 1.063 | 1.063 | available | 31 | SS 35/10 kV Radutinskaya | 1.6 | 0.0672 | 0.6042 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 0.9958 | 0.9958 | available
32 | SS 35/6 kV Ushchepye | 1.6 | 0.294 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 1.306 | 1.306 | available | 32 | SS 35/6 kV Ushchepye | 1.6 | 0.0118 | 0.3058 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 1.2942 | 1.2942 | available
32 | SS 35/10 kV Ushchepye | 1.6 | 0.049 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 1.551 | 1.551 | available | 32 | SS 35/10 kV Ushchepye | 1.6 | 0 | 0.049 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 1.551 | 1.551 | available
33 | SS 35/10 kV Yakovskaya | 2.5 | 0.547 | 2.5 | 1 day and night | 2.5 | 0 | 2.5 | 1.953 | 1.953 | available | 33 | SS 35/10 kV Yakovskaya | 2.5 | 0.13804 | 0.68504 | 2.5 | 1 day and night | 2.5 | 0 | 2.5 | 1.815 | 1.815 | available
34 | SS 110/35/6 kV Aksinino | 40+40 | 18.677 | 0 | 0 | 18.677 | 0 | 42 | 23.323 | 23.323 | available | 34 | SS 110/35/6 kV Aksinino | 40+40 | 0.0174 | 18.6944 | 0 | 0 | 18.6944 | 0 | 42 | 23.3056 | 23.3056 | available
| Nom. capacity MV, MVA | 40+40 | 2.57 | 0 | 0 | 2.57 | 0 | 42 | 39.43 |  |  |  | Nom. capacity MV, MVA | 40+40 |  | 2.57 | 0 | 0 | 2.57 | 0 | 42 | 39.43
| Nom. capacity LV, MVA | 40+40 | 16.107 | 0 | 0 | 16.107 | 0 | 42 | 25.893 |  |  |  | Nom. capacity LV, MVA | 40+40 | 0.0174 | 16.1244 | 0 | 0 | 16.1244 | 0 | 42 | 25.8756
35 | SS 110/10 kV Airport | 6,3+6,3 | 0.715 | 0 | 0 | 0.715 | 0 | 6.615 | 5.9 | 5.9 | available | 35 | SS 110/10 kV Airport | 6,3+6,3 | 0.1044 | 0.8194 | 0 | 0 | 0.8194 | 0 | 6.615 | 5.7956 | 5.7956 | available
36 | SS 110/6 kV Bezhitskaya | 25+40 | 27.183 | 0 | 0 | 27.183 | 0 | 26.25 | -0.933 | -0.933 | unavailable | 36 | SS 110/6 kV Bezhitskaya | 25+40 | 4.9837 | 32.1667 | 0 | 0 | 32.1667 | 0 | 26.25 | -5.9167 | -5.9167 | unavailable
37 | SS 110/6 kV Water intake | 6,3+6,3 | 3.6 | 0 | 0 | 3.6 | 0 | 6.615 | 3.015 | 3.015 | available | 37 | SS 110/6 kV Water intake | 6,3+6,3 | 1.8979 | 5.4979 | 0 | 0 | 5.4979 | 0 | 6.615 | 1.1171 | 1.1171 | available
38 | SS 110/6 kV Gorodishchenskaya | 16+16 | 20.67 | 1.5 | 12 hours | 19.17 | 0 | 16.8 | -2.37 | -2.37 | unavailable | 38 | SS 110/6 kV Gorodishchenskaya | 16+16 | 8.7721 | 29.4421 | 1.5 | 12 hours | 27.9421 | 0 | 16.8 | -11.1421 | -11.1421 | unavailable
39 | SS 110/10 kV Dobrunskaya | 6,3+4 | 4.405 | 0 | 0 | 4.405 | 0 | 4.2 | -0.205 | -0.205 | unavailable | 39 | SS 110/10 kV Dobrunskaya | 6,3+4 | 2.4721 | 6.8771 | 0 | 0 | 6.8771 | 0 | 4.2 | -2.6771 | -2.6771 | unavailable
40 | SS 110/35/6 kV Dormashevskaya | 40+63 | 44.456 | 0 | 0 | 44.456 | 0 | 42 | -2.456 | -2.456 | unavailable | 40 | SS 110/35/6 kV Dormashevskaya | 40+63 | 12.2011 | 56.6571 | 0 | 0 | 56.6571 | 0 | 42 | -14.6571 | -14.6571 | unavailable
| Nom. capacity MV, MVA | 40+63 | 24.363 | 0 | 0 | 24.363 | 0 | 42 | 17.637 |  |  |  | Nom. capacity MV, MVA | 40+63 |  | 24.363 | 0 | 0 | 24.363 | 0 | 42 | 17.637
| Nom. capacity LV, MVA | 40+63 | 20.093 | 0 | 0 | 20.093 | 0 | 42 | 21.907 |  |  |  | Nom. capacity LV, MVA | 40+63 | 12.2011 | 32.2941 | 0 | 0 | 32.2941 | 0 | 42 | 9.7059
41 | SS 110/35/10 kV Dubrovskaya | 16+16 | 9.892 | 0 | 0 | 9.892 | 0 | 16.8 | 6.908 | 6.908 | available | 41 | SS 110/35/10 kV Dubrovskaya | 16+16 | 0.1038 | 9.9958 | 0 | 0 | 9.9958 | 0 | 16.8 | 6.8042 | 6.8042 | available
| Nom. capacity MV, MVA | 16+16 | 6.161 | 0 | 0 | 6.161 | 0 | 16.8 | 10.639 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 6.161 | 0 | 0 | 6.161 | 0 | 16.8 | 10.639
| Nom. capacity LV, MVA | 16+16 | 3.731 | 0 | 0 | 3.731 | 0 | 16.8 | 13.069 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.1038 | 3.8348 | 0 | 0 | 3.8348 | 0 | 16.8 | 12.9652
42 | SS 110/35/6 kV Dyadkovkskaya | 25+25 | 28.415 | 0 | 0 | 28.415 | 0 | 26.25 | -2.165 | -2.165 | unavailable | 42 | SS 110/35/6 kV Dyadkovkskaya | 25+25 | 0.62958 | 29.0446 | 0 | 0 | 29.0446 | 0 | 26.25 | -2.7946 | -2.7946 | unavailable
| Nom. capacity MV, MVA | 25+25 | 7.92 | 0 | 0 | 7.92 | 0 | 26.25 | 18.33 |  |  |  | Nom. capacity MV, MVA | 25+25 |  | 7.92 | 0 | 0 | 7.92 | 0 | 26.25 | 18.33
| Nom. capacity LV, MVA | 25+25 | 20.495 | 0 | 0 | 20.495 | 0 | 26.25 | 5.755 |  |  |  | Nom. capacity LV, MVA | 25+25 | 0.62958 | 21.1246 | 0 | 0 | 21.1246 | 0 | 26.25 | 5.1254
43 | SS 110/35/10 kV Zhukovskaya | 16+25 | 14.693 | 5.2 | 6 hours | 9.493 | 0 | 16.8 | 7.307 | 7.307 | available | 43 | SS 110/35/10 kV Zhukovskaya | 16+25 | 0.30193 | 14.9949 | 5.2 | 6 hours | 9.7949 | 0 | 16.8 | 7.0051 | 7.0051 | available
| Nom. capacity MV, MVA | 16+25 | 6.789 | 5.2 | 6 hours | 1.589 | 0 | 16.8 | 10.011 |  |  |  | Nom. capacity MV, MVA | 16+25 |  | 6.789 | 5.2 | 6 hours | 1.589 | 0 | 16.8 | 10.011
| Nom. capacity LV, MVA | 16+25 | 7.904 | 0 | 0 | 7.904 | 0 | 16.8 | 8.896 |  |  |  | Nom. capacity LV, MVA | 16+25 | 0.30193 | 8.2059 | 0 | 0 | 8.2059 | 0 | 16.8 | 8.5941
44 | SS 110/6 kV Zarechnaya | 10+10 | 7.923 | 0 | 0 | 7.923 | 0 | 10.5 | 2.577 | 2.577 | available | 44 | SS 110/6 kV Zarechnaya | 10+10 | 1.721 | 9.644 | 0 | 0 | 9.644 | 0 | 10.5 | 0.856 | 0.856 | available
45 | SS 110/35/6 kV Ivotskaya | 25+25 | 8.434 | 2.68 | 6 hours | 5.754 | 0 | 26.25 | 20.496 | 20.496 | available | 45 | SS 110/35/6 kV Ivotskaya | 25+25 | 0 | 8.434 | 2.4 | 6 hours | 6.034 | 0 | 26.25 | 20.216 | 20.216 | available
| Nom. capacity MV, MVA | 25+25 | 5.229 | 2.68 | 6 hours | 2.549 | 0 | 26.25 | 21.021 |  |  |  | Nom. capacity MV, MVA | 25+25 |  | 5.229 | 2.4 | 6 hours | 2.829 | 0 | 26.25 | 21.021
| Nom. capacity LV, MVA | 25+25 | 3.205 | 0 | 0 | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. capacity LV, MVA | 25+25 | 0 | 3.205 | 0 | 0 | 0 | 0 | 26.25 | 26.25
46 | SS 110/6 kV Kamvolnaya | 25+25 | 16.253 | 0 | 0 | 16.253 | 0 | 26.25 | 9.997 | 9.997 | available | 46 | SS 110/6 kV Kamvolnaya | 25+25 | 6.0558 | 22.3088 | 0 | 0 | 22.3088 | 0 | 26.25 | 3.9412 | 3.9412 | available
47 | SS 110/6 kV Karachevskaya | 16+25 | 11.914 | 0 | 0 | 11.914 | 0 | 16.8 | 4.886 | 4.886 | available | 47 | SS 110/6 kV Karachevskaya | 16+25 | 1.0469 | 12.9609 | 0 | 0 | 12.9609 | 0 | 16.8 | 3.8391 | 3.8391 | available
48 | SS 110/6 kV Karachizhskaya | 10+10 | 13.931 | 0 | 0 | 13.931 | 0 | 10.5 | -3.431 | -3.431 | unavailable | 48 | SS 110/6 kV Karachizhskaya | 10+10 | 2.8926 | 16.8236 | 0 | 0 | 16.8236 | 0 | 10.5 | -6.3236 | -6.3236 | unavailable
49 | SS 110/35/10 kV Kletnyanskaya | 10+16 | 6.545 | 1.4 | 6 hours | 5.145 | 0 | 10.5 | 5.355 | 5.355 | available | 49 | SS 110/35/10 kV Kletnyanskaya | 10+16 | 0.75028 | 7.2953 | 1.4 | 6 hours | 5.8953 | 0 | 10.5 | 4.6047 | 4.6047 | available
| Nom. capacity MV, MVA | 10+16 | 2.149 | 1.4 | 6 hours | 0.749 | 0 | 10.5 | 8.351 |  |  |  | Nom. capacity MV, MVA | 10+16 |  | 2.149 | 1.4 | 6 hours | 0.749 | 0 | 10.5 | 8.351
| Nom. capacity LV, MVA | 10+16 | 4.396 | 0 | 0 | 4.396 | 0 | 10.5 | 6.104 |  |  |  | Nom. capacity LV, MVA | 10+16 | 0.75028 | 5.1463 | 0 | 0 | 5.1463 | 0 | 10.5 | 5.3537
50 | SS 110/35/10 kV Komarichi | 16+16 | 9.208 | 3.7 | 6 hours | 5.508 | 0 | 16.8 | 11.292 | 11.292 | available | 50 | SS 110/35/10 kV Komarichi | 16+16 | 0.2245 | 9.4325 | 3.7 | 6 hours | 5.7325 | 0 | 16.8 | 11.0675 | 11.0675 | available
| Nom. capacity MV, MVA | 16+16 | 4.72 | 3.7 | 6 hours | 1.02 | 0 | 16.8 | 12.08 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 4.72 | 3.7 | 6 hours | 1.02 | 0 | 16.8 | 12.08
| Nom. capacity LV, MVA | 16+16 | 4.488 | 0 | 0 | 4.488 | 0 | 16.8 | 12.312 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.2245 | 4.7125 | 0 | 0 | 4.7125 | 0 | 16.8 | 12.0875
51 | SS 110/10 kV Letoshniki | 6,3+2,5 | 0.815 | 0 | 0 | 0.815 | 0 | 2.625 | 1.81 | 1.81 | available | 51 | SS 110/10 kV Letoshniki | 6,3+2,5 | 0.2898 | 1.1048 | 0 | 0 | 1.1048 | 0 | 2.625 | 1.5202 | 1.5202 | available
52 | SS 110/6 kV Mamonovskaya | 16+16 | 14.723 | 0 | 0 | 14.723 | 0 | 16.8 | 2.077 | 2.077 | available | 52 | SS 110/6 kV Mamonovskaya | 16+16 | 0.9592 | 15.6822 | 0 | 0 | 15.6822 | 0 | 16.8 | 1.1178 | 1.1178 | available
53 | SS 110/35/10 kV Maritskaya | 10+16 | 6.54 | 4.5 | 6 hours | 2.04 | 0 | 10.5 | 8.46 | 4.72 | available | 53 | SS 110/35/10 kV Maritskaya | 10+16 | 2.8756 | 9.4156 | 4.5 | 6 hours | 4.9156 | 0 | 10.5 | 5.5844 | 4.72 | available
| Nom. capacity MV, MVA | 10+16 | 5.78 | 4.5 | 6 hours | 0 | 0 | 10.5 | 4.72 |  |  |  | Nom. capacity MV, MVA | 10+16 |  | 5.78 | 4.5 | 6 hours | 0 | 0 | 10.5 | 4.72
| Nom. capacity LV, MVA | 10+16 | 0.76 | 0 | 0 | 0.76 | 0 | 10.5 | 9.74 |  |  |  | Nom. capacity LV, MVA | 10+16 | 2.8756 | 3.6356 | 0 | 0 | 3.6356 | 0 | 10.5 | 6.8644
54 | SS 110/6 kV Michurinskaya | 10+10 | 3.612 | 0 | 0 | 3.612 | 0 | 10.5 | 6.888 | 6.888 | available | 54 | SS 110/6 kV Michurinskaya | 10+10 | 2.1211 | 5.7331 | 0 | 0 | 5.7331 | 0 | 10.5 | 4.7669 | 4.7669 | available
55 | SS 110/10 kV Molotinskaya | 6,3+6,3 | 0.368 | 0 | 0 | 0.368 | 0 | 6.615 | 6.247 | 6.247 | available | 55 | SS 110/10 kV Molotinskaya | 6,3+6,3 | 0.37048 | 0.73848 | 0 | 0 | 0.73848 | 0 | 6.615 | 5.8765 | 5.8765 | available
56 | SS 110/10 kV Polpinskaya | 16+16 | 5.645 | 0 | 0 | 5.645 | 0 | 16.8 | 11.155 | 11.155 | available | 56 | SS 110/10 kV Polpinskaya | 16+16 | 0.308 | 5.953 | 0 | 0 | 5.953 | 0 | 16.8 | 10.847 | 10.847 | available
57 | SS 110/6 kV Sovetskaya | 40+25+40 | 34.56 | 0 | 0 | 34.56 | 0 | 68.25 | 33.69 | 33.69 | available | 57 | SS 110/6 kV Sovetskaya | 40+25+40 | 19.7663 | 54.3263 | 0 | 0 | 54.3263 | 0 | 68.25 | 13.9237 | 13.9237 | available
58 | SS 110/6 kV Staleliteynaya | 40+31,5+40 | 27.791 | 0 | 0 | 27.791 | 0 | 75.075 | 47.284 | 47.284 | available | 58 | SS 110/6 kV Staleliteynaya | 40+31,5+40 | 0.5952 | 28.3862 | 0 | 0 | 28.3862 | 0 | 75.075 | 46.6888 | 46.6888 | available
59 | SS 110/10 kV Teplichnaya | 10+10 | 4.954 | 0 | 0 | 4.954 | 0 | 10.5 | 5.546 | 5.546 | available | 59 | SS 110/10 kV Teplichnaya | 10+10 | 1.2376 | 6.1916 | 0 | 0 | 6.1916 | 0 | 10.5 | 4.3084 | 4.3084 | available
60 | SS 110/6 kV Uritskaya | 20+20 | 10.207 | 0 | 0 | 10.207 | 0 | 21 | 10.793 | 10.793 | available | 60 | SS 110/6 kV Uritskaya | 20+20 | 0.1742 | 10.3812 | 0 | 0 | 10.3812 | 0 | 21 | 10.6188 | 10.6188 | available
61 | SS 110/35/10 kV Tsentralnaya | 16+16 | 14.498 | 4.8 | 6 hours | 9.698 | 0 | 16.8 | 7.102 | 7.102 | available | 61 | SS 110/35/10 kV Tsentralnaya | 16+16 | 0.164 | 14.662 | 4.8 | 6 hours | 9.862 | 0 | 16.8 | 6.938 | 6.938 | available
| Nom. capacity MV, MVA | 16+16 | 6.59 | 4.8 | 6 hours | 1.79 | 0 | 16.8 | 10.21 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 6.59 | 4.8 | 6 hours | 1.79 | 0 | 16.8 | 10.21
| Nom. capacity LV, MVA | 16+16 | 7.908 | 0 | 0 | 7.908 | 0 | 16.8 | 8.892 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.164 | 8.072 | 0 | 0 | 8.072 | 0 | 16.8 | 8.728
62 | SS 110/6 kV Yuzhnaya | 16+25 | 15.518 | 0 | 0 | 15.518 | 0 | 16.8 | 1.282 | 1.282 | available | 62 | SS 110/6 kV Yuzhnaya | 16+25 | 0.238 | 15.756 | 0 | 0 | 15.756 | 0 | 16.8 | 1.044 | 1.044 | available
63 | SS 110/10 kV Bobovichi | 6,3+2,5 | 0.937 | 0 | 0 | 0.937 | 0 | 2.625 | 1.688 | 1.688 | available | 63 | SS 110/10 kV Bobovichi | 6,3+2,5 | 0.0107 | 0.9477 | 0 | 0 | 0.9477 | 0 | 2.625 | 1.6773 | 1.6773 | available
64 | SS 110/6 kV Belaya Berezka | 16+25 | 5.17 | 0 | 0 | 5.17 | 0 | 16.8 | 11.63 | 11.63 | available | 64 | SS 110/6 kV Belaya Berezka | 16+25 | 0 | 5.17 | 0 | 0 | 5.17 | 0 | 16.8 | 11.63 | 11.63 | available
65 | SS 110/10 kV Valuets | 4+6,3 | 0.988 | 0 | 0 | 0.988 | 0 | 4.2 | 3.212 | 3.212 | available | 65 | SS 110/10 kV Valuets | 4+6,3 | 0.3224 | 1.3104 | 0 | 0 | 1.3104 | 0 | 4.2 | 2.8896 | 2.8896 | available
66 | SS 110/35/6 kV Vodoochistnaya | 10+6,3 | 1.915 | 0.54 | 3 hours | 1.375 | 0 | 6.615 | 5.24 | 4.747 | available | 66 | SS 110/35/6 kV Vodoochistnaya | 10+6,3 | 0 | 1.915 | 0.54 | 3 hours | 1.375 | 0 | 6.615 | 5.24 | 4.747 | available
| Nom. capacity MV, MVA | 10+6,3 | 0.047 | 0.54 | 3 hours | 0 | 0 | 6.615 | 6.568 |  |  |  | Nom. capacity MV, MVA | 10+6,3 |  | 0.047 | 0.54 | 3 hours | 0 | 0 | 6.615 | 6.568
| Nom. capacity LV, MVA | 10+6,3 | 1.868 | 0 | 0 | 1.868 | 0 | 6.615 | 4.747 |  |  |  | Nom. capacity LV, MVA | 10+6,3 | 0 | 1.868 | 0 | 0 | 1.868 | 0 | 6.615 | 4.747
67 | SS 110/6 kV Vysokoe | 40+40 | 25.614 | 0 | 0 | 25.614 | 0 | 42 | 16.386 | 16.386 | available | 67 | SS 110/6 kV Vysokoe | 40+40 | 0.0589 | 25.6729 | 0 | 0 | 25.6729 | 0 | 42 | 16.3271 | 16.3271 | available
68 | SS 110/10 kV Zalineynaya | 10+6,3 | 3.863 | 0 | 0 | 3.863 | 0 | 6.615 | 2.752 | 2.752 | available | 68 | SS 110/10 kV Zalineynaya | 10+6,3 | 0.43895 | 4.302 | 0 | 0 | 4.302 | 0 | 6.615 | 2.313 | 2.313 | available
69 | SS 110/6 kV Zapadnaya | 10+10 | 12.538 | 0 | 0 | 12.538 | 0 | 10.5 | -2.038 | -2.038 | unavailable | 69 | SS 110/6 kV Zapadnaya | 10+10 | 0.5904 | 13.1284 | 0 | 0 | 13.1284 | 0 | 10.5 | -2.6284 | -2.6284 | unavailable
70 | SS 110/35/10 kV Klimovo | 16+16 | 11.388 | 1.64 | 6 hours | 9.748 | 0 | 16.8 | 7.052 | 7.052 | available | 70 | SS 110/35/10 kV Klimovo | 16+16 | 0.22881 | 11.6168 | 1.64 | 6 hours | 9.9768 | 0 | 16.8 | 6.8232 | 6.8232 | available
| Nom. capacity MV, MVA | 16+16 | 4.073 | 1.64 | 6 hours | 2.433 | 0 | 16.8 | 12.727 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 4.073 | 1.64 | 6 hours | 2.433 | 0 | 16.8 | 12.727
| Nom. capacity LV, MVA | 16+16 | 7.315 | 0 | 0 | 7.315 | 0 | 16.8 | 9.485 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.22881 | 7.5438 | 0 | 0 | 7.5438 | 0 | 16.8 | 9.2562
71 | SS 110/35/6 kV Kozhany | 10+10 | 3.184 | 3.12 | 6 hours | 0.064 | 0 | 10.5 | 10.436 | 8.022 | available | 71 | SS 110/35/6 kV Kozhany | 10+10 | 0.0136 | 3.1976 | 3.12 | 6 hours | 0.0776 | 0 | 10.5 | 10.4224 | 8.022 | available
| Nom. capacity MV, MVA | 10+10 | 2.478 | 3.12 | 6 hours | -0.642 | 0 | 10.5 | 8.022 |  |  |  | Nom. capacity MV, MVA | 10+10 |  | 2.478 | 3.12 | 6 hours | -0.642 | 0 | 10.5 | 8.022
| Nom. capacity LV, MVA | 10+10 | 0.706 | 0 | 0 | 0.706 | 0 | 10.5 | 9.794 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.0136 | 0.7196 | 0 | 0 | 0.7196 | 0 | 10.5 | 9.7804
72 | SS 110/10 kV Krasny Rog | 2,5+2,5 | 1.004 | 0 | 0 | 1.004 | 0 | 2.625 | 1.621 | 1.621 | available | 72 | SS 110/10 kV Krasny Rog | 2,5+2,5 | 0.1938 | 1.1978 | 0 | 0 | 1.1978 | 0 | 2.625 | 1.4272 | 1.4272 | available
73 | SS 110/35/10 kV Pogar | 16+16+16 | 12.488 | 1.8 | 6 hours | 10.688 | 0 | 33.6 | 22.912 | 22.912 | available | 73 | SS 110/35/10 kV Pogar | 16+16+16 | 1.7287 | 14.2167 | 1.8 | 6 hours | 12.4167 | 0 | 33.6 | 21.1833 | 21.1833 | available
| Nom. capacity MV, MVA | 16+16 | 2.853 | 1.8 | 6 hours | 1.053 | 0 | 33.6 | 30.747 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 2.853 | 1.8 | 6 hours | 1.053 | 0 | 33.6 | 30.747
| Nom. capacity LV, MVA | 16+16 | 9.635 | 0 | 0 | 9.635 | 0 | 33.6 | 23.965 |  |  |  | Nom. capacity LV, MVA | 16+16 | 1.7287 | 11.3637 | 0 | 0 | 11.3637 | 0 | 33.6 | 22.2363
74 | SS 110/35/10 kV Pochepskaya | 25+25 | 12.455 | 2.21 | 3 hours | 10.245 | 0 | 26.25 | 16.005 | 16.005 | available | 74 | SS 110/35/10 kV Pochepskaya | 25+25 | 3.5774 | 16.0324 | 2.21 | 3 hours | 13.8224 | 0 | 26.25 | 12.4276 | 12.4276 | available
| Nom. capacity MV, MVA | 25+25 | 2.776 | 2.21 | 3 hours | 0.566 | 0 | 26.25 | 23.474 |  |  |  | Nom. capacity MV, MVA | 25+25 |  | 2.776 | 2.21 | 3 hours | 0.566 | 0 | 26.25 | 23.474
| Nom. capacity LV, MVA | 25+25 | 9.679 | 0 | 0 | 9.679 | 0 | 26.25 | 16.571 |  |  |  | Nom. capacity LV, MVA | 25+25 | 3.5774 | 13.2564 | 0 | 0 | 13.2564 | 0 | 26.25 | 12.9936
75 | SS 110/10 kV Semyachki | 2,5+2,5 | 0.369 | 0 | 0 | 0.369 | 0 | 2.625 | 2.256 | 2.256 | available | 75 | SS 110/10 kV Semyachki | 2,5+2,5 | 0.0286 | 0.3976 | 0 | 0 | 0.3976 | 0 | 2.625 | 2.2274 | 2.2274 | available
76 | SS 110/35/10 kV Starodub | 16+16 | 14.8 | 7.34 | 6 hours | 7.46 | 0 | 16.8 | 9.34 | 6.877 | available | 76 | SS 110/35/10 kV Starodub | 16+16 | 0.0621 | 14.8621 | 7.34 | 6 hours | 7.5221 | 0 | 16.8 | 9.2779 | 6.877 | available
| Nom. capacity MV, MVA | 16+16 | 9.923 | 7.34 | 6 hours | 2.583 | 0 | 16.8 | 6.877 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 9.923 | 7.34 | 6 hours | 2.583 | 0 | 16.8 | 6.877
| Nom. capacity LV, MVA | 16+16 | 4.877 | 0 | 0 | 4.877 | 0 | 16.8 | 11.923 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.0621 | 4.9391 | 0 | 0 | 4.9391 | 0 | 16.8 | 11.8609
77 | SS 110/10 kV Staroselye | 6,3+6,3 | 1.018 | 0 | 0 | 1.018 | 0 | 6.615 | 5.597 | 5.597 | available | 77 | SS 110/10 kV Staroselye | 6,3+6,3 | 0.17001 | 1.188 | 0 | 0 | 1.188 | 0 | 6.615 | 5.427 | 5.427 | available
78 | SS 110/35/6 kV Surazh | 16+16 | 18.458 | 0 | 0 | 18.458 | 0 | 16.8 | -1.658 | -1.658 | unavailable | 78 | SS 110/35/6 kV Surazh | 16+16 | 0 | 18.458 | 0 | 0 | 18.458 | 0 | 16.8 | -1.658 | -1.658 | unavailable
| Nom. capacity MV, MVA | 16+16 | 3.769 | 0 | 0 | 3.769 | 0 | 16.8 | 13.031 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 3.769 | 0 | 0 | 3.769 | 0 | 16.8 | 13.031
| Nom. capacity LV, MVA | 16+16 | 14.689 | 0 | 0 | 14.689 | 0 | 16.8 | 2.111 |  |  |  | Nom. capacity LV, MVA | 16+16 |  | 14.689 | 0 | 0 | 14.689 | 0 | 16.8 | 2.111
79 | SS 110/10 kV Trubchevsk | 16+10 | 7.895 | 0 | 0 | 7.895 | 0 | 10.5 | 2.605 | 2.605 | available | 79 | SS 110/10 kV Trubchevsk | 16+10 | 1.0631 | 8.9581 | 0 | 0 | 8.9581 | 0 | 10.5 | 1.5419 | 1.5419 | available
80 | SS 110/10 kV Shelomy | 6,3+6,3 | 0.808 | 0 | 0 | 0.808 | 0 | 6.615 | 5.807 | 5.807 | available | 80 | SS 110/10 kV Shelomy | 6,3+6,3 | 0.0318 | 0.8398 | 0 | 0 | 0.8398 | 0 | 6.615 | 5.7752 | 5.7752 | available
81 | SS 110/35/6 kV Yubileynaya | 16+16 | 13.364 | 6.45 | 3 hours | 6.914 | 0 | 16.8 | 9.886 | 7.47 | available | 81 | SS 110/35/6 kV Yubileynaya | 16+16 | 1.8544 | 15.2184 | 6.45 | 3 hours | 8.7684 | 0 | 16.8 | 8.0316 | 5.6156 | available
| Nom. capacity MV, MVA | 16+16 | 4.034 | 6.45 | 3 hours | 0 | 0 | 16.8 | 12.766 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 4.034 | 6.45 | 3 hours | 0 | 0 | 16.8 | 12.766
| Nom. capacity LV, MVA | 16+16 | 9.33 | 0 | 0 | 9.33 | 0 | 16.8 | 7.47 |  |  |  | Nom. capacity LV, MVA | 16+16 | 1.8544 | 11.1844 | 0 | 0 | 11.1844 | 0 | 16.8 | 5.6156
82 | SS 35/6 kV Beloberezhskaya | 6,3+6,3 | 2.983 | 0 | 0 | 2.983 | 0 | 6.615 | 3.632 | 3.632 | available | 82 | SS 35/6 kV Beloberezhskaya | 6,3+6,3 | 0.043 | 3.026 | 0 | 0 | 3.026 | 0 | 6.615 | 3.589 | 3.589 | available
83 | SS 35/10 kV Brasovskaya | 6,3+6,3 | 3.28 | 0 | 0 | 3.28 | 0 | 6.615 | 3.335 | 3.335 | available | 83 | SS 35/10 kV Brasovskaya | 6,3+6,3 | 0.0187 | 3.2987 | 0 | 0 | 3.2987 | 0 | 6.615 | 3.3163 | 3.3163 | available
84 | SS 35/10 kV Bulshevskaya | 1,6+1,6 | 0.549 | 0 | 0 | 0.549 | 0 | 1.68 | 1.131 | 1.131 | available | 84 | SS 35/10 kV Bulshevskaya | 1,6+1,6 | 0.2228 | 0.7718 | 0 | 0 | 0.7718 | 0 | 1.68 | 0.9082 | 0.9082 | available
85 | SS 35/6 kV Bytosh | 3,2+6,3 | 2.632 | 0 | 0 | 2.632 | 0 | 3.36 | 0.728 | 0.728 | available | 85 | SS 35/6 kV Bytosh | 3,2+6,3 | 0.0183 | 2.6503 | 0 | 0 | 2.6503 | 0 | 3.36 | 0.7097 | 0.7097 | available
86 | SS 35/6 kV Velyaminovskaya | 4+4 | 1.237 | 0 | 0 | 1.237 | 0 | 4.2 | 2.963 | 2.963 | available | 86 | SS 35/6 kV Velyaminovskaya | 4+4 | 0.1314 | 1.3684 | 0 | 0 | 1.3684 | 0 | 4.2 | 2.8316 | 2.8316 | available
87 | SS 35/6 kV Vetma | 2,5+2,5 | 0.536 | 0 | 0 | 0.536 | 0 | 2.625 | 2.089 | 2.089 | available | 87 | SS 35/6 kV Vetma | 2,5+2,5 | 0.087528 | 0.62353 | 0 | 0 | 0.62353 | 0 | 2.625 | 2.0015 | 2.0015 | available
88 | SS 35/6 kV Volodarskaya | 10+6,3 | 11.314 | 0 | 0 | 11.314 | 0 | 6.615 | -4.699 | -4.699 | unavailable | 88 | SS 35/6 kV Volodarskaya | 10+6,3 | 0 | 11.314 | 0 | 0 | 11.314 | 0 | 6.615 | -4.699 | -4.699 | unavailable
89 | SS 35/10 kV Glodnevskaya | 4+2,5 | 1.174 | 0 | 0 | 1.174 | 0 | 2.625 | 1.451 | 1.451 | available | 89 | SS 35/10 kV Glodnevskaya | 4+2,5 | 0.047 | 1.221 | 0 | 0 | 1.221 | 0 | 2.625 | 1.404 | 1.404 | available
90 | SS 35/6 kV Gorodskaya | 10+10 | 11.754 | 0 | 0 | 11.754 | 0 | 10.5 | -1.254 | -1.254 | unavailable | 90 | SS 35/6 kV Gorodskaya | 10+10 | 0 | 11.754 | 0 | 0 | 11.754 | 0 | 10.5 | -1.254 | -1.254 | unavailable
91 | SS 35/10 kV Grishina Sloboda | 4+4 | 0.771 | 0 | 0 | 0.771 | 0 | 4.2 | 3.429 | 3.429 | available | 91 | SS 35/10 kV Grishina Sloboda | 4+4 | 0.045 | 0.816 | 0 | 0 | 0.816 | 0 | 4.2 | 3.384 | 3.384 | available
92 | SS 35/10 kV Dobrovodye | 1,6+1,6 | 0.33 | 0 | 0 | 0.33 | 0 | 1.68 | 1.35 | 1.35 | available | 92 | SS 35/10 kV Dobrovodye | 1,6+1,6 | 0.0065 | 0.3365 | 0 | 0 | 0.3365 | 0 | 1.68 | 1.3435 | 1.3435 | available
93 | SS 35/10 kV Zhiryatinskaya | 4+4 | 1.911 | 0 | 0 | 1.911 | 0 | 4.2 | 2.289 | 2.289 | available | 93 | SS 35/10 kV Zhiryatinskaya | 4+4 | 0.69773 | 2.6087 | 0 | 0 | 2.6087 | 0 | 4.2 | 1.5913 | 1.5913 | available
94 | SS 35/10 kV Igritskaya | 4+6,3 | 1.812 | 0 | 0 | 1.812 | 0 | 4.2 | 2.388 | 2.388 | available | 94 | SS 35/10 kV Igritskaya | 4+6,3 | 0.038644 | 1.8506 | 0 | 0 | 1.8506 | 0 | 4.2 | 2.3494 | 2.3494 | available
95 | SS 35/10 kV Kasilovskaya | 2,5+1 | 0.12 | 0 | 0 | 0.12 | 0 | 1.05 | 0.93 | 0.93 | available | 95 | SS 35/10 kV Kasilovskaya | 2,5+1 | 0.0133 | 0.1333 | 0 | 0 | 0.1333 | 0 | 1.05 | 0.9167 | 0.9167 | available
96 | SS 35/10 kV Kositskaya | 2,5+2,5 | 0.245 | 0 | 0 | 0.245 | 0 | 2.625 | 2.38 | 2.38 | available | 96 | SS 35/10 kV Kositskaya | 2,5+2,5 | 0.0165 | 0.2615 | 0 | 0 | 0.2615 | 0 | 2.625 | 2.3635 | 2.3635 | available
97 | SS 35/10 kV Krupets | 2,5+2,5 | 0.508 | 0 | 0 | 0.508 | 0 | 2.625 | 2.117 | 2.117 | available | 97 | SS 35/10 kV Krupets | 2,5+2,5 | 0.7679 | 1.2759 | 0 | 0 | 1.2759 | 0 | 2.625 | 1.3491 | 1.3491 | available
98 | SS 35/10 kV Luna | 1,6+1,6 | 1.131 | 0 | 0 | 1.131 | 0 | 1.68 | 0.549 | 0.549 | available | 98 | SS 35/10 kV Luna | 1,6+1,6 | 0 | 1.131 | 0 | 0 | 1.131 | 0 | 1.68 | 0.549 | 0.549 | available
99 | SS 35/6 kV Lyubokhna | 6,3+6,3 | 4.202 | 0 | 0 | 4.202 | 0 | 6.615 | 2.413 | 2.413 | available | 99 | SS 35/6 kV Lyubokhna | 6,3+6,3 | 0.0339 | 4.2359 | 0 | 0 | 4.2359 | 0 | 6.615 | 2.3791 | 2.3791 | available
100 | SS 35/10 kV Mareevskaya | 1,6+1,6 | 0.823 | 0 | 0 | 0.823 | 0 | 1.68 | 0.857 | 0.857 | available | 100 | SS 35/10 kV Mareevskaya | 1,6+1,6 | 0.0345 | 0.8575 | 0 | 0 | 0.8575 | 0 | 1.68 | 0.8225 | 0.8225 | available
101 | SS 35/10 kV Nevdolsk | 1,6+1,6 | 0.162 | 0 | 0 | 0.162 | 0 | 1.68 | 1.518 | 1.518 | available | 101 | SS 35/10 kV Nevdolsk | 1,6+1,6 | 0.0195 | 0.1815 | 0 | 0 | 0.1815 | 0 | 1.68 | 1.4985 | 1.4985 | available
102 | SS 35/10 kV Norinskaya | 4+4 | 0.52 | 0 | 0 | 0.52 | 0 | 4.2 | 3.68 | 3.68 | available | 102 | SS 35/10 kV Norinskaya | 4+4 | 0.0239 | 0.5439 | 0 | 0 | 0.5439 | 0 | 4.2 | 3.6561 | 3.6561 | available
103 | SS 35/6 kV Paltso | 4+2,5 | 0.47 | 0 | 0 | 0.47 | 0 | 2.625 | 2.155 | 2.155 | available | 103 | SS 35/6 kV Paltso | 4+2,5 | 0.0148 | 0.4848 | 0 | 0 | 0.4848 | 0 | 2.625 | 2.1402 | 2.1402 | available
104 | SS 35/6 kV Pobeda | 4+4 | 2.478 | 0 | 0 | 2.478 | 0 | 4.2 | 1.722 | 1.722 | available | 104 | SS 35/6 kV Pobeda | 4+4 | 0.0153 | 2.4933 | 0 | 0 | 2.4933 | 0 | 4.2 | 1.7067 | 1.7067 | available
105 | SS 35/10 kV Pogreby | 4+4 | 1.068 | 0 | 0 | 1.068 | 0 | 4.2 | 3.132 | 3.132 | available | 105 | SS 35/10 kV Pogreby | 4+4 | 0.0761 | 1.1441 | 0 | 0 | 1.1441 | 0 | 4.2 | 3.0559 | 3.0559 | available
106 | SS 35/10 kV Privolskaya | 2,5+1,6 | 1.31 | 0 | 0 | 1.31 | 0 | 1.68 | 0.37 | 0.37 | available | 106 | SS 35/10 kV Privolskaya | 2,5+1,6 | 0.3571 | 1.6671 | 0 | 0 | 1.6671 | 0 | 1.68 | 0.0129 | 0.0129 | available
107 | SS 35/10 kV Rzhanitskaya | 2,5+2,5 | 0.983 | 0 | 0 | 0.983 | 0 | 2.625 | 1.642 | 1.642 | available | 107 | SS 35/10 kV Rzhanitskaya | 2,5+2,5 | 0 | 0.983 | 0 | 0 | 0.983 | 0 | 2.625 | 1.642 | 1.642 | available
108 | SS 35/10 kV Rognedinskaya | 4+6,3 | 1.315 | 0 | 0 | 1.315 | 0 | 4.2 | 2.885 | 2.885 | available | 108 | SS 35/10 kV Rognedinskaya | 4+6,3 | 0.056952 | 1.372 | 0 | 0 | 1.372 | 0 | 4.2 | 2.828 | 2.828 | available
109 | SS 35/10,5 kV Ruzhnenskaya | 4+4 | 0.766 | 0 | 0 | 0.766 | 0 | 4.2 | 3.434 | 3.434 | available | 109 | SS 35/10,5 kV Ruzhnenskaya | 4+4 | 0.0409 | 0.8069 | 0 | 0 | 0.8069 | 0 | 4.2 | 3.3931 | 3.3931 | available
110 | SS 35/10 kV Sevskaya | 6,3+6,3 | 4.521 | 0 | 0 | 4.521 | 0 | 6.615 | 2.094 | 2.094 | available | 110 | SS 35/10 kV Sevskaya | 6,3+6,3 | 0.83628 | 5.3573 | 0 | 0 | 5.3573 | 0 | 6.615 | 1.2577 | 1.2577 | available
21 | SS 35/6 kc Seshcha | 4+4 | 1.989 | 0 | 0 | 1.989 | 0 | 4.2 | 2.211 | 2.211 | unavailable | 21 | SS 35/6 kc Seshcha | 4+4 | 0.603 | 2.592 | 0 | 0 | 2.592 | 0 | 4.2 | 1.608 | 1.608 | available
111 | SS 35/6 kV Star | 10+10 | 2.358 | 0 | 0 | 2.358 | 0 | 10.5 | 8.142 | 8.142 | available | 111 | SS 35/6 kV Star | 10+10 | 0 | 2.358 | 0 | 0 | 2.358 | 0 | 10.5 | 8.142 | 8.142 | available
112 | SS 35/10 kV Teplovskaya | 2,5+2,5 | 0.579 | 0 | 0 | 0.579 | 0 | 2.625 | 2.046 | 2.046 | available | 112 | SS 35/10 kV Teplovskaya | 2,5+2,5 | 0.4545 | 1.0335 | 0 | 0 | 1.0335 | 0 | 2.625 | 1.5915 | 1.5915 | available
113 | SS 35/10 kV Fedorovskaya | 1,6+1,8 | 0.484 | 0 | 0 | 0.484 | 0 | 1.68 | 1.196 | 1.196 | available | 113 | SS 35/10 kV Fedorovskaya | 1,6+1,8 | 0.0145 | 0.4985 | 0 | 0 | 0.4985 | 0 | 1.68 | 1.1815 | 1.1815 | available
114 | SS 35/6 kV Fokinskaya | 16+16+16 | 16.125 | 0 | 0 | 16.125 | 0 | 33.6 | 17.475 | 17.475 | available | 114 | SS 35/6 kV Fokinskaya | 16+16+16 | 3.8532 | 19.9782 | 0 | 0 | 19.9782 | 0 | 33.6 | 13.6218 | 13.6218 | available
115 | SS 35/6 kV Fosforitnaya | 6,3+5,6+16 | 10.76 | 0 | 0 | 10.76 | 0 | 12.495 | 1.735 | 1.735 | available | 115 | SS 35/6 kV Fosforitnaya | 6,3+5,6+16 | 0.0158 | 10.7758 | 0 | 0 | 10.7758 | 0 | 12.495 | 1.7192 | 1.7192 | available
116 | SS 35/10 kV Khvoshchevskaya | 2,5+4 | 0.994 | 0 | 0 | 0.994 | 0 | 2.625 | 1.631 | 1.631 | available | 116 | SS 35/10 kV Khvoshchevskaya | 2,5+4 | 0.36166 | 1.3557 | 0 | 0 | 1.3557 | 0 | 2.625 | 1.2693 | 1.2693 | available
117 | SS 35/10 kV Abarinskaya | 4+4 | 0.957 | 0 | 0 | 0.957 | 0 | 4.2 | 3.243 | 3.243 | available | 117 | SS 35/10 kV Abarinskaya | 4+4 | 0.1053 | 1.0623 | 0 | 0 | 1.0623 | 0 | 4.2 | 3.1377 | 3.1377 | available
118 | SS 35/10 kV Andreykovichi | 2,5+2,5 | 0.828 | 0 | 0 | 0.828 | 0 | 2.625 | 1.797 | 1.797 | available | 118 | SS 35/10 kV Andreykovichi | 2,5+2,5 | 0.0688 | 0.8968 | 0 | 0 | 0.8968 | 0 | 2.625 | 1.7282 | 1.7282 | available
119 | SS 35/10 kV Borshchevo | 1,6+1,6 | 0.932 | 0 | 0 | 0.932 | 0 | 1.68 | 0.748 | 0.748 | available | 119 | SS 35/10 kV Borshchevo | 1,6+1,6 | 0.0361 | 0.9681 | 0 | 0 | 0.9681 | 0 | 1.68 | 0.7119 | 0.7119 | available
120 | SS 35/10 kV Vlazovichi | 2,5+1,6 | 0.489 | 0 | 0 | 0.489 | 0 | 1.68 | 1.191 | 1.191 | available | 120 | SS 35/10 kV Vlazovichi | 2,5+1,6 | 0.016 | 0.505 | 0 | 0 | 0.505 | 0 | 1.68 | 1.175 | 1.175 | available
121 | SS 35/6 kV Water intake | 2,5+2,5 | 0.445 | 0 | 0 | 0.445 | 0 | 2.625 | 2.18 | 2.18 | available | 121 | SS 35/6 kV Water intake | 2,5+2,5 | 0 | 0.445 | 0 | 0 | 0.445 | 0 | 2.625 | 2.18 | 2.18 | available
122 | SS 35/10 kV Voronok | 2,5+3,2 | 1.551 | 0 | 0 | 1.551 | 0 | 2.625 | 1.074 | 1.074 | available | 122 | SS 35/10 kV Voronok | 2,5+3,2 | 0.0372 | 1.5882 | 0 | 0 | 1.5882 | 0 | 2.625 | 1.0368 | 1.0368 | available
123 | SS 35/10 kV Gordeevka | 4+4 | 2.361 | 0 | 0 | 2.361 | 0 | 4.2 | 1.839 | 1.839 | available | 123 | SS 35/10 kV Gordeevka | 4+4 | 0.085376 | 2.4464 | 0 | 0 | 2.4464 | 0 | 4.2 | 1.7536 | 1.7536 | available
124 | SS 35/10 kV Gridenki | 2,5+3,2 | 1.757 | 0 | 0 | 1.757 | 0 | 2.625 | 0.868 | 0.868 | available | 124 | SS 35/10 kV Gridenki | 2,5+3,2 | 0.1219 | 1.8789 | 0 | 0 | 1.8789 | 0 | 2.625 | 0.7461 | 0.7461 | available
125 | SS 35/10 kV Zavodskaya | 4+2,5 | 1.583 | 0 | 0 | 1.583 | 0 | 2.625 | 1.042 | 1.042 | available | 125 | SS 35/10 kV Zavodskaya | 4+2,5 | 0.034 | 1.617 | 0 | 0 | 1.617 | 0 | 2.625 | 1.008 | 1.008 | available
126 | SS 35/10 kV Istopki | 1,6+1,6 | 0.721 | 0 | 0 | 0.721 | 0 | 1.68 | 0.959 | 0.959 | available | 126 | SS 35/10 kV Istopki | 1,6+1,6 | 0.034502 | 0.7555 | 0 | 0 | 0.7555 | 0 | 1.68 | 0.9245 | 0.9245 | available
127 | SS 35/10 kV Katashin | 1,6+1,6 | 0.47 | 0 | 0 | 0.47 | 0 | 1.68 | 1.21 | 1.21 | available | 127 | SS 35/10 kV Katashin | 1,6+1,6 | 0.0159 | 0.4859 | 0 | 0 | 0.4859 | 0 | 1.68 | 1.1941 | 1.1941 | available
128 | SS 35/10 kV Kivay | 2,5+2,5 | 1.894 | 0 | 0 | 1.894 | 0 | 2.625 | 0.731 | 0.731 | available | 128 | SS 35/10 kV Kivay | 2,5+2,5 | 0.24065 | 2.1347 | 0 | 0 | 2.1347 | 0 | 2.625 | 0.49035 | 0.49035 | available
129 | SS 35/10 kV Krutoyar | 2,5+1,6 | 0.749 | 0 | 0 | 0.749 | 0 | 1.68 | 0.931 | 0.931 | available | 129 | SS 35/10 kV Krutoyar | 2,5+1,6 | 0.0093 | 0.7583 | 0 | 0 | 0.7583 | 0 | 1.68 | 0.9217 | 0.9217 | available
130 | SS 35/10 kV Logovatoe | 2,5+1,6 | 1.022 | 0 | 0 | 1.022 | 0 | 1.68 | 0.658 | 0.658 | available | 130 | SS 35/10 kV Logovatoe | 2,5+1,6 | 0.17654 | 1.1985 | 0 | 0 | 1.1985 | 0 | 1.68 | 0.48146 | 0.48146 | available
131 | SS 35/10 kV Lopazna | 2,5+2,5 | 0.354 | 0 | 0 | 0.354 | 0 | 2.625 | 2.271 | 2.271 | available | 131 | SS 35/10 kV Lopazna | 2,5+2,5 | 0.0357 | 0.3897 | 0 | 0 | 0.3897 | 0 | 2.625 | 2.2353 | 2.2353 | available
132 | SS 35/10 kV Mglinskaya | 4+4 | 3.387 | 0 | 0 | 3.387 | 0 | 4.2 | 0.813 | 0.813 | available | 132 | SS 35/10 kV Mglinskaya | 4+4 | 0.20604 | 3.593 | 0 | 0 | 3.593 | 0 | 4.2 | 0.60696 | 0.60696 | available
133 | SS 35/10 kV Mishkovka | 1,6+1,6 | 0.654 | 0 | 0 | 0.654 | 0 | 1.68 | 1.026 | 1.026 | available | 133 | SS 35/10 kV Mishkovka | 1,6+1,6 | 0.0118 | 0.6658 | 0 | 0 | 0.6658 | 0 | 1.68 | 1.0142 | 1.0142 | available
134 | SS 35/10 kV Novo-Drokov | 2,5+2,5 | 0.552 | 0 | 0 | 0.552 | 0 | 2.625 | 2.073 | 2.073 | available | 134 | SS 35/10 kV Novo-Drokov | 2,5+2,5 | 0.2074 | 0.7594 | 0 | 0 | 0.7594 | 0 | 2.625 | 1.8656 | 1.8656 | available
135 | SS 35/10 kV Putevaya | 6,3+6,3 | 6.452 | 0 | 0 | 6.452 | 0 | 6.615 | 0.163 | 0.163 | available | 135 | SS 35/10 kV Putevaya | 6,3+6,3 | 0.0726 | 6.5246 | 0 | 0 | 6.5246 | 0 | 6.615 | 0.0904 | 0.0904 | available
136 | SS 35/10 kV Selishchanskaya | 2,5+2,5 | 1.201 | 0 | 0 | 1.201 | 0 | 2.625 | 1.424 | 1.424 | available | 136 | SS 35/10 kV Selishchanskaya | 2,5+2,5 | 0.261 | 1.462 | 0 | 0 | 1.462 | 0 | 2.625 | 1.163 | 1.163 | available
137 | SS 35/10 kV Slava | 2,5+1,6 | 0.919 | 0 | 0 | 0.919 | 0 | 1.68 | 0.761 | 0.761 | available | 137 | SS 35/10 kV Slava | 2,5+1,6 | 0.0927 | 1.0117 | 0 | 0 | 1.0117 | 0 | 1.68 | 0.6683 | 0.6683 | available
138 | SS 35/10 kV Smolevichi | 6,3+6,3 | 3.665 | 0 | 0 | 3.665 | 0 | 6.615 | 2.95 | 2.95 | available | 138 | SS 35/10 kV Smolevichi | 6,3+6,3 | 0.21715 | 3.8822 | 0 | 0 | 3.8822 | 0 | 6.615 | 2.7328 | 2.7328 | available
139 | SS 35/10 kV Solovyevka | 1,6+1,6 | 0.403 | 0 | 0 | 0.403 | 0 | 1.68 | 1.277 | 1.277 | available | 139 | SS 35/10 kV Solovyevka | 1,6+1,6 | 0.0029 | 0.4059 | 0 | 0 | 0.4059 | 0 | 1.68 | 1.2741 | 1.2741 | available
140 | SS 35/10 kV Sytaya Buda | 2,5+2,5 | 0.785 | 0 | 0 | 0.785 | 0 | 2.625 | 1.84 | 1.84 | available | 140 | SS 35/10 kV Sytaya Buda | 2,5+2,5 | 0.0232 | 0.8082 | 0 | 0 | 0.8082 | 0 | 2.625 | 1.8168 | 1.8168 | available
141 | SS 35/6 kV Tembr | 4+4+3,2 | 6.377 | 0 | 0 | 6.377 | 0 | 7.56 | 1.183 | 1.183 | available | 141 | SS 35/6 kV Tembr | 4+4+3,2 | 0.1324 | 6.5094 | 0 | 0 | 6.5094 | 0 | 7.56 | 1.0506 | 1.0506 | available
142 | SS 35/10 kV Churovichi | 2,5+4 | 0.689 | 0 | 0 | 0.689 | 0 | 2.625 | 1.936 | 1.936 | available | 142 | SS 35/10 kV Churovichi | 2,5+4 | 0.098807 | 0.78781 | 0 | 0 | 0.78781 | 0 | 2.625 | 1.8372 | 1.8372 | available
143 | SS 35/10 kV Shcherbinichi | 2,5+2,5 | 1.099 | 0 | 0 | 1.099 | 0 | 2.625 | 1.526 | 1.526 | available | 143 | SS 35/10 kV Shcherbinichi | 2,5+2,5 | 0.0465 | 1.1455 | 0 | 0 | 1.1455 | 0 | 2.625 | 1.4795 | 1.4795 | available
| Total: | 2312.9 | 706.794 | [8 empty] | 2: Total:; 3: 2312.9; 4: 107.6365; 5: 814.4305
| deficit | [8 empty] | -23.951 |  | 2: deficit; Min 12: -58.228
| proficit | [8 empty] | 553.265 |  | 2: proficit; Min 12: 506.7993

## Total current deficit (winter)
The list of closed supply centers of IDGC of Centre following the results of winter load operation in 2010 (current deficit of capacity).
No. | Name of supply center, voltage class |  | Current deficit, MVA | [5 empty] | Current deficit, MVA
Bryanskenergo
1 | SS 110/6 kV Bezhitskaya | 25+40 | 34.57 | 0 | 0 | 34.57 | 0 | 26.25 | -0.933
2 | SS 110/6 kV Gorodishchenskaya | 16+16 | 25.56 | 1.5 | 12 hours | 24.06 | 0 | 16.8 | -2.37
3 | SS 110/10 kV Dobrunskaya | 6,3+4 | 4.338 | 0 | 0 | 4.338 | 0 | 4.2 | -0.205
4 | SS 110/35/6 kV Dormashevskaya | 40+63 | 44.04 | 0 | 0 | 44.04 | 0 | 42 | -2.456
| Nom. capacity MV, MVA | 40+63 | 22.42 | 0 | 0 | 22.42 | 0 | 42
| Nom. capacity LV, MVA | 40+63 | 21.62 | 0 | 0 | 21.62 | 0 | 42
5 | SS 110/35/6 kV Dyatkovkskaya | 25+25 | 36.72 | 8.9 | 12 hours | 27.82 | 0 | 26.25 | -2.165
| Nom. capacity MV, MVA | 25+25 | 8.85 | 8.9 | 12 hours | -0.05 | 0 | 26.25
| Nom. capacity LV, MVA | 25+25 | 27.87 | 0 | 0 | 27.87 | 0 | 26.25
6 | SS 110/6 kV Karachizhskaya | 10+10 | 18.28 | 0 | 0 | 18.28 | 0 | 10.5 | -3.431
7 | SS 110/6 kV Energoremont | 10 | 19.43 | 0 | 0 | 19.43 | 0 | 16.8 | -2.742
8 | SS 110/6 kV Zapadnaya | 10+10 | 19.43 | 0 | 0 | 19.43 | 0 | 16.8 | -2.038
9 | SS 110/35/6 kV Surazh | 16+16 | [6 empty] | -1.658
10 | SS 35/6 kV Volodarskaya | 10+6,3 | 11.13 | 0 | 0 | 11.13 | 0 | 6.615 | -4.699
11 | SS 35/6 kV Gorodskaya | 10+10 | 10.88 | 0 | 0 | 10.88 | 0 | 10.5 | -1.254
Total current deficit (winter) |  | 378.6 | [6 empty] | -23.951

## Total expected deficit (winter)
The list of closed supply centers of IDGC of Centre with expected load taking into account new connections and other development of the electical networks.
Item # | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number provided that technical requirements at connections or other measures performed for reconstruction of the supply center, pcs/ MVA | Дополнительная мощность по выданным ТУ на ТП, МВА | Ожидаемая нагрузка ЦП, МВА | Полная перераспределяемая мощность в перспективе с учетом выполнения мероприятий ТУ или других мероприятий по реконструкции сети инвестпрограмм и др. |  | Полная мощность с учётом перераспределения, МВА | Ограничивающие факторы, МВА | Допустимая нагрузка расчётная в режиме n-1, МВА | Пропускная способность ЦП, МВА | Current deficit/proficit, MVA
[5 empty] | МВА | Мин.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
Bryanskenergo
1 | SS 110/6 kV Bezhitskaya | 25+40 | 3.182 | #REF! | 0 | 0 | #REF! | 0 | 26.25 | #REF! | -5.9167 | unavailable
2 | SS 110/6 kV Gorodishchenskaya | 16+16 | 0.806 | #REF! | 1.5 | 12 hours | #REF! | 0 | 16.8 | #REF! | -11.1421 | unavailable
3 | SS 110/10 kV Dobrunskaya | 6,3+4 | 0.524 | #REF! | 0 | 0 | #REF! | 0 | 4.2 | #REF! | -2.6771 | unavailable
4 | SS 110/35/6 kV Dormashevskaya | 40+63 | 3.226 | 42.736 | 0 | 0 | 42.736 | 0 | 42 | -0.736 | -14.6571 | unavailable
| Nom. capacity MV, MVA | 40+63 |  | #REF! | 0 | 0 | #REF! | 0 | 42 | #REF!
| Nom. capacity LV, MVA | 40+63 | 3.226 | #REF! | 0 | 0 | #REF! | 0 | 42 | #REF!
5 | SS 110/35/6 kV Dyatkovkskaya | 25+25 | 0 | 36.72 | 8.9 | 12 hours | 27.82 | 0 | 26.25 | -1.57 | -2.7946 | unavailable
| Nom. capacity MV, MVA | 25+25 |  | #REF! | 8.9 | 12 hours | #REF! | 0 | 26.25 | #REF!
| Nom. capacity LV, MVA | 25+25 |  | #REF! | 0 | 0 | #REF! | 0 | 26.25 | #REF!
6 | SS 110/6 kV Karachizhskaya | 10+10 | 0.457 | #REF! | 0 | 0 | #REF! | 0 | 10.5 | #REF! | -6.3236 | unavailable
7 | SS 110/6 kV Naytopovichi 8NA | 10+10 | 1.472 | #REF! | 0 | 0 | #REF! | 0 | 10.5 | #REF! | -2.6284 | unavailable
8 | SS 110/35/10 kV Klimovo | 16+16 | 0.238 | #REF! | 0 | 0 | #REF! | 0 | 16.8 | #REF! | -1.658 | unavailable
9 | Nom. capacity MV, MVA | 10 | [8 empty] | -4.4774 | unavailable
10 | SS 35/6 kV Volodarskaya | 10+6,3 | 0 | #REF! | 0 | 0 | #REF! | 0 | 6.615 | #REF! | -4.699 | unavailable
11 | SS 35/6 kV Gorodskaya | 10+10 | 0 | #REF! | 0 | 0 | #REF! | 0 | 10.5 | #REF! | -1.254 | unavailable
| Total: | 378.6 | [8 empty] | -58.228