## Orel
Calculation of transmission capacity of supply centres of IDGC of Center - Orelenergo following the winter peak load measurements in 2010
table 1
No. | Name of supply center, voltage class | Current deficit | [8 empty] | Note | No. | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity, MVA | Current deficit/proficit MVA |  |  |  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load of Supply Center, MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity of Supply Center, MVA | Expected deficit/proficit, MVA
|  |  | MVA | MVA | Min | [11 empty] | MVA | Min
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | SS 35/10 kV Almazovo | 2.5 | 0.49 | 0.83 | 30 | 0.83 | 0 | 0.83 | 0.34 | 0.34 | available | 1 | SS 35/10 kV Almazovo | 2.5 | 0.065 | 0.555 | 0.83 | 30 | 0.83 | 0 | 0.83 | 0.275 | 0.275 | available
2 | SS 35/10 kV Voronets | 2.5 | 0.23 | 0.91 | 90 | 0.91 | 0 | 0.91 | 0.68 | 0.68 | available | 2 | SS 35/10 kV Voronets | 2.5 | 0 | 0.23 | 0.91 | 90 | 0.91 | 0 | 0.91 | 0.68 | 0.68 | available
3 | SS 35/10 kV Gostoml | 2.5 | 0.79 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 0.81 | 0.81 | available | 3 | SS 35/10 kV Gostoml | 2.5 | 0.059 | 0.849 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 0.751 | 0.751 | available
4 | SS 35/10 kV Gubkino | 3.2 | 0.39 | 1.56 | 30 | 1.56 | 0 | 1.56 | 1.17 | 1.17 | available | 4 | SS 35/10 kV Gubkino | 3.2 | 0.014 | 0.404 | 1.56 | 30 | 1.56 | 0 | 1.56 | 1.156 | 1.156 | available
5 | SS 35/10 kV Devyatino | 1.6 | 0.21 | 0.71 | 45 | 0.71 | 0 | 0.71 | 0.5 | 0.5 | available | 5 | SS 35/10 kV Devyatino | 1.6 | 0.012 | 0.222 | 0.71 | 45 | 0.71 | 0 | 0.71 | 0.488 | 0.488 | available
6 | SS 35/10 kV Kamenka | 2.5 | 0.89 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 0.71 | 0.71 | available | 6 | SS 35/10 kV Kamenka | 2.5 | 0.043 | 0.933 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 0.667 | 0.667 | available
7 | SS 35/10 kV Kozminskaya | 2.5 | 0.33 | 1.29 | 45 | 1.29 | 0 | 1.29 | 0.96 | 0.96 | available | 7 | SS 35/10 kV Kozminskaya | 2.5 | 0.071 | 0.401 | 1.29 | 45 | 1.29 | 0 | 1.29 | 0.889 | 0.889 | available
8 | SS 110/35/10 kV Maloarkhangelskaya | 10 | 4.23 | 6.14 | 60 | 1.91 | 0 | 6.14 | 1.91 | 0.04 | available | 8 | SS 110/35/10 kV Maloarkhangelskaya | 10 | 3.075 | 7.305 | 6.14 | 60 | 6.14 | 0 | 6.14 | -1.165 | -1.165 | unavailable
| Nom. capacity MV, MVA | 10 | 1.9 | 1.94 | 60 | 1.94 | 0 | 1.94 | 0.04 |  |  |  | Nom. capacity MV, MVA | 10 | 0.081 | 1.981 | 1.94 | 60 | 1.94 | 0 | 1.94 | -0.041
| Nom. capacity LV, MVA | 10 | 2.33 | 4.2 | 60 | 1.87 | 0 | 4.2 | 1.87 |  |  |  | Nom. capacity LV, MVA | 10 | 2.994 | 5.324 | 4.2 | 60 | 4.2 | 0 | 4.2 | -1.124
9 | SS 110/35/10 kV Novopolevo | 16 | 4.5 | 3.71 | 30 | 3.71 | 0 | 3.71 | -0.79 | -0.79 | unavailable | 9 | SS 110/35/10 kV Novopolevo | 16 | 0.749 | 5.249 | 3.71 | 30 | 3.71 | 0 | 3.71 | -1.539 | -1.539 | unavailable
| Nom. capacity MV, MVA | 16 | 3.2 | 2.6 | 30 | 2.6 | 0 | 2.6 | -0.6 |  |  |  | Nom. capacity MV, MVA | 16 | 0.316 | 3.516 | 2.6 | 30 | 2.6 | 0 | 2.6 | -0.916
| Nom. capacity LV, MVA | 16 | 1.3 | 1.11 | 30 | 1.11 | 0 | 1.11 | -0.19 |  |  |  | Nom. capacity LV, MVA | 16 | 0.433 | 1.733 | 1.11 | 30 | 1.11 | 0 | 1.11 | -0.623
10 | SS 35/10 kV Nikolskaya | 2.5 | 0.51 | 1.33 | 45 | 1.33 | 0 | 1.33 | 0.82 | 0.82 | available | 10 | SS 35/10 kV Nikolskaya | 2.5 | 0.088 | 0.598 | 1.33 | 45 | 1.33 | 0 | 1.33 | 0.732 | 0.732 | available
11 | SS 35/10 kV Paramonovo | 1.8 | 0.34 | 0.48 | 90 | 0.48 | 0 | 0.48 | 0.14 | 0.14 | available | 11 | SS 35/10 kV Paramonovo | 1.8 | 0.127 | 0.467 | 0.48 | 90 | 0.48 | 0 | 0.48 | 0.013 | 0.013 | available
12 | SS 35/10 kV Senkovo | 1.6 | 0.42 | 1.29 | 30 | 1.29 | 0 | 1.29 | 0.87 | 0.87 | available | 12 | SS 35/10 kV Senkovo | 1.6 | 0.134 | 0.554 | 1.29 | 30 | 1.29 | 0 | 1.29 | 0.736 | 0.736 | available
13 | SS 35/10 kV Somovo | 2.5 | 0.34 | 0.96 | 60 | 0.96 | 0 | 0.96 | 0.62 | 0.62 | available | 13 | SS 35/10 kV Somovo | 2.5 | 0.033 | 0.373 | 0.96 | 60 | 0.96 | 0 | 0.96 | 0.587 | 0.587 | available
14 | SS 110/35/10 kV Trosna | 16 | 3.74 | 4.16 | 45 | 4.16 | 0 | 4.16 | 0.42 | -0.3 | unavailable | 14 | SS 110/35/10 kV Trosna | 16 | 0.895 | 4.635 | 4.16 | 45 | 4.16 | 0 | 4.16 | -0.475 | -0.475 | unavailable
| Nom. capacity MV, MVA | 16 | 2.66 | 2.36 | 45 | 2.36 | 0 | 2.36 | -0.3 |  |  |  | Nom. capacity MV, MVA | 16 | 0.076 | 2.736 | 2.36 | 45 | 2.36 | 0 | 2.36 | -0.376
| Nom. capacity LV, MVA | 16 | 1.08 | 1.8 | 45 | 1.8 | 0 | 1.8 | 0.72 |  |  |  | Nom. capacity LV, MVA | 16 | 0.819 | 1.899 | 1.8 | 45 | 1.8 | 0 | 1.8 | -0.099
15 | SS 35/10 kV Shablykino | 5.6 | 0.1 | 0.8 | 90 | 0.8 | 0 | 0.8 | 0.7 | 0.7 | available | 15 | SS 35/10 kV Shablykino | 5.6 | 0 | 0.1 | 0.8 | 90 | 0.8 | 0 | 0.8 | 0.7 | 0.7 | available
16 | SS 35/10 kV Yuryevo | 2.5 | 0.17 | 1.07 | 60 | 1.07 | 0 | 1.07 | 0.9 | 0.9 | available | 16 | SS 35/10 kV Yuryevo | 2.5 | 0.047 | 0.217 | 1.07 | 60 | 1.07 | 0 | 1.07 | 0.853 | 0.853 | available
17 | SS 110/35/10 kV Region V | 10 | 4.48 | 5.4 | 120 | 5.4 | 0 | 5.4 | 0.92 | 0 | available | 17 | SS 110/35/10 kV Region V | 10 | 0.2 | 4.689 | 5.4 | 120 | 5.4 | 0 | 5.4 | 0.711 | 0.711 | available
| Nom. capacity MV, MVA | 10 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | Nom. capacity MV, MVA | 10 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| Nom. capacity LV, MVA | 10 | 4.04 | 5.4 | 120 | 5.4 | 0 | 5.4 | 1.36 |  |  |  | Nom. capacity LV, MVA | 10 | 0.649 | 4.689 | 5.4 | 120 | 5.4 | 0 | 5.4 | 0.711
18 | SS 110/10 kV Pishchevaya | 6.3 | 1.79 | 1.875 | 60 | 1.875 | 0 | 1.875 | 0.085 | 0.085 | available | 18 | SS 110/10 kV Pishchevaya | 6.3 | 2.588 | 4.378 | 1.875 | 60 | 1.875 | 0 | 1.875 | -2.503 | -2.503 | unavailable
19 | SS 110/10 kV Telchye | 3.2 | 1.56 | 1.46 | 120 | 1.46 | 0 | 1.46 | -0.1 | -0.1 | unavailable | 19 | SS 110/10 kV Telchye | 3.2 | 0.078 | 1.638 | 1.46 | 120 | 1.46 | 0 | 1.46 | -0.178 | -0.178 | unavailable
20 | SS 110/10 kV B.Chern | 2.5 | 0.43 | 1 | 120 | 1 | 0 | 1 | 0.57 | 0.57 | available | 20 | SS 110/10 kV B.Chern | 2.5 | 0.272 | 0.702 | 1 | 120 | 1 | 0 | 1 | 0.298 | 0.298 | available
21 | SS 35/10 kV Bashkatovo | 1.6 | 0.46 | 0.8 | 120 | 0.8 | 0 | 0.8 | 0.34 | 0.34 | available | 21 | SS 35/10 kV Bashkatovo | 1.6 | 0.024 | 0.484 | 0.8 | 120 | 0.8 | 0 | 0.8 | 0.316 | 0.316 | available
22 | SS 35/10 kV Vysokoe | 1.6 | 0.2 | 1.24 | 120 | 1.24 | 0 | 1.24 | 1.04 | 1.04 | available | 22 | SS 35/10 kV Vysokoe | 1.6 | 0.026 | 0.226 | 1.24 | 120 | 1.24 | 0 | 1.24 | 1.014 | 1.014 | available
23 | SS 35/10 kV Gladkoe | 2.5 | 0.32 | 1.46 | 120 | 1.46 | 0 | 1.46 | 1.14 | 1.14 | available | 23 | SS 35/10 kV Gladkoe | 2.5 | 0.024 | 0.344 | 1.46 | 120 | 1.46 | 0 | 1.46 | 1.116 | 1.116 | available
24 | SS 35/10 kV Lykovo | 2.5 | 0.72 | 1.24 | 120 | 1.24 | 0 | 1.24 | 0.52 | 0.52 | available | 24 | SS 35/10 kV Lykovo | 2.5 | 0.199 | 0.919 | 1.24 | 120 | 1.24 | 0 | 1.24 | 0.321 | 0.321 | available
25 | SS 35/6 kV Sugar mill | 4 | 0.93 | 1 | 120 | 1 | 0 | 1 | 0.07 | 0.07 | available | 25 | SS 35/6 kV Sugar mill | 4 | 0 | 0.93 | 1 | 120 | 1 | 0 | 1 | 0.07 | 0.07 | available
26 | SS 35/10 kV Gnezdilivo | 1.6 | 0.38 | 0.68 | 120 | 0.68 | 0 | 0.68 | 0.3 | 0.3 | available | 26 | SS 35/10 kV Gnezdilivo | 1.6 | 0.014 | 0.394 | 0.68 | 120 | 0.68 | 0 | 0.68 | 0.286 | 0.286 | available
27 | SS 35/10 kV Koptevo | 2.5 | 0.24 | 0.44 | 120 | 0.44 | 0 | 0.44 | 0.2 | 0.2 | available | 27 | SS 35/10 kV Koptevo | 2.5 | 0 | 0.24 | 0.44 | 120 | 0.44 | 0 | 0.44 | 0.2 | 0.2 | available
28 | SS 110/35/10/6 kV Meat processing factory | 10 | 1.89 | 2.13 | 120 | 2.13 | 0 | 2.13 | 0.24 | 0 | available | 28 | SS 110/35/10/6 kV Meat processing factory | 10 | 0.012 | 1.909 | 2.13 | 120 | 2.13 | 0 | 2.13 | 0.221 | 0.221 | available
| Nom. capacity MV, MVA | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | Nom. capacity MV, MVA | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Nom. capacity LV, MVA | 10 | 1.89 | 2.13 | 120 | 2.13 | 0 | 2.13 | 0.24 |  |  |  | Nom. capacity LV, MVA | 10 | 0.019 | 1.909 | 2.13 | 120 | 2.13 | 0 | 2.13 | 0.221
29 | SS 110/35/10 kV Shatilovo | 10 | 1.21 | 0.69 | 120 | 0.69 | 0 | 0.69 | -0.52 | -0.52 | unavailable | 29 | SS 110/35/10 kV Shatilovo | 10 | 0.005 | 1.312 | 0.69 | 120 | 0.69 | 0 | 0.69 | -0.622 | -0.622 | unavailable
| Nom. capacity MV, MVA | 10 | 0.52 | 0.16 | 180 | 0.16 | 0 | 0.16 | -0.36 |  |  |  | Nom. capacity MV, MVA | 10 | 0.059 | 0.579 | 0.16 | 180 | 0.16 | 0 | 0.16 | -0.419
| Nom. capacity LV, MVA | 10 | 0.68 | 0.53 | 120 | 0.53 | 0 | 0.53 | -0.15 |  |  |  | Nom. capacity LV, MVA | 10 | 0.053 | 0.733 | 0.53 | 120 | 0.53 | 0 | 0.53 | -0.203
30 | SS 110/35/10 kV Sovkhoznaya | 10 | 3.33 | 8.96 | 120 | 8.96 | 0 | 8.96 | 5.63 | 1.06 | available | 30 | SS 110/35/10 kV Sovkhoznaya | 10 | 2.101 | 5.441 | 8.96 | 120 | 8.96 | 0 | 8.96 | 3.519 | 0.975 | available
| Nom. capacity MV, MVA | 10 | 2.06 | 6.62 | 120 | 6.62 | 0 | 6.62 | 4.56 |  |  |  | Nom. capacity MV, MVA | 10 | 2.016 | 4.076 | 6.62 | 120 | 6.62 | 0 | 6.62 | 2.544
| Nom. capacity LV, MVA | 10 | 1.28 | 2.34 | 120 | 2.34 | 0 | 2.34 | 1.06 |  |  |  | Nom. capacity LV, MVA | 10 | 0.085 | 1.365 | 2.34 | 120 | 2.34 | 0 | 2.34 | 0.975
31 | SS 35/10 kV Danilovskaya | 1.6 | 0.28 | 0.54 | 120 | 0.54 | 0 | 0.54 | 0.26 | 0.26 | available | 31 | SS 35/10 kV Danilovskaya | 1.6 | 0 | 0.28 | 0.54 | 120 | 0.54 | 0 | 0.54 | 0.26 | 0.26 | available
32 | SS 35/10 kV Korseevo | 1.8 | 0.04 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.84 | 0.84 | available | 32 | SS 35/10 kV Korseevo | 1.8 | 0 | 0.04 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.84 | 0.84 | available
33 | SS 35/10 kV Lipovets | 2.5 | 0.74 | 1.39 | 120 | 1.39 | 0 | 1.39 | 0.65 | 0.65 | available | 33 | SS 35/10 kV Lipovets | 2.5 | 0.316 | 1.056 | 1.39 | 120 | 1.39 | 0 | 1.39 | 0.334 | 0.334 | available
34 | SS 35/10 kV Misaylovo | 1.6 | 0.3 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.3 | 1.3 | available | 34 | SS 35/10 kV Misaylovo | 1.6 | 0.012 | 0.312 | 1.6 |  | 1.6 | 0 | 1.6 | 1.288 | 1.288 | available
35 | SS 35/10 kV Mikhaylovka | 2.5 | 0.26 | 0.31 | 80 | 0.31 | 0 | 0.31 | 0.05 | 0.05 | available | 35 | SS 35/10 kV Mikhaylovka | 2.5 | 0.009 | 0.269 | 0.31 | 80 | 0.31 | 0 | 0.31 | 0.041 | 0.041 | available
36 | SS 35/10 kV Pankovo | 1.8 | 0.52 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.08 | 1.08 | available | 36 | SS 35/10 kV Pankovo | 1.8 | 0.059 | 0.579 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.021 | 1.021 | available
37 | SS 35/10 kV Sudbishchi | 2.5 | 0.65 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 0.95 | 0.95 | available | 37 | SS 35/10 kV Sudbishchi | 2.5 | 0.015 | 0.665 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 0.935 | 0.935 | available
38 | SS 35/10 kV Tim | 1.6 | 0.52 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.08 | 1.08 | available | 38 | SS 35/10 kV Tim | 1.6 | 0.006 | 0.526 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.074 | 1.074 | available
39 | SS 35/10 kV Topki | 1 | 0.19 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.41 | 1.41 | available | 39 | SS 35/10 kV Topki | 1 | 0.051 | 0.241 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.359 | 1.359 | available
40 | SS 35/10 kV Yarishche | 2.5 | 0.29 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.31 | 1.31 | available | 40 | SS 35/10 kV Yarishche | 2.5 | 0.032 | 0.322 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.278 | 1.278 | available
41 | SS 110/10 kV Alshanskaya | 10+10 | 4.06 | 3.88 | 30 | 0.18 | 0 | 10.5 | 10.32 | 10.32 | available | 41 | SS 110/10 kV Alshanskaya | 10+10 | 0.556 | 4.616 | 3.88 | 30 | 0.736 | 0 | 10.5 | 9.764 | 9.764 | available
42 | SS 35/10 kV Arkhangelskaya | 2,5+2,5 | 0.4 | 0.93 | 90 | -0.53 | 0 | 2.625 | 3.155 | 3.155 | available | 42 | SS 35/10 kV Arkhangelskaya | 2,5+2,5 | 0.018 | 0.418 | 0.93 | 90 | -0.512 | 0 | 2.625 | 3.137 | 3.137 | available
43 | SS 35/10 kV Atyaevskaya | 1,6+2,5 | 0.7 | 0 | - | 0.7 | 0 | 1.68 | 0.98 | 0.98 | available | 43 | SS 35/10 kV Atyaevskaya | 1,6+2,5 | 0.394 | 1.094 | 0 |  | 1.094 | 0 | 1.68 | 0.586 | 0.586 | available
44 | SS 110/35/10 kV Bogoroditskaya | 10+10 | 2.64 | 3.06 | 90 | -0.42 | 0 | 10.5 | 10.92 | 10.51 | available | 44 | SS 110/35/10 kV Bogoroditskaya | 10+10 | 0.811 | 3.451 | 3.06 | 90 | 0.391 | 0 | 10.5 | 10.109 | 10.109 | available
| Nom. capacity MV, MVA | 10+10 | 2.42 | 2.43 | 90 | -0.01 | 0 | 10.5 | 10.51 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.811 | 3.231 | 2.43 | 90 | 0.801 | 0 | 10.5 | 9.699
| Nom. capacity LV, MVA | 10+10 | 0.22 | 0.63 | 90 | -0.41 | 0 | 10.5 | 10.91 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0 | 0.22 | 0.63 | 90 | -0.41 | 0 | 10.5 | 10.91
45 | SS 35/10 kV Baklanovo | 1,6+1,6 | 1.01 | 0.64 | 60 | 0.37 | 0 | 1.68 | 1.31 | 1.31 | available | 45 | SS 35/10 kV Baklanovo | 1,6+1,6 | 0.316 | 1.326 | 0.64 | 60 | 0.686 | 0 | 1.68 | 0.994 | 0.994 | available
46 | SS 35/10 kV Biofactory | 6,3+6,3 | 3.07 | 2.05 | 90 | 1.02 | 0 | 6.615 | 5.595 | 5.595 | available | 46 | SS 35/10 kV Biofactory | 6,3+6,3 | 0.464 | 3.534 | 2.05 | 90 | 1.484 | 0 | 6.615 | 5.131 | 5.131 | available
47 | SS 110/10 kV Volodarskaya | 2,5+6,3 | 3.19 | 1.46 | 30 | 1.73 | 0 | 2.625 | 0.895 | 0.895 | available | 47 | SS 110/10 kV Volodarskaya | 2,5+6,3 | 4.009 | 7.199 | 1.46 | 30 | 5.739 | 0 | 2.625 | -3.114 | -3.114 | unavailable
48 | SS 110/10 kV Vostochnaya | 15+15 | 13.63 | 5.87 | 120 | 7.76 | 0 | 15.75 | 7.99 | 7.99 | available | 48 | SS 110/10 kV Vostochnaya | 15+15 | 0.659 | 14.289 | 5.87 | 120 | 8.419 |  | 15.75 | 7.331 | 7.331 | available
49 | SS 110/35/10 kV Dmitrovskaya | 10+10 | 3.26 | 0.45 | 60 | 2.81 | 0 | 10.5 | 7.69 | 7.69 | available | 49 | SS 110/35/10 kV Dmitrovskaya | 10+10 | 0.228 | 3.488 | 0.45 | 60 | 3.038 | 0 | 10.5 | 7.462 | 7.462 | available
| Nom. capacity MV, MVA | 10+10 | 0.25 | 0 | 0 | 0.25 | 0 | 10.5 | 10.25 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.012 | 0.262 | 0 |  | 0.262 | 0 | 10.5 | 10.238
| Nom. capacity LV, MVA | 10+10 | 3.01 | 0.45 | 60 | 2.56 | 0 | 10.5 | 7.94 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.216 | 3.226 | 0.45 | 60 | 2.776 | 0 | 10.5 | 7.724
50 | SS 110/10 kV Zheleznodorozhnaya | 16+16 | 11.84 | 3.98 | 180 | 7.86 | 0 | 16.8 | 8.94 | 8.94 | available | 50 | SS 110/10 kV Zheleznodorozhnaya | 16+16 | 0.382 | 12.222 | 3.98 | 180 | 8.242 | 0 | 16.8 | 8.558 | 8.558 | available
51 | SS 35/10 kV Zhilyaevskaya | 1,8+1,8 | 0.98 | 0.64 | 60 | 0.34 | 0 | 1.89 | 1.55 | 1.55 | available | 51 | SS 35/10 kV Zhilyaevskaya | 1,8+1,8 | 0.019 | 0.999 | 0.64 | 60 | 0.359 | 0 | 1.89 | 1.531 | 1.531 | available
52 | SS 110/6 kV Zavodskaya | 40+25 | 11.83 | 4.39 | 150 | 7.44 | 0 | 26.25 | 18.81 | 18.81 | available | 52 | SS 110/6 kV Zavodskaya | 40+25 | 1.612 | 13.442 | 4.39 | 150 | 9.052 | 0 | 26.25 | 17.198 | 17.198 | available
53 | SS 110/6 kV Zapadnaya | 63+63 | 25.39 | 5.37 | 120 | 20.02 | 19 | 66.15 | 27.13 | 27.13 | available | 53 | SS 110/6 kV Zapadnaya | 63+63 | 15.235 | 40.625 | 5.37 | 120 | 35.255 | 19 | 66.15 | 11.895 | 11.895 | available
54 | SS 35/10 kV Zvyaginki | 2,5+2,5 | 1.87 | 1.48 | 60 | 0.39 | 0 | 2.625 | 2.235 | 2.235 | available | 54 | SS 35/10 kV Zvyaginki | 2,5+2,5 | 1.181 | 3.051 | 1.48 | 60 | 1.571 | 0 | 2.625 | 1.054 | 1.054 | available
55 | SS 35/10 kV Ilyinskaya | 3,2+1,6 | 0.84 | 1.18 | 30 | -0.34 | 0 | 1.68 | 2.02 | 2.02 | available | 55 | SS 35/10 kV Ilyinskaya | 3,2+1,6 | 0.153 | 0.993 | 1.18 | 30 | -0.187 | 0 | 1.68 | 1.867 | 1.867 | available
56 | SS 110/35/10 kV Kulikovskaya | 10+10 | 5.59 | 1.44 | 90 | 4.15 | 0 | 10.5 | 6.35 | 6.35 | available | 56 | SS 110/35/10 kV Kulikovskaya | 10+10 | 6.623 | 12.213 | 1.44 | 90 | 10.773 | 0 | 10.5 | -0.273 | -0.273 | unavailable
| Nom. capacity MV, MVA | 10+10 | 1.76 | 1 | 90 | 0.76 | 0 | 10.5 | 9.74 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.715 | 2.475 | 1 | 90 | 1.475 | 0 | 10.5 | 9.025
| Nom. capacity LV, MVA | 10+10 | 3.83 | 0.44 | 90 | 3.39 | 0 | 10.5 | 7.11 |  |  |  | Nom. capacity LV, MVA | 10+10 | 5.908 | 9.738 | 0.44 | 90 | 9.298 | 0 | 10.5 | 1.202
57 | SS 110/35/10 kV Kromskaya | 16+16 | 6.68 | 6.83 | 45 | -0.15 | 0 | 16.8 | 16.95 | 15.28 | available | 57 | SS 110/35/10 kV Kromskaya | 16+16 | 7.07 | 13.75 | 6.83 | 45 | 6.92 | 0 | 16.8 | 9.88 | 9.88 | available
| Nom. capacity MV, MVA | 16+16 | 3.33 | 5 | 45 | -1.67 | 0 | 16.8 | 18.47 |  |  |  | Nom. capacity MV, MVA | 16+16 | 6.478 | 9.808 | 5 | 45 | 4.808 | 0 | 16.8 | 11.992
| Nom. capacity LV, MVA | 16+16 | 3.35 | 1.83 | 45 | 1.52 | 0 | 16.8 | 15.28 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.592 | 3.942 | 1.83 | 45 | 2.112 | 0 | 16.8 | 14.688
58 | SS 35/10 kV Krasnoarmeyskaya | 2,5+2,5 | 1.63 | 0.95 | 30 | 0.68 | 0 | 2.625 | 1.945 | 1.945 | available | 58 | SS 35/10 kV Krasnoarmeyskaya | 2,5+2,5 | 0.076 | 1.706 | 0.95 | 30 | 0.756 | 0 | 2.625 | 1.869 | 1.869 | available
59 | SS 35/10 kV Kurakinskaya | 1,6+1,8 | 0.56 | 0 | - | 0.56 | 0 | 1.68 | 1.12 | 1.12 | available | 59 | SS 35/10 kV Kurakinskaya | 1,6+1,8 | 0.02 | 0.58 | 0 |  | 0.58 | 0 | 1.68 | 1.1 | 1.1 | available
60 | SS 35/10 kV Kutafino | 1,6+1,6 | 0.66 | 0.83 | 30 | -0.17 | 0 | 1.68 | 1.85 | 1.85 | available | 60 | SS 35/10 kV Kutafino | 1,6+1,6 | 5.905 | 6.565 | 0.83 | 30 | 5.735 | 0 | 1.68 | -4.055 | -4.055 | unavailable
61 | SS 35/10 kV Lovchikovo | 2,5+2,5 | 0.89 | 1.59 | 30 | -0.7 | 0 | 2.625 | 3.325 | 3.325 | available | 61 | SS 35/10 kV Lovchikovo | 2,5+2,5 | 0.127 | 1.017 | 1.59 | 30 | -0.573 | 0 | 2.625 | 3.198 | 3.198 | available
62 | SS 35/10 kV Lubyanskaya | 1+1,6 | 0.48 | 0.47 | 60 | 0.01 | 0 | 1.05 | 1.04 | 1.04 | available | 62 | SS 35/10 kV Lubyanskaya | 1+1,6 | 0.02 | 0.5 | 0.47 | 60 | 0.03 | 0 | 1.05 | 1.02 | 1.02 | available
63 | SS 35/10 kV Lukovets | 1,8+2,5 | 0.33 | 0.99 | 90 | -0.66 | 0 | 1.89 | 2.55 | 2.55 | available | 63 | SS 35/10 kV Lukovets | 1,8+2,5 | 0.024 | 0.354 | 0.99 | 90 | -0.636 | 0 | 1.89 | 2.526 | 2.526 | available
64 | SS 35/10 kV Malorkhangelskaya | 5,6+5,6 | 0.47 | 1.7 | 30 | -1.23 | 0 | 5.88 | 7.11 | 7.11 | available | 64 | SS 35/10 kV Malorkhangelskaya | 5,6+5,6 | 1.088 | 1.558 | 1.7 | 30 | -0.142 | 0 | 5.88 | 6.022 | 6.022 | available
65 | SS 110/35/10 kV Naryshkinskaya | 10+10 | 9.2 | 1.41 | 90 | 7.79 | 0 | 10.5 | 2.71 | 2.71 | available | 65 | SS 110/35/10 kV Naryshkinskaya | 10+10 | 1.045 | 10.245 | 1.41 | 90 | 8.835 | 0 | 10.5 | 1.665 | 1.665 | available
| Nom. capacity MV, MVA | 10+10 | 2.76 | 0.86 | 90 | 1.9 | 0 | 10.5 | 8.6 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.147 | 2.907 | 0.86 | 90 | 2.047 | 0 | 10.5 | 8.453
| Nom. capacity LV, MVA | 10+10 | 6.44 | 0.55 | 90 | 5.89 | 0 | 10.5 | 4.61 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.898 | 7.338 | 0.55 | 90 | 6.788 | 0 | 10.5 | 3.712
66 | SS 35/10 kV Nizhnyaya Sloboda | 2,5+5,6 | 0.68 | 1.63 | 45 | -0.95 | 0 | 2.625 | 3.575 | 3.575 | available | 66 | SS 35/10 kV Nizhnyaya Sloboda | 2,5+5,6 | 0.035 | 0.715 | 1.63 | 45 | -0.915 | 0 | 2.625 | 3.54 | 3.54 | available
67 | SS 35/10 kV Novopetrovka | 2,5+1,6 | 0.52 | 0.73 | 60 | -0.21 | 0 | 1.68 | 1.89 | 1.89 | available | 67 | SS 35/10 kV Novopetrovka | 2,5+1,6 | 0.066 | 0.586 | 0.73 | 60 | -0.144 | 0 | 1.68 | 1.824 | 1.824 | available
68 | SS 35/10 kV Putimets | 2,5+2,5 | 1.31 | 1.53 | 90 | -0.22 | 0 | 2.625 | 2.845 | 2.845 | available | 68 | SS 35/10 kV Putimets | 2,5+2,5 | 0.193 | 1.503 | 1.53 | 90 | -0.027 | 0 | 2.625 | 2.652 | 2.652 | available
69 | SS 110/10 kV Pishchevaya* | 40+25 | 5.38 | 2.22 | 60 | 3.16 | 0 | 26.25 | 23.09 | 23.09 | available | 69 | SS 110/10 kV Pishchevaya* | 40+25 | 0.374 | 5.754 | 2.22 | 60 | 3.534 | 0 | 26.25 | 22.716 | 22.716 | available
70 | SS 35/10 kV Ryzhkovo | 2,5+2,5 | 0.43 | 0.65 | 90 | -0.22 | 0 | 2.625 | 2.845 | 2.845 | available | 70 | SS 35/10 kV Ryzhkovo | 2,5+2,5 | 0.051 | 0.481 | 0.65 | 90 | -0.169 | 0 | 2.625 | 2.794 | 2.794 | available
71 | SS 110/35/10 kV Sverdlovskaya | 10+10 | 2.69 | 1.98 | 45 | 0.71 | 0 | 10.5 | 9.79 | 9.74 | available | 71 | SS 110/35/10 kV Sverdlovskaya | 10+10 | 0.879 | 3.569 | 1.98 | 45 | 1.589 | 0 | 10.5 | 8.911 | 8.911 | available
| Nom. capacity MV, MVA | 10+10 | 1.36 | 1.41 | 45 | -0.05 | 0 | 10.5 | 10.55 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.225 | 1.585 | 1.41 | 45 | 0.175 | 0 | 10.5 | 10.325
| Nom. capacity LV, MVA | 10+10 | 1.33 | 0.57 | 45 | 0.76 | 0 | 10.5 | 9.74 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.654 | 1.984 | 0.57 | 45 | 1.414 | 0 | 10.5 | 9.086
72 | SS 35/10 kV Streletskaya | 4+4 | 1.66 | 0.91 | 90 | 0.75 | 0 | 4.2 | 3.45 | 3.45 | available | 72 | SS 35/10 kV Streletskaya | 4+4 | 1.869 | 3.529 | 0.91 | 90 | 2.619 | 0 | 4.2 | 1.581 | 1.581 | available
73 | SS 110/35/10/6 kV Sovetskaya | 20+20+25+40 | 27.61 | 3.86 | 180 | 23.75 | 0 | 68.25 | 44.5 | 19.36 | available | 73 | SS 110/35/10/6 kV Sovetskaya | 20+20+25+40 | 9.153 | 29.433 | 3.86 | 180 | 25.573 | 0 | 68.25 | 42.677 | 16.565 | available
| Nom. capacity MV -35kV; MVA | 20+20 | 6.74 | 5.1 | 90 | 1.64 | 0 | 21 | 19.36 |  |  |  | Nom. capacity MV -35kV; MVA | 20+20 | 2.795 | 9.535 | 5.1 | 90 | 4.435 | 0 | 21 | 16.565
| Nom. capacity LV-10kV; MVA | 25+40 | 7.53 | 3 | 180 | 4.53 | 0 | 26.25 | 21.72 |  |  |  | Nom. capacity LV-10kV; MVA | 25+40 | 0 | 7.53 | 3 | 180 | 4.53 | 0 | 26.25 | 21.72
| Nom. capacity LV-6kV; MVA | 20+20+40 | 13.54 | 3.86 | 180 | 9.68 | 0 | 42 | 32.32 |  |  |  | Nom. capacity LV-6kV; MVA | 20+20+40 | 6.358 | 19.898 | 3.86 | 180 | 16.038 | 0 | 42 | 25.962
74 | SS 35/10 kV Soskovskaya | 4+3,2 | 1.13 | 0.64 | 90 | 0.49 | 0 | 3.36 | 2.87 | 2.87 | available | 74 | SS 35/10 kV Soskovskaya | 4+3,2 | 0.049 | 1.179 | 0.64 | 90 | 0.539 | 0 | 3.36 | 2.821 | 2.821 | available
75 | SS 35/10 kV Trosna | 5,6+3,2 | 0.69 | 1.76 | 30 | -1.07 | 0 | 3.36 | 4.43 | 4.43 | available | 75 | SS 35/10 kV Trosna | 5,6+3,2 | 0.045 | 0.735 | 1.76 | 30 | -1.025 | 0 | 3.36 | 4.385 | 4.385 | available
76 | SS 110/10 kV Khimmash | 25+25 | 6.32 | 1.51 | 120 | 4.81 | 0 | 26.25 | 21.44 | 21.44 | available | 76 | SS 110/10 kV Khimmash | 25+25 | 7.694 | 14.014 | 1.51 | 120 | 12.504 | 0 | 26.25 | 13.746 | 13.746 | available
77 | SS 35/10kV Khleboprodukty | 5,6+6,3 | 0.97 | 0 | - | 0.97 | 0 | 5.88 | 4.91 | 4.91 | available | 77 | SS 35/10kV Khleboprodukty | 5,6+6,3 | 0 | 0.97 | 0 |  | 0.97 | 0 | 5.88 | 4.91 | 4.91 | available
78 | SS 35/10 kV Khotynetskaya | 4+2,5 | 2.2 | 1.49 | 80 | 0.71 | 0 | 2.625 | 1.915 | 1.915 | available | 78 | SS 35/10 kV Khotynetskaya | 4+2,5 | 0.764 | 2.964 | 1.49 | 80 | 1.474 | 0 | 2.625 | 1.151 | 1.151 | available
79 | SS 35/10 kV Khotkovo | 1,6+1,6 | 0.58 | 1.03 | 80 | -0.45 | 0 | 1.68 | 2.13 | 2.13 | available | 79 | SS 35/10 kV Khotkovo | 1,6+1,6 | 0.064 | 0.644 | 1.03 | 80 | -0.386 | 0 | 1.68 | 2.066 | 2.066 | available
80 | SS 110/10/6 kV Tsentralnaya | 25+25 | 12.48 | 3.46 | 135 | 9.02 | 0 | 26.25 | 17.23 | 17.23 | available | 80 | SS 110/10/6 kV Tsentralnaya | 25+25 | 1.529 | 14.009 | 3.46 | 135 | 10.549 | 0 | 26.25 | 15.701 | 15.701 | available
81 | SS 110/35/10 kV Shablykino | 6,3+6,3 | 2.68 | 1.36 | 30 | 1.32 | 0 | 6.615 | 5.295 | 5.295 | available | 81 | SS 110/35/10 kV Shablykino | 6,3+6,3 | 0.115 | 2.795 | 1.36 | 30 | 1.435 | 0 | 6.615 | 5.18 | 5.18 | available
| Nom. capacity MV, MVA | 6,3+6,3 | 1.08 | 0.54 | 30 | 0.54 | 0 | 6.615 | 6.075 |  |  |  | Nom. capacity MV, MVA | 6,3+6,3 | 0.097 | 1.177 | 0.54 | 30 | 0.637 | 0 | 6.615 | 5.978
| Nom. capacity LV, MVA | 6,3+6,3 | 1.6 | 0.82 | 30 | 0.78 | 0 | 6.615 | 5.835 |  |  |  | Nom. capacity LV, MVA | 6,3+6,3 | 0.018 | 1.618 | 0.82 | 30 | 0.798 | 0 | 6.615 | 5.817
82 | SS 110/35/10 kV Shakhovo | 10+10 | 4.21 | 2.55 | 120 | 1.66 | 0 | 10.5 | 8.84 | 8.84 | available | 82 | SS 110/35/10 kV Shakhovo | 10+10 | 4.348 | 8.558 | 2.55 | 120 | 6.008 | 0 | 10.5 | 4.492 | 4.492 | available
| Nom. capacity MV, MVA | 10+10 | 1.33 | 0.39 | 120 | 0.94 | 0 | 10.5 | 9.56 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.193 | 1.523 | 0.39 | 120 | 1.133 | 0 | 10.5 | 9.367
| Nom. capacity LV, MVA | 10+10 | 2.88 | 2.16 | 120 | 0.72 | 0 | 10.5 | 9.78 |  |  |  | Nom. capacity LV, MVA | 10+10 | 4.155 | 7.035 | 2.16 | 120 | 4.875 | 0 | 10.5 | 5.625
83 | SS 35/10 kV Shepino | 2,5+1,6 | 1.6 | 1.1 | 120 | 0.5 | 0 | 1.68 | 1.18 | 1.18 | available | 83 | SS 35/10 kV Shepino | 2,5+1,6 | 0.715 | 2.315 | 1.1 | 120 | 1.215 | 0 | 1.68 | 0.465 | 0.465 | available
84 | SS 110/10/6 kV Yugo-Vostochnaya | 25+25 | 9.8 | 0.74 | 60 | 9.06 | 0 | 26.25 | 17.19 | 17.19 | available | 84 | SS 110/10/6 kV Yugo-Vostochnaya | 25+25 | 1.647 | 11.447 | 0.74 | 60 | 10.707 | 0 | 26.25 | 15.543 | 15.543 | available
85 | SS 110/10 kV Yuzhnaya | 10+10 | 7.42 | 1.05 | 90 | 6.37 | 0 | 10.5 | 4.13 | 4.13 | available | 85 | SS 110/10 kV Yuzhnaya | 10+10 | 2.053 | 9.473 | 1.05 | 90 | 8.423 | 0 | 10.5 | 2.077 | 2.077 | available
86 | SS 220/110/10 kV Mtsensk | 40+40 | 9.57 | 0 | - | 9.57 | 0 | 42 | 32.43 | 32.43 | available | 86 | SS 220/110/10 kV Mtsensk | 40+40 | 0.529 | 10.099 | 0 |  | 10.099 | 0 | 42 | 31.901 | 31.901 | available
87 | SS 110/35/10 kV Kommash | 10+16 | 10.26 | 4.65 | 90 | 5.61 | 0 | 10.5 | 4.89 | 4.89 | available | 87 | SS 110/35/10 kV Kommash | 10+16 | 4.596 | 14.856 | 4.65 | 90 | 10.206 | 0 | 10.5 | 0.294 | 0.294 | available
| Nom. capacity MV, MVA | 10+16 | 0 | 0 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, MVA | 10+16 | 0 | 0 | 0 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, MVA | 10+16 | 10.26 | 4.65 | 90 | 5.61 | 0 | 10.5 | 4.89 |  |  |  | Nom. capacity LV, MVA | 10+16 | 4.596 | 14.856 | 4.65 | 90 | 10.206 | 0 | 10.5 | 0.294
88 | SS 110/35/10 kV Novosergievka | 6,3+10 | 1.84 | 4.13 | 120 | -2.29 | 0 | 6.615 | 8.905 | 7.365 | available | 88 | SS 110/35/10 kV Novosergievka | 6,3+10 | 0.332 | 2.142 | 4.13 | 120 | -1.988 | 0 | 6.615 | 8.603 | 7.033 | available
| Nom. capacity MV, MVA | 6,3+10 | 1.65 | 2.4 | 120 | -0.75 | 0 | 6.615 | 7.365 |  |  |  | Nom. capacity MV, MVA | 6,3+10 | 0.332 | 1.982 | 2.4 | 120 | -0.418 | 0 | 6.615 | 7.033
| Nom. capacity LV, MVA | 6,3+10 | 0.16 | 1.73 | 120 | -1.57 | 0 | 6.615 | 8.185 |  |  |  | Nom. capacity LV, MVA | 6,3+10 | 0 | 0.16 | 1.73 | 120 | -1.57 | 0 | 6.615 | 8.185
89 | SS 110/10 kV 1 Voin | 6,3+6,3 | 2.52 | 1.83 | 120 | 0.69 | 0 | 6.615 | 5.925 | 5.925 | available | 89 | SS 110/10 kV 1 Voin | 6,3+6,3 | 0.576 | 3.096 | 1.83 | 120 | 1.266 | 0 | 6.615 | 5.349 | 5.349 | available
90 | SS 110/35/10 kV Zalegoshch | 10+16 | 6 | 3.95 | 120 | 2.05 | 0 | 10.5 | 8.45 | 8.45 | available | 90 | SS 110/35/10 kV Zalegoshch | 10+16 | 0.243 | 6.243 | 3.95 | 120 | 2.293 | 0 | 10.5 | 8.207 | 8.207 | available
| Nom. capacity MV, MVA | 10+16 | 2.71 | 2.39 | 120 | 0.32 | 0 | 10.5 | 10.18 |  |  |  | Nom. capacity MV, MVA | 10+16 | 0.11 | 2.82 | 2.39 | 120 | 0.43 | 0 | 10.5 | 10.07
| Nom. capacity LV, MVA | 10+16 | 3.29 | 1.56 | 120 | 1.73 | 0 | 10.5 | 8.77 |  |  |  | Nom. capacity LV, MVA | 10+16 | 0.133 | 3.423 | 1.56 | 120 | 1.863 | 0 | 10.5 | 8.637
91 | SS 110/10 kV Kochety | 2,5+2,5 | 0.26 | 0.66 | 120 | -0.4 | 0 | 2.625 | 3.025 | 3.025 | available | 91 | SS 110/10 kV Kochety | 2,5+2,5 | 0.029 | 0.289 | 0.66 | 120 | -0.371 | 0 | 2.625 | 2.996 | 2.996 | available
92 | SS 110/35/10 kV Bolkhov | 10+10 | 7.69 | 4.1 | 120 | 3.59 | 0 | 10.5 | 6.91 | 6.88 | available | 92 | SS 110/35/10 kV Bolkhov | 10+10 | 0.476 | 8.156 | 4.1 | 120 | 4.056 | 0 | 10.5 | 6.444 | 6.444 | available
| Nom. capacity MV, MVA | 10+10 | 2.41 | 2.45 | 120 | -0.04 | 0 | 10.5 | 10.54 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.391 | 2.801 | 2.45 | 120 | 0.351 | 0 | 10.5 | 10.149
| Nom. capacity LV, MVA | 10+10 | 5.27 | 1.65 | 120 | 3.62 | 0 | 10.5 | 6.88 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.085 | 5.355 | 1.65 | 120 | 3.705 | 0 | 10.5 | 6.795
93 | SS 110/35/10 kV Novosil | 10+10 | 4.98 | 2.98 | 120 | 2 | 0 | 10.5 | 8.5 | 8.5 | available | 93 | SS 110/35/10 kV Novosil | 10+10 | 0.193 | 5.213 | 2.98 | 120 | 2.233 | 0 | 10.5 | 8.267 | 8.267 | available
| Nom. capacity MV, MVA | 10+10 | 2.53 | 1.46 | 120 | 1.07 | 0 | 10.5 | 9.43 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.095 | 2.625 | 1.46 | 120 | 1.165 | 0 | 10.5 | 9.335
| Nom. capacity LV, MVA | 10+10 | 2.49 | 1.52 | 120 | 0.97 | 0 | 10.5 | 9.53 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.098 | 2.588 | 1.52 | 120 | 1.068 | 0 | 10.5 | 9.432
94 | SS 110/35/10 kV Znamenskaya | 10+10 | 2.14 | 1.78 | 120 | 0.36 | 0 | 10.5 | 10.14 | 10.14 | available | 94 | SS 110/35/10 kV Znamenskaya | 10+10 | 0.107 | 2.207 | 1.78 | 120 | 0.427 | 0 | 10.5 | 10.073 | 10.073 | available
| Nom. capacity MV, MVA | 10+10 | 0.39 | 0.34 | 120 | 0.05 | 0 | 10.5 | 10.45 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.016 | 0.406 | 0.34 | 120 | 0.066 | 0 | 10.5 | 10.434
| Nom. capacity LV, MVA | 10+10 | 1.71 | 1.44 | 120 | 0.27 | 0 | 10.5 | 10.23 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.091 | 1.801 | 1.44 | 120 | 0.361 | 0 | 10.5 | 10.139
95 | SS 35/10 kV Apalkovo | 1,8+1,8 | 0.29 | 0.48 | 120 | -0.19 | 0 | 1.89 | 2.08 | 2.08 | available | 95 | SS 35/10 kV Apalkovo | 1,8+1,8 | 0.021 | 0.311 | 0.48 | 120 | -0.169 | 0 | 1.89 | 2.059 | 2.059 | available
96 | SS 35/10 kV Podberyozovo | 4+1 | 0.14 | 0.59 | 120 | -0.45 | 0 | 1.05 | 1.5 | 1.5 | available | 96 | SS 35/10 kV Podberyozovo | 4+1 | 0.016 | 0.156 | 0.59 | 120 | -0.434 | 0 | 1.05 | 1.484 | 1.484 | available
97 | SS 35/10 kV Protasovo | 2,5+1,6 | 0.54 | 0 |  | 0.54 | 0 | 1.68 | 1.14 | 1.14 | available | 97 | SS 35/10 kV Protasovo | 2,5+1,6 | 0.018 | 0.558 | 0 |  | 0.558 | 0 | 1.68 | 1.122 | 1.122 | available
98 | SS 35/10 kV Alyoshnya | 1+1 | 0.34 | 0.24 | 120 | 0.1 | 0 | 1.05 | 0.95 | 0.95 | available | 98 | SS 35/10 kV Alyoshnya | 1+1 | 0.034 | 0.374 | 0.24 | 120 | 0.134 | 0 | 1.05 | 0.916 | 0.916 | available
99 | SS 35/10 kV Lomovoe | 2,5+2,5 | 1.25 | 0 | - | 1.25 | 0 | 2.625 | 1.375 | 1.375 | available | 99 | SS 35/10 kV Lomovoe | 2,5+2,5 | 0.029 | 1.279 | 0 |  | 1.279 | 0 | 2.625 | 1.346 | 1.346 | available
100 | SS 35/10 kV Mokhovoe | 2,5+4 | 0.89 | 0.63 | 120 | 0.26 |  | 2.625 | 2.365 | 2.365 | available | 100 | SS 35/10 kV Mokhovoe | 2,5+4 | 0.047 | 0.937 | 0.63 | 120 | 0.307 | 0 | 2.625 | 2.318 | 2.318 | available
101 | SS 35/10 kV Mishkovo 2 | 1,6+1,6 | 0.23 | 0.47 | 120 | -0.24 | 0 | 1.68 | 1.92 | 1.92 | available | 101 | SS 35/10 kV Mishkovo 2 | 1,6+1,6 | 0 | 0.23 | 0.47 | 120 | -0.24 | 0 | 1.68 | 1.92 | 1.92 | available
102 | SS 35/10 kV Vyazovoe | 2,5+2,5 | 0.33 | 0 | - | 0.33 | 0 | 2.625 | 2.295 | 2.295 | available | 102 | SS 35/10 kV Vyazovoe | 2,5+2,5 | 0.042 | 0.372 | 0 |  | 0.372 | 0 | 2.625 | 2.253 | 2.253 | available
103 | SS 35/10 kV Krasnoznamenka | 2,5+2,5 | 0.66 | 0.67 | 120 | -0.01 | 0 | 2.625 | 2.635 | 2.635 | available | 103 | SS 35/10 kV Krasnoznamenka | 2,5+2,5 | 0.222 | 0.882 | 0.67 | 120 | 0.212 | 0 | 2.625 | 2.413 | 2.413 | available
104 | SS 35/10 kV Fatnevo | 1,6+1,6 | 0.59 | 0.37 | 120 | 0.22 | 0 | 1.68 | 1.46 | 1.46 | available | 104 | SS 35/10 kV Fatnevo | 1,6+1,6 | 0.068 | 0.658 | 0.37 | 120 | 0.288 | 0 | 1.68 | 1.392 | 1.392 | available
105 | SS 35/10 kV Varvarinka | 2,5+2,5 | 0.6 | 0.69 | 120 | -0.09 | 0 | 2.625 | 2.715 | 2.715 | available | 105 | SS 35/10 kV Varvarinka | 2,5+2,5 | 0 | 0.6 | 0.69 | 120 | -0.09 | 0 | 2.625 | 2.715 | 2.715 | available
106 | SS 35/10 kV Odinok | 1,6+1,6 | 0.36 | 0 | - | 0.36 | 0 | 1.68 | 1.32 | 1.32 | available | 106 | SS 35/10 kV Odinok | 1,6+1,6 | 0.039 | 0.399 | 0 |  | 0.399 | 0 | 1.68 | 1.281 | 1.281 | available
107 | SS 35/10 kV Uzkoe | 1,6+1 | 0.18 | 0.25 | 120 | -0.07 | 0 | 1.05 | 1.12 | 1.12 | available | 107 | SS 35/10 kV Uzkoe | 1,6+1 | 0.016 | 0.196 | 0.25 | 120 | -0.054 | 0 | 1.05 | 1.104 | 1.104 | available
108 | SS 35/10 kV Korsakovo | 2,5+4 | 0.76 | 0.69 | 120 | 0.07 | 0 | 2.625 | 2.555 | 2.555 | available | 108 | SS 35/10 kV Korsakovo | 2,5+4 | 0.091 | 0.851 | 0.69 | 120 | 0.161 | 0 | 2.625 | 2.464 | 2.464 | available
109 | SS 35/10 kV Paramonovo | 4+2,5 | 1.06 | 0.76 | 120 | 0.3 | 0 | 2.625 | 2.325 | 2.325 | available | 109 | SS 35/10 kV Paramonovo | 4+2,5 | 0.056 | 1.116 | 0.76 | 120 | 0.356 | 0 | 2.625 | 2.269 | 2.269 | available
110 | SS 35/10 kV Speshnevo | 1,6+1,6 | 0.19 | 0 | - | 0.19 | 0 | 1.68 | 1.49 | 1.49 | available | 110 | SS 35/10 kV Speshnevo | 1,6+1,6 | 0.067 | 0.257 | 0 |  | 0.257 | 0 | 1.68 | 1.423 | 1.423 | available
111 | SS 110/35/10 kV Verkhovye I | 16+10 | 7.34 | 3.65 | 120 | 3.69 | 0 | 10.5 | 6.81 | 6.81 | available | 111 | SS 110/35/10 kV Verkhovye I | 16+10 | 0.475 | 7.815 | 3.65 | 120 | 4.165 | 0 | 10.5 | 6.335 | 6.335 | available
| Nom. capacity MV, MVA | 16+10 | 2.25 | 2.05 | 120 | 0.2 | 0 | 10.5 | 10.3 |  |  |  | Nom. capacity MV, MVA | 16+10 | 0.297 | 2.547 | 2.05 | 120 | 0.497 | 0 | 10.5 | 10.003
| Nom. capacity LV, MVA | 16+10 | 5.09 | 1.6 | 120 | 3.49 | 0 | 10.5 | 7.01 |  |  |  | Nom. capacity LV, MVA | 16+10 | 0.178 | 5.268 | 1.6 | 120 | 3.668 | 0 | 10.5 | 6.832
112 | SS 110/35/10 kV Verkhovye II | 40+40 | 7.05 | 0.3 | - | 6.75 | 0 | 42 | 35.25 | 35.25 | available | 112 | SS 110/35/10 kV Verkhovye II | 40+40 | 0.009 | 7.099 | 0.3 |  | 6.799 | 0 | 42 | 35.201 | 35.201 | available
| Nom. capacity MV, MVA | 40+40 | 0.37 | 0.3 | - | 0.07 | 0 | 42 | 41.93 |  |  |  | Nom. capacity MV, MVA | 40+40 | 0.009 | 0.379 | 0.3 |  | 0.079 | 0 | 42 | 41.921
| Nom. capacity LV, MVA | 40+40 | 6.72 | 0 | - | 6.72 | 0 | 42 | 35.28 |  |  |  | Nom. capacity LV, MVA | 40+40 | 0 | 6.72 | 0 |  | 6.72 | 0 | 42 | 35.28
113 | SS 110/35/10 kV Dolgoe | 16+10 | 4.82 | 3.38 | 120 | 1.44 | 0 | 10.5 | 9.06 | 8.55 | available | 113 | SS 110/35/10 kV Dolgoe | 16+10 | 0.116 | 4.936 | 3.38 | 120 | 1.556 | 0 | 10.5 | 8.944 | 8.452 | available
| Nom. capacity MV, MVA | 16+10 | 1.87 | 2.38 | 120 | -0.51 | 0 | 10.5 | 11.01 |  |  |  | Nom. capacity MV, MVA | 16+10 | 0.018 | 1.888 | 2.38 | 120 | -0.492 | 0 | 10.5 | 10.992
| Nom. capacity LV, MVA | 16+10 | 2.95 | 1 | 120 | 1.95 | 0 | 10.5 | 8.55 |  |  |  | Nom. capacity LV, MVA | 16+10 | 0.098 | 3.048 | 1 | 120 | 2.048 | 0 | 10.5 | 8.452
114 | SS 110/35/10 kV Kolpny-110 | 10+16 | 3.73 | 2.79 | 120 | 0.94 | 0 | 10.5 | 9.56 | 9.35 | available | 114 | SS 110/35/10 kV Kolpny-110 | 10+16 | 0.284 | 4.014 | 2.79 | 120 | 1.224 | 0 | 10.5 | 9.276 | 9.208 | available
| Nom. capacity MV, MVA | 10+16 | 2.25 | 2.46 | 120 | -0.21 | 0 | 10.5 | 10.71 |  |  |  | Nom. capacity MV, MVA | 10+16 | 0.142 | 2.392 | 2.46 | 120 | -0.068 | 0 | 10.5 | 10.568
| Nom. capacity LV, MVA | 10+16 | 1.48 | 0.33 | 120 | 1.15 | 0 | 10.5 | 9.35 |  |  |  | Nom. capacity LV, MVA | 10+16 | 0.142 | 1.622 | 0.33 | 120 | 1.292 | 0 | 10.5 | 9.208
115 | SS 110/35/10 kV Kr. Zarya | 10+10 | 3.69 | 1.54 | 120 | 2.15 | 0 | 10.5 | 8.35 | 8.35 | available | 115 | SS 110/35/10 kV Kr. Zarya | 10+10 | 0.07 | 3.78 | 1.54 | 120 | 2.24 | 0 | 10.5 | 8.26 | 8.26 | available
| Nom. capacity MV, MVA | 10+10 | 1.6 | 1.29 | 120 | 0.31 | 0 | 10.5 | 10.19 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.024 | 1.624 | 1.29 | 120 | 0.334 | 0 | 10.5 | 10.166
| Nom. capacity LV, MVA | 10+10 | 2.11 | 0.25 | 120 | 1.86 | 0 | 10.5 | 8.64 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.046 | 2.156 | 0.25 | 120 | 1.906 | 0 | 10.5 | 8.594
116 | SS 110/35/10 kV Pokrovskaya | 10+10 | 5.36 | 2.84 | 120 | 2.52 | 0 | 10.5 | 7.98 | 7.98 | available | 116 | SS 110/35/10 kV Pokrovskaya | 10+10 | 0.672 | 6.042 | 2.84 | 120 | 3.202 | 0 | 10.5 | 7.298 | 7.298 | available
| Nom. capacity MV, MVA | 10+10 | 2.47 | 2.12 | 120 | 0.35 | 0 | 10.5 | 10.15 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.206 | 2.676 | 2.12 | 120 | 0.556 | 0 | 10.5 | 9.944
| Nom. capacity LV, MVA | 10+10 | 2.9 | 0.72 | 120 | 2.18 | 0 | 10.5 | 8.32 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.466 | 3.366 | 0.72 | 120 | 2.646 | 0 | 10.5 | 7.854
117 | SS 110/35/6 kV Cherkasskaya | 40+25 | 21.65 | 13.39 | 120 | 8.26 | 0 | 26.25 | 17.99 | 17.99 | available | 117 | SS 110/35/6 kV Cherkasskaya | 40+25 | 3.907 | 25.577 | 13.39 | 120 | 12.187 | 0 | 26.25 | 14.063 | 14.063 | available
| Nom. capacity MV, MVA | 40+25 | 15.2 | 10.84 | 120 | 4.36 | 0 | 26.25 | 21.89 |  |  |  | Nom. capacity MV, MVA | 40+25 | 2.913 | 18.113 | 10.84 | 120 | 7.273 | 0 | 26.25 | 18.977
| Nom. capacity LV, MVA | 40+25 | 6.47 | 2.55 | 120 | 3.92 | 0 | 26.25 | 22.33 |  |  |  | Nom. capacity LV, MVA | 40+25 | 0.994 | 7.464 | 2.55 | 120 | 4.914 | 0 | 26.25 | 21.336
118 | SS 110/6 kV Plastmass | 16+16 | 9.77 | 0 | - | 9.77 | 0 | 16.8 | 7.03 | 7.03 | available | 118 | SS 110/6 kV Plastmass | 16+16 | 0 | 9.77 | 0 |  | 9.77 | 0 | 16.8 | 7.03 | 7.03 | available
119 | SS 110/10 kV PM | 10+10 | 3.48 | 0 | - | 3.48 | 0 | 10.5 | 7.02 | 7.02 | available | 119 | SS 110/10 kV PM | 10+10 | 0 | 3.48 | 0 |  | 3.48 | 0 | 10.5 | 7.02 | 7.02 | available
120 | SS 110/10 kV Rechitsa | 6,3+6,3 | 0.95 | 1.85 | 120 | -0.9 | 0 | 6.615 | 7.515 | 7.515 | available | 120 | SS 110/10 kV Rechitsa | 6,3+6,3 | 0.033 | 0.983 | 1.85 | 120 | -0.867 | 0 | 6.615 | 7.482 | 7.482 | available
121 | SS 110/10 kV R.Brod | 5,6+10 | 1.6 | 0.29 | 120 | 1.31 | 0 | 5.88 | 4.57 | 4.57 | available | 121 | SS 110/10 kV R.Brod | 5,6+10 | 0.135 | 1.735 | 0.29 | 120 | 1.445 | 0 | 5.88 | 4.435 | 4.435 | available
122 | SS 35/10 kV Alekseevskaya | 1,6+1,6 | 0.63 | 0.13 | 120 | 0.5 | 0 | 1.68 | 1.18 | 1.18 | available | 122 | SS 35/10 kV Alekseevskaya | 1,6+1,6 | 0.098 | 0.728 | 0.13 | 120 | 0.598 | 0 | 1.68 | 1.082 | 1.082 | available
123 | SS 35/10 kV V.Dubrava | 2,5+2,5 | 0.85 | 0.65 | 120 | 0.2 | 0 | 2.625 | 2.425 | 2.425 | available | 123 | SS 35/10 kV V.Dubrava | 2,5+2,5 | 0.113 | 0.963 | 0.65 | 120 | 0.313 | 0 | 2.625 | 2.312 | 2.312 | available
124 | SS 35/10 kV V.Olshanoe | 4+2,5 | 0.52 | 0.43 | 120 | 0.09 | 0 | 2.625 | 2.535 | 2.535 | available | 124 | SS 35/10 kV V.Olshanoe | 4+2,5 | 0 | 0.52 | 0.43 | 120 | 0.09 | 0 | 2.625 | 2.535 | 2.535 | available
125 | SS 35/10 kV Vvedenskoe | 1,6+1,8 | 0.68 | 0.56 | 120 | 0.12 | 0 | 1.68 | 1.56 | 1.56 | available | 125 | SS 35/10 kV Vvedenskoe | 1,6+1,8 | 0.027 | 0.707 | 0.56 | 120 | 0.147 | 0 | 1.68 | 1.533 | 1.533 | available
126 | SS 35/10 kV Droskovo | 4+2,5 | 1.57 | 0 | - | 1.57 | 0 | 2.625 | 1.055 | 1.055 | available | 126 | SS 35/10 kV Droskovo | 4+2,5 | 0.108 | 1.678 | 0 |  | 1.678 | 0 | 2.625 | 0.947 | 0.947 | available
127 | SS 35/10 kV Kolpny-35 | 6,3+6,3 | 0.96 | 0.39 | 120 | 0.57 | 0 | 6.615 | 6.045 | 6.045 | available | 127 | SS 35/10 kV Kolpny-35 | 6,3+6,3 | 0.035 | 0.995 | 0.39 | 120 | 0.605 | 0 | 6.615 | 6.01 | 6.01 | available
128 | SS 35/10 kV Krutoe | 2,5+2,5 | 1.41 | 0.87 | 120 | 0.54 | 0 | 2.625 | 2.085 | 2.085 | available | 128 | SS 35/10 kV Krutoe | 2,5+2,5 | 0.204 | 1.614 | 0.87 | 120 | 0.744 | 0 | 2.625 | 1.881 | 1.881 | available
129 | SS 35/10 kV Mezentsevo | 4+6,3 | 1.66 | 1.11 | 80 | 0.55 | 0 | 4.2 | 3.65 | 3.65 | available | 129 | SS 35/10 kV Mezentsevo | 4+6,3 | 0.313 | 1.973 | 1.11 | 80 | 0.863 | 0 | 4.2 | 3.337 | 3.337 | available
130 | SS 35/10 kV N.Zhernovets | 1,6+1,6 | 0.19 | 0 | - | 0.19 | 0 | 1.68 | 1.49 | 1.49 | available | 130 | SS 35/10 kV N.Zhernovets | 1,6+1,6 | 0.008 | 0.198 | 0 |  | 0.198 | 0 | 1.68 | 1.482 | 1.482 | available
131 | SS 35/10 kV Netrubezh | 2,5+2,5 | 0.55 | 0.39 | - | 0.16 | 0 | 2.625 | 2.465 | 2.465 | available | 131 | SS 35/10 kV Netrubezh | 2,5+2,5 | 0.009 | 0.559 | 0.39 |  | 0.169 | 0 | 2.625 | 2.456 | 2.456 | available
132 | SS 35/10 kV Nikolskaya | 2,5+3,2 | 1.14 | 0.54 | 80 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | available | 132 | SS 35/10 kV Nikolskaya | 2,5+3,2 | 0.066 | 1.206 | 0.54 | 80 | 0.666 | 0 | 2.625 | 1.959 | 1.959 | available
133 | SS 35/10 kV Pesochnaya | 3,2+3,2 | 0.37 | 1.67 | 120 | -1.3 | 0 | 3.36 | 4.66 | 4.66 | available | 133 | SS 35/10 kV Pesochnaya | 3,2+3,2 | 0.009 | 0.379 | 1.67 | 120 | -1.291 | 0 | 3.36 | 4.651 | 4.651 | available
134 | SS 35/6 kV Pushkarskaya | 4+4 | 5 | 0 |  | 5 | 0 | 4.2 | -0.8 | -0.8 | unavailable | 134 | SS 35/6 kV Pushkarskaya | 4+4 | 0 | 5 | 0 |  | 5 | 0 | 4.2 | -0.8 | -0.8 | unavailable
135 | SS 35/10 kV Rakhmanovo | 2,5+2,5 | 0.65 | 0.25 | 120 | 0.4 | 0 | 2.625 | 2.225 | 2.225 | available | 135 | SS 35/10 kV Rakhmanovo | 2,5+2,5 | 0 | 0.65 | 0.25 | 120 | 0.4 | 0 | 2.625 | 2.225 | 2.225 | available
136 | SS 35/10 kV Rosstani | 2,5+2,5 | 0.97 | 0.7 | 80 | 0.27 | 0 | 2.625 | 2.355 | 2.355 | available | 136 | SS 35/10 kV Rosstani | 2,5+2,5 | 0.188 | 1.158 | 0.7 | 80 | 0.458 | 0 | 2.625 | 2.167 | 2.167 | available
137 | SS 35/10 kV Sergievskaya | 4+2,5 | 1.31 | 1.5 | 120 | -0.19 | 0 | 2.625 | 2.815 | 2.815 | available | 137 | SS 35/10 kV Sergievskaya | 4+2,5 | 1.7 | 3.01 | 1.5 | 120 | 1.51 | 0 | 2.625 | 1.115 | 1.115 | available
138 | SS 35/10 kV Skorodnoe | 1,6+1,6 | 0.3 | 0.33 | 120 | -0.03 | 0 | 1.68 | 1.71 | 1.71 | available | 138 | SS 35/10 kV Skorodnoe | 1,6+1,6 | 0.025 | 0.325 | 0.33 | 120 | -0.005 | 0 | 1.68 | 1.685 | 1.685 | available
139 | SS 35/10 kV Spasskaya | 2,5+1,6 | 0.25 | 0 | 120 | 0.25 | 0 | 1.68 | 1.43 | 1.43 | available | 139 | SS 35/10 kV Spasskaya | 2,5+1,6 | 0.035 | 0.285 | 0 |  | 0.285 | 0 | 1.68 | 1.395 | 1.395 | available
140 | SS 35/10 kV SSK | 1,6+1,6 | 0.07 | 0 |  | 0.07 | 0 | 1.68 | 1.61 | 1.61 | available | 140 | SS 35/10 kV SSK | 1,6+1,6 | 0.012 | 0.082 | 0 |  | 0.082 | 0 | 1.68 | 1.598 | 1.598 | available
141 | SS 35/10 kV Urynok | 1,6+1,6 | 0.84 | 0.52 | 20 | 0.32 | 0 | 1.68 | 1.36 | 1.36 | available | 141 | SS 35/10 kV Urynok | 1,6+1,6 | 0.012 | 0.852 | 0.52 | 20 | 0.332 | 0 | 1.68 | 1.348 | 1.348 | available
142 | SS 35/10 kV Khomutovo | 4+4 | 1.96 | 0.31 | 80 | 1.65 | 0 | 4.2 | 2.55 | 2.55 | available | 142 | SS 35/10 kV Khomutovo | 4+4 | 0.272 | 2.232 | 0.31 | 80 | 1.922 | 0 | 4.2 | 2.278 | 2.278 | available
| Total: | [10 empty] | 2: Total:; 4: 157.267; 5: 710.37
| deficit | [8 empty] | -2.51 |  | 2: deficit; Min 12: -14.724
| proficit | [8 empty] | 618.475 |  | 2: proficit; Min 12: 470.813