## Orel
Transmission capacity of supply centers of IDGC of Centre - Orelenergo division following the results of measurements of peak loads in winter 2011-2012
table 1
No. | Name of supply center, voltage class | Current deficit | [8 empty] | Note | No. | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity, MVA | Current deficit/proficit MVA |  |  |  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load of Supply Center, MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transfer capacity of Supply Center, MVA | Expected deficit/proficit, MVA
|  |  | MVA | MVA | Min | [11 empty] | MVA | Min
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | SS 35/10 kV Almazovo | 2.5 | 0.37 | 0.83 | 30 | 0.83 | 0 | 0.83 | 0.46 | 0.46 | available | 1 | SS 35/10 kV Almazovo | 2.5 | 0.064 | 0.434 | 0.83 | 30 | 0.83 | 0 | 0.83 | 0.396 | 0.396 | available
2 | SS 35/10 kV Voronets | 2.5 | 0.23 | 0.91 | 90 | 0.91 | 0 | 0.91 | 0.68 | 0.68 | available | 2 | SS 35/10 kV Voronets | 2.5 | 0 | 0.23 | 0.91 | 90 | 0.91 | 0 | 0.91 | 0.68 | 0.68 | available
3 | SS 35/10 kV Gostoml | 2.5 | 0.75 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 0.85 | 0.85 | available | 3 | SS 35/10 kV Gostoml | 2.5 | 0.094118 | 0.84412 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 0.75588 | 0.75588 | available
4 | SS 35/10 kV Gubkino | 3.2 | 0.37 | 1.56 | 30 | 1.56 | 0 | 1.56 | 1.19 | 1.19 | available | 4 | SS 35/10 kV Gubkino | 3.2 | 0.055294 | 0.42529 | 1.56 | 30 | 1.56 | 0 | 1.56 | 1.1347 | 1.1347 | available
5 | SS 35/10 kV Devyatino | 1.6 | 0.16 | 0.71 | 45 | 0.71 | 0 | 0.71 | 0.55 | 0.55 | available | 5 | SS 35/10 kV Devyatino | 1.6 | 0 | 0.16 | 0.71 | 45 | 0.71 | 0 | 0.71 | 0.55 | 0.55 | available
6 | SS 35/10 kV Kamenka | 2.5 | 0.75 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 0.85 | 0.85 | available | 6 | SS 35/10 kV Kamenka | 2.5 | 0.023529 | 0.77353 | 1.6 | 1 day and night | 1.6 | 0 | 1.6 | 0.82647 | 0.82647 | available
7 | SS 35/10 kV Kozminskaya | 1.6 | 0.23 | 1.29 | 45 | 1.29 | 0 | 1.29 | 1.06 | 1.06 | available | 7 | SS 35/10 kV Kozminskaya | 1.6 | 0.044706 | 0.27471 | 1.29 | 45 | 1.29 | 0 | 1.29 | 1.0153 | 1.0153 | available
8 | SS 110/35/10 kV Maloarkhangelskaya | 10 | 4.02 | 6.14 | 60 | 2.12 | 0 | 6.14 | 2.12 | 0.32 | available | 8 | SS 110/35/10 kV Maloarkhangelskaya | 10 | 3.1965 | 7.2165 | 6.14 | 60 | 6.14 | 0 | 6.14 | -1.0765 | -1.0765 | unavailable
| Nom. capacity MV, MVA | 10 | 1.62 | 1.94 | 60 | 1.94 | 0 | 1.94 | 0.32 |  |  |  | Nom. capacity MV, MVA | 10 | 0.10824 | 1.7282 | 1.94 | 60 | 1.94 | 0 | 1.94 | 0.21176
| Nom. capacity LV, MVA | 10 | 2.4 | 4.2 | 60 | 1.8 | 0 | 4.2 | 1.8 |  |  |  | Nom. capacity LV, MVA | 10 | 3.0882 | 5.4882 | 4.2 | 60 | 4.2 | 0 | 4.2 | -1.2882
9 | SS 110/35/10 kV Novopolevo | 16 | 4.05 | 4.31 | 30 | 4.31 | 0 | 4.31 | 0.26 | -0.4 | unavailable | 9 | SS 110/35/10 kV Novopolevo | 16 | 0.53265 | 4.5826 | 4.31 | 30 | 4.31 | 0 | 4.31 | -0.27265 | -0.27265 | unavailable
| Nom. capacity MV, MVA | 16 | 2.54 | 3.2 | 30 | 3.2 | 0 | 3.2 | 0.66 |  |  |  | Nom. capacity MV, MVA | 16 | 0.15676 | 2.6968 | 3.2 | 30 | 3.2 | 0 | 3.2 | 0.50324
| Nom. capacity LV, MVA | 16 | 1.51 | 1.11 | 30 | 1.11 | 0 | 1.11 | -0.4 |  |  |  | Nom. capacity LV, MVA | 16 | 0.37588 | 1.8859 | 1.11 | 30 | 1.11 | 0 | 1.11 | -0.77588
10 | SS 35/10 kV Nikolskaya | 2.5 | 0.56 | 1.33 | 45 | 1.33 | 0 | 1.33 | 0.77 | 0.77 | available | 10 | SS 35/10 kV Nikolskaya | 2.5 | 0.033529 | 0.59353 | 1.33 | 45 | 1.33 | 0 | 1.33 | 0.73647 | 0.73647 | available
11 | SS 35/10 kV Paramonovo | 1.8 | 0.15 | 0.48 | 90 | 0.48 | 0 | 0.48 | 0.33 | 0.33 | available | 11 | SS 35/10 kV Paramonovo | 1.8 | 0 | 0.15 | 0.48 | 90 | 0.48 | 0 | 0.48 | 0.33 | 0.33 | available
12 | SS 35/10 kV Senkovo | 1.6 | 0.47 | 1.29 | 30 | 1.29 | 0 | 1.29 | 0.82 | 0.82 | available | 12 | SS 35/10 kV Senkovo | 1.6 | 0.020882 | 0.49088 | 1.29 | 30 | 1.29 | 0 | 1.29 | 0.79912 | 0.79912 | available
13 | SS 35/10 kV Somovo | 2.5 | 0.29 | 0.96 | 60 | 0.96 | 0 | 0.96 | 0.67 | 0.67 | available | 13 | SS 35/10 kV Somovo | 2.5 | 0.029412 | 0.31941 | 0.96 | 60 | 0.96 | 0 | 0.96 | 0.64059 | 0.64059 | available
14 | SS 110/35/10 kV Trosna | 16 | 3.67 | 4.16 | 45 | 4.16 | 0 | 4.16 | 0.49 | -0.02 | unavailable | 14 | SS 110/35/10 kV Trosna | 16 | 0.377 | 4.047 | 4.16 | 45 | 4.16 | 0 | 4.16 | 0.113 | -0.132 | unavailable
| Nom. capacity MV, MVA | 16 | 2.38 | 2.36 | 45 | 2.36 | 0 | 2.36 | -0.02 |  |  |  | Nom. capacity MV, MVA | 16 | 0.112 | 2.492 | 2.36 | 45 | 2.36 | 0 | 2.36 | -0.132
| Nom. capacity LV, MVA | 16 | 1.29 | 1.8 | 45 | 1.8 | 0 | 1.8 | 0.51 |  |  |  | Nom. capacity LV, MVA | 16 | 0.265 | 1.555 | 1.8 | 45 | 1.8 | 0 | 1.8 | 0.245
15 | SS 35/10 kV Shablykino | 5.6 | 0.1 | 0.8 | 90 | 0.8 | 0 | 0.8 | 0.7 | 0.7 | available | 15 | SS 35/10 kV Shablykino | 5.6 | 0 | 0.1 | 0.8 | 90 | 0.8 | 0 | 0.8 | 0.7 | 0.7 | available
16 | SS 35/10 kV Yuryevo | 2.5 | 0.13 | 1.07 | 60 | 1.07 | 0 | 1.07 | 0.94 | 0.94 | available | 16 | SS 35/10 kV Yuryevo | 2.5 | 0.029412 | 0.15941 | 1.07 | 60 | 1.07 | 0 | 1.07 | 0.91059 | 0.91059 | available
17 | SS 110/35/10 kV Region V | 10 | 3.53 | 5.4 | 120 | 5.4 | 0 | 5.4 | 1.87 | 1.87 | available | 17 | SS 110/35/10 kV Region V | 10 | 0.2 | 4.102 | 5.4 | 120 | 5.4 | 0 | 5.4 | 1.298 | 1.298 | available
| Nom. capacity MV, MVA | 10 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | Nom. capacity MV, MVA | 10 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| Nom. capacity LV, MVA | 10 | 3.53 | 5.4 | 120 | 5.4 | 0 | 5.4 | 1.87 |  |  |  | Nom. capacity LV, MVA | 10 | 0.572 | 4.102 | 5.4 | 120 | 5.4 | 0 | 5.4 | 1.298
18 | SS 110/10 kV Pishchevaya | 6.3 | 1.62 | 1.875 | 60 | 1.875 | 0 | 1.875 | 0.255 | 0.255 | available | 18 | SS 110/10 kV Pishchevaya | 6.3 | 1.021 | 2.641 | 1.875 | 60 | 1.875 | 0 | 1.875 | -0.766 | -0.766 | unavailable
19 | SS 110/10 kV Telchye | 3.2 | 1.63 | 1.46 | 120 | 1.46 | 0 | 1.46 | -0.17 | -0.17 | unavailable | 19 | SS 110/10 kV Telchye | 3.2 | 0.22353 | 1.8535 | 1.46 | 120 | 1.46 | 0 | 1.46 | -0.39353 | -0.39353 | unavailable
20 | SS 110/10 kV B.Chern | 2.5 | 0.17 | 1 | 120 | 1 | 0 | 1 | 0.83 | 0.83 | available | 20 | SS 110/10 kV B.Chern | 2.5 | 0.273 | 0.443 | 1 | 120 | 1 | 0 | 1 | 0.557 | 0.557 | available
21 | SS 35/10 kV Bashkatovo | 1.6 | 0.26 | 0.8 | 120 | 0.8 | 0 | 0.8 | 0.54 | 0.54 | available | 21 | SS 35/10 kV Bashkatovo | 1.6 | 0.055 | 0.315 | 0.8 | 120 | 0.8 | 0 | 0.8 | 0.485 | 0.485 | available
22 | SS 35/10 kV Vysokoe | 1.6 | 0.18 | 1.24 | 120 | 1.24 | 0 | 1.24 | 1.06 | 1.06 | available | 22 | SS 35/10 kV Vysokoe | 1.6 | 0.056471 | 0.23647 | 1.24 | 120 | 1.24 | 0 | 1.24 | 1.0035 | 1.0035 | available
23 | SS 35/10 kV Gladkoe | 2.5 | 0.34 | 1.46 | 120 | 1.46 | 0 | 1.46 | 1.12 | 1.12 | available | 23 | SS 35/10 kV Gladkoe | 2.5 | 0.022353 | 0.36235 | 1.46 | 120 | 1.46 | 0 | 1.46 | 1.0976 | 1.0976 | available
24 | SS 35/10 kV Lykovo | 2.5 | 0.68 | 1.24 | 120 | 1.24 | 0 | 1.24 | 0.56 | 0.56 | available | 24 | SS 35/10 kV Lykovo | 2.5 | 0.225 | 0.905 | 1.24 | 120 | 1.24 | 0 | 1.24 | 0.335 | 0.335 | available
25 | SS 35/6 kV Sugar mill | 4 | 0.01 | 1 | 120 | 1 | 0 | 1 | 0.99 | 0.99 | available | 25 | SS 35/6 kV Sugar mill | 4 | 0 | 0.01 | 1 | 120 | 1 | 0 | 1 | 0.99 | 0.99 | available
26 | SS 35/10 kV Gnezdilivo | 1.6 | 0.24 | 0.68 | 120 | 0.68 | 0 | 0.68 | 0.44 | 0.44 | available | 26 | SS 35/10 kV Gnezdilivo | 1.6 | 0.082353 | 0.32235 | 0.68 | 120 | 0.68 | 0 | 0.68 | 0.35765 | 0.35765 | available
27 | SS 35/10 kV Koptevo | 1.6 | 0.32 | 0.44 | 120 | 0.44 | 0 | 0.44 | 0.12 | 0.12 | available | 27 | SS 35/10 kV Koptevo | 1.6 | 0 | 0.32 | 0.44 | 120 | 0.44 | 0 | 0.44 | 0.12 | 0.12 | available
28 | SS 110/35/10/6 kV Meat processing factory | 10 | 1.68 | 2.13 | 120 | 2.13 | 0 | 2.13 | 0.45 | 0.45 | available | 28 | SS 110/35/10/6 kV Meat processing factory | 10 | 0.012 | 1.7165 | 2.13 | 120 | 2.13 | 0 | 2.13 | 0.41353 | 0.41353 | available
| Nom. capacity MV, MVA | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | Nom. capacity MV, MVA | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Nom. capacity LV, MVA | 10 | 1.68 | 2.13 | 120 | 2.13 | 0 | 2.13 | 0.45 |  |  |  | Nom. capacity LV, MVA | 10 | 0.036471 | 1.7165 | 2.13 | 120 | 2.13 | 0 | 2.13 | 0.41353
29 | SS 110/35/10 kV Shatilovo | 10 | 0.9 | 0.69 | 120 | 0.69 | 0 | 0.69 | -0.21 | -0.21 | unavailable | 29 | SS 110/35/10 kV Shatilovo | 10 | 0.005 | 1.0047 | 0.69 | 120 | 0.69 | 0 | 0.69 | -0.31471 | -0.31471 | unavailable
| Nom. capacity MV, MVA | 10 | 0.32 | 0.16 | 180 | 0.16 | 0 | 0.16 | -0.16 |  |  |  | Nom. capacity MV, MVA | 10 | 0.069412 | 0.38941 | 0.16 | 180 | 0.16 | 0 | 0.16 | -0.22941
| Nom. capacity LV, MVA | 10 | 0.58 | 0.53 | 120 | 0.53 | 0 | 0.53 | -0.05 |  |  |  | Nom. capacity LV, MVA | 10 | 0.035294 | 0.61529 | 0.53 | 120 | 0.53 | 0 | 0.53 | -0.085294
30 | SS 110/35/10 kV Sovkhoznaya | 10 | 3.12 | 8.96 | 120 | 8.96 | 0 | 8.96 | 5.84 | 1.58 | available | 30 | SS 110/35/10 kV Sovkhoznaya | 10 | 0.87671 | 3.9967 | 8.96 | 120 | 8.96 | 0 | 8.96 | 4.9633 | 1.54 | available
| Nom. capacity MV, MVA | 10 | 2.36 | 6.62 | 120 | 6.62 | 0 | 6.62 | 4.26 |  |  |  | Nom. capacity MV, MVA | 10 | 0.83671 | 3.1967 | 6.62 | 120 | 6.62 | 0 | 6.62 | 3.4233
| Nom. capacity LV, MVA | 10 | 0.76 | 2.34 | 120 | 2.34 | 0 | 2.34 | 1.58 |  |  |  | Nom. capacity LV, MVA | 10 | 0.04 | 0.8 | 2.34 | 120 | 2.34 | 0 | 2.34 | 1.54
31 | SS 35/10 kV Danilovskaya | 1.6 | 0.62 | 0.68 | 120 | 0.68 | 0 | 0.68 | 0.06 | 0.06 | available | 31 | SS 35/10 kV Danilovskaya | 1.6 | 0 | 0.62 | 0.68 | 120 | 0.68 | 0 | 0.68 | 0.06 | 0.06 | available
32 | SS 35/10 kV Korseevo | 1.8 | 0.02 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.86 | 0.86 | available | 32 | SS 35/10 kV Korseevo | 1.8 | 0 | 0.02 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.86 | 0.86 | available
33 | SS 35/10 kV Lipovets | 2.5 | 0.83 | 1.39 | 120 | 1.39 | 0 | 1.39 | 0.56 | 0.56 | available | 33 | SS 35/10 kV Lipovets | 2.5 | 0.22471 | 1.0547 | 1.39 | 120 | 1.39 | 0 | 1.39 | 0.33529 | 0.33529 | available
34 | SS 35/10 kV Misaylovo | 1.6 | 0.38 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.22 | 1.22 | available | 34 | SS 35/10 kV Misaylovo | 1.6 | 0.047059 | 0.42706 | 1.6 |  | 1.6 | 0 | 1.6 | 1.1729 | 1.1729 | available
35 | SS 35/10 kV Mikhaylovka | 2.5 | 0.29 | 0.31 | 80 | 0.31 | 0 | 0.31 | 0.02 | 0.02 | available | 35 | SS 35/10 kV Mikhaylovka | 2.5 | 0 | 0.29 | 0.31 | 80 | 0.31 | 0 | 0.31 | 0.02 | 0.02 | available
36 | SS 35/10 kV Pankovo | 1.8 | 0.32 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.28 | 1.28 | available | 36 | SS 35/10 kV Pankovo | 1.8 | 0.069412 | 0.38941 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.2106 | 1.2106 | available
37 | SS 35/10 kV Sudbishchi | 2.5 | 0.8 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 0.8 | 0.8 | available | 37 | SS 35/10 kV Sudbishchi | 2.5 | 0 | 0.8 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 0.8 | 0.8 | available
38 | SS 35/10 kV Tim | 1.6 | 0.58 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.02 | 1.02 | available | 38 | SS 35/10 kV Tim | 1.6 | 0.02 | 0.6 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1 | 1 | available
39 | SS 35/10 kV Topki | 1 | 0.55 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.05 | 1.05 | available | 39 | SS 35/10 kV Topki | 1 | 0.072941 | 0.62294 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 0.97706 | 0.97706 | available
40 | SS 35/10 kV Yarishche | 2.5 | 0.32 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.28 | 1.28 | available | 40 | SS 35/10 kV Yarishche | 2.5 | 0.057412 | 0.37741 | 1.6 | 1day and night | 1.6 | 0 | 1.6 | 1.2226 | 1.2226 | available
41 | SS 110/10 kV Alshanskaya | 10+10 | 4.31 | 3.88 | 30 | 0.43 | 0 | 10.5 | 10.07 | 10.07 | available | 41 | SS 110/10 kV Alshanskaya | 10+10 | 1.101 | 5.411 | 3.88 | 30 | 1.531 | 0 | 10.5 | 8.969 | 8.969 | available
42 | SS 35/10 kV Arkhangelskaya | 2,5+2,5 | 0.57 | 0.93 | 90 | -0.36 | 0 | 2.625 | 2.985 | 2.985 | available | 42 | SS 35/10 kV Arkhangelskaya | 2,5+2,5 | 0.027 | 0.597 | 0.93 | 90 | -0.333 | 0 | 2.625 | 2.958 | 2.958 | available
43 | SS 35/10 kV Atyaevskaya | 1,6+2,5 | 0.54 | 0 | - | 0.54 | 0 | 1.68 | 1.14 | 1.14 | available | 43 | SS 35/10 kV Atyaevskaya | 1,6+2,5 | 0.37059 | 0.91059 | 0 |  | 0.91059 | 0 | 1.68 | 0.76941 | 0.76941 | available
44 | SS 110/35/10 kV Bogoroditskaya | 10+10 | 2.36 | 3.06 | 90 | -0.7 | 0 | 10.5 | 11.2 | 10.75 | available | 44 | SS 110/35/10 kV Bogoroditskaya | 10+10 | 0.81882 | 3.1788 | 3.06 | 90 | 0.11882 | 0 | 10.5 | 10.3812 | 10.3812 | available
| Nom. capacity MV, MVA | 10+10 | 2.18 | 2.43 | 90 | -0.25 | 0 | 10.5 | 10.75 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.80118 | 2.9812 | 2.43 | 90 | 0.55118 | 0 | 10.5 | 9.9488
| Nom. capacity LV, MVA | 10+10 | 0.18 | 0.63 | 90 | -0.45 | 0 | 10.5 | 10.95 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.017647 | 0.19765 | 0.63 | 90 | -0.43235 | 0 | 10.5 | 10.9324
45 | SS 35/10 kV Baklanovo | 1,6+1,6 | 0.83 | 0.64 | 60 | 0.19 | 0 | 1.68 | 1.49 | 1.49 | available | 45 | SS 35/10 kV Baklanovo | 1,6+1,6 | 0.32941 | 1.1594 | 0.64 | 60 | 0.51941 | 0 | 1.68 | 1.1606 | 1.1606 | available
46 | SS 35/10 kV Biofactory | 6,3+6,3 | 3.09 | 2.05 | 90 | 1.04 | 0 | 6.615 | 5.575 | 5.575 | available | 46 | SS 35/10 kV Biofactory | 6,3+6,3 | 2.226 | 5.316 | 2.05 | 90 | 3.266 | 0 | 6.615 | 3.349 | 3.349 | available
47 | SS 110/10 kV Volodarskaya | 2,5+6,3 | 3.56 | 1.46 | 30 | 2.1 | 0 | 2.625 | 0.525 | 0.525 | available | 47 | SS 110/10 kV Volodarskaya | 2,5+6,3 | 5.666 | 9.226 | 1.46 | 30 | 7.766 | 0 | 2.625 | -5.141 | -5.141 | unavailable
48 | SS 110/10 kV Vostochnaya | 15+15 | 12.83 | 5.87 | 120 | 6.96 | 0 | 15.75 | 8.79 | 8.79 | available | 48 | SS 110/10 kV Vostochnaya | 15+15 | 0.66235 | 13.4924 | 5.87 | 120 | 7.6224 |  | 15.75 | 8.1276 | 8.1276 | available
49 | SS 110/35/10 kV Dmitrovskaya | 10+10 | 3.62 | 0.7 | 60 | 2.92 | 0 | 10.5 | 7.58 | 7.58 | available | 49 | SS 110/35/10 kV Dmitrovskaya | 10+10 | 0.122 | 3.742 | 0.7 | 60 | 3.042 | 0 | 10.5 | 7.458 | 7.458 | available
| Nom. capacity MV, MVA | 10+10 | 0.62 | 0.25 | 120 | 0.37 | 0 | 10.5 | 10.13 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0 | 0.62 | 0.25 |  | 0.37 | 0 | 10.5 | 10.13
| Nom. capacity LV, MVA | 10+10 | 3 | 0.45 | 60 | 2.55 | 0 | 10.5 | 7.95 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.122 | 3.122 | 0.45 | 60 | 2.672 | 0 | 10.5 | 7.828
50 | SS 110/10 kV Zheleznodorozhnaya | 16+16 | 11.28 | 3.98 | 180 | 7.3 | 0 | 16.8 | 9.5 | 9.5 | available | 50 | SS 110/10 kV Zheleznodorozhnaya | 16+16 | 0.44541 | 11.7254 | 3.98 | 180 | 7.7454 | 0 | 16.8 | 9.0546 | 9.0546 | available
51 | SS 35/10 kV Zhilyaevskaya | 1,8+1,8 | 0.63 | 0.64 | 60 | -0.01 | 0 | 1.89 | 1.9 | 1.9 | available | 51 | SS 35/10 kV Zhilyaevskaya | 1,8+1,8 | 0.107 | 0.737 | 0.64 | 60 | 0.097 | 0 | 1.89 | 1.793 | 1.793 | available
52 | SS 110/6 kV Zavodskaya | 40+25 | 15.35 | 4.39 | 150 | 10.96 | 0 | 26.25 | 15.29 | 15.29 | available | 52 | SS 110/6 kV Zavodskaya | 40+25 | 1.5581 | 16.9081 | 4.39 | 150 | 12.5181 | 0 | 26.25 | 13.7319 | 13.7319 | available
53 | SS 110/6 kV Zapadnaya | 63+63 | 24.88 | 5.37 | 120 | 19.51 | 19 | 66.15 | 27.64 | 27.64 | available | 53 | SS 110/6 kV Zapadnaya | 63+63 | 0 | 24.88 | 5.37 | 120 | 19.51 | 19 | 66.15 | 27.64 | 27.64 | available
54 | SS 35/10 kV Zvyaginki | 2,5+2,5 | 2.27 | 1.48 | 60 | 0.79 | 0 | 2.625 | 1.835 | 1.835 | available | 54 | SS 35/10 kV Zvyaginki | 2,5+2,5 | 2.658 | 4.928 | 1.48 | 60 | 3.448 | 0 | 2.625 | -0.823 | -0.823 | unavailable
55 | SS 35/10 kV Ilyinskaya | 3,2+2,5 | 0.76 | 1.18 | 30 | -0.42 | 0 | 2.625 | 3.045 | 3.045 | available | 55 | SS 35/10 kV Ilyinskaya | 3,2+2,5 | 0.286 | 1.046 | 1.18 | 30 | -0.134 | 0 | 2.625 | 2.759 | 2.759 | available
56 | SS 110/35/10 kV Kulikovskaya | 10+10 | 6.3 | 0.44 | 90 | 5.86 | 0 | 10.5 | 4.64 | 4.64 | available | 56 | SS 110/35/10 kV Kulikovskaya | 10+10 | 4.9136 | 11.2136 | 0.44 | 90 | 10.7736 | 0 | 10.5 | -0.27365 | -0.27365 | unavailable
| Nom. capacity MV, MVA | 10+10 | 2.39 | 0 | 0 | 2.39 | 0 | 10.5 | 8.11 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.94765 | 3.3376 | 0 | 0 | 3.3376 | 0 | 10.5 | 7.1624
| Nom. capacity LV, MVA | 10+10 | 3.91 | 0.44 | 90 | 3.47 | 0 | 10.5 | 7.03 |  |  |  | Nom. capacity LV, MVA | 10+10 | 3.966 | 7.876 | 0.44 | 90 | 7.436 | 0 | 10.5 | 3.064
57 | SS 110/35/10 kV Kromskaya | 16+16 | 6.23 | 9.43 | 45 | -3.2 | 0 | 16.8 | 20 | 18.23 | available | 57 | SS 110/35/10 kV Kromskaya | 16+16 | 1.1772 | 7.4072 | 9.43 | 45 | -2.0228 | 0 | 16.8 | 18.8228 | 18.8228 | available
| Nom. capacity MV, MVA | 16+16 | 3.23 | 5 | 45 | -1.77 | 0 | 16.8 | 18.57 |  |  |  | Nom. capacity MV, MVA | 16+16 | 0.58665 | 3.8166 | 5 | 45 | -1.1834 | 0 | 16.8 | 17.9834
| Nom. capacity LV, MVA | 16+16 | 3 | 4.43 | 45 | -1.43 | 0 | 16.8 | 18.23 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.59059 | 3.5906 | 4.43 | 45 | -0.83941 | 0 | 16.8 | 17.6394
58 | SS 35/10 kV Krasnoarmeyskaya | 2,5+2,5 | 1.4 | 0.95 | 30 | 0.45 | 0 | 2.625 | 2.175 | 2.175 | available | 58 | SS 35/10 kV Krasnoarmeyskaya | 2,5+2,5 | 0.112 | 1.512 | 0.95 | 30 | 0.562 | 0 | 2.625 | 2.063 | 2.063 | available
59 | SS 35/10 kV Kurakinskaya | 1,6+1,8 | 0.54 | 0 | - | 0.54 | 0 | 1.68 | 1.14 | 1.14 | available | 59 | SS 35/10 kV Kurakinskaya | 1,6+1,8 | 0.038824 | 0.57882 | 0 |  | 0.57882 | 0 | 1.68 | 1.1012 | 1.1012 | available
60 | SS 35/10 kV Kutafino | 6,3+6,3 | 0.77 | 0.83 | 30 | -0.06 | 0 | 6.615 | 6.675 | 6.675 | available | 60 | SS 35/10 kV Kutafino | 6,3+6,3 | 0.029 | 0.799 | 0.83 | 30 | -0.031 | 0 | 6.615 | 6.646 | 6.646 | available
61 | SS 35/10 kV Lovchikovo | 2,5+2,5 | 0.9 | 1.59 | 30 | -0.69 | 0 | 2.625 | 3.315 | 3.315 | available | 61 | SS 35/10 kV Lovchikovo | 2,5+2,5 | 0.056176 | 0.95618 | 1.59 | 30 | -0.63382 | 0 | 2.625 | 3.2588 | 3.2588 | available
62 | SS 35/10 kV Lubyanskaya | 1+1,6 | 0.45 | 0.47 | 60 | -0.02 | 0 | 1.05 | 1.07 | 1.07 | available | 62 | SS 35/10 kV Lubyanskaya | 1+1,6 | 0.023529 | 0.47353 | 0.47 | 60 | 0.0035294 | 0 | 1.05 | 1.0465 | 1.0465 | available
63 | SS 35/10 kV Lukovets | 1,8+2,5 | 0.5 | 0.99 | 90 | -0.49 | 0 | 1.89 | 2.38 | 2.38 | available | 63 | SS 35/10 kV Lukovets | 1,8+2,5 | 0.029412 | 0.52941 | 0.99 | 90 | -0.46059 | 0 | 1.89 | 2.3506 | 2.3506 | available
64 | SS 35/10 kV Malorkhangelskaya | 5,6+5,6 | 0.44 | 1.7 | 30 | -1.26 | 0 | 5.88 | 7.14 | 7.14 | available | 64 | SS 35/10 kV Malorkhangelskaya | 5,6+5,6 | 1.1 | 1.54 | 1.7 | 30 | -0.16 | 0 | 5.88 | 6.04 | 6.04 | available
65 | SS 110/35/10 kV Naryshkinskaya | 10+10 | 6.71 | 3.31 | 90 | 3.4 | 0 | 10.5 | 7.1 | 5.28 | available | 65 | SS 110/35/10 kV Naryshkinskaya | 10+10 | 0.71806 | 7.4281 | 3.31 | 90 | 4.1181 | 0 | 10.5 | 6.3819 | 6.3819 | available
| Nom. capacity MV, MVA | 10+10 | 0.94 | 2.76 | 90 | -1.82 | 0 | 10.5 | 12.32 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.096882 | 1.0369 | 2.76 | 90 | -1.7231 | 0 | 10.5 | 12.2231
| Nom. capacity LV, MVA | 10+10 | 5.77 | 0.55 | 90 | 5.22 | 0 | 10.5 | 5.28 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.62118 | 6.3912 | 0.55 | 90 | 5.8412 | 0 | 10.5 | 4.6588
66 | SS 35/10 kV Nizhnyaya Sloboda | 2,5+5,6 | 0.63 | 1.63 | 45 | -1 | 0 | 2.625 | 3.625 | 3.625 | available | 66 | SS 35/10 kV Nizhnyaya Sloboda | 2,5+5,6 | 0.040882 | 0.67088 | 1.63 | 45 | -0.95912 | 0 | 2.625 | 3.5841 | 3.5841 | available
67 | SS 35/10 kV Novopetrovka | 2,5+1,6 | 0.39 | 0 |  | 0.39 | 0 | 1.68 | 1.29 | 1.29 | available | 67 | SS 35/10 kV Novopetrovka | 2,5+1,6 | 0.019412 | 0.40941 | 0 | 0 | 0.40941 | 0 | 1.68 | 1.2706 | 1.2706 | available
68 | SS 35/10 kV Putimets | 2,5+2,5 | 0.49 | 1.53 | 90 | -1.04 | 0 | 2.625 | 3.665 | 3.665 | available | 68 | SS 35/10 kV Putimets | 2,5+2,5 | 1.081 | 1.571 | 1.53 | 90 | 0.041 | 0 | 2.625 | 2.584 | 2.584 | available
69 | SS 110/10 kV Pishchevaya* | 40+25 | 5.7 | 2.22 | 60 | 3.48 | 0 | 26.25 | 22.77 | 22.77 | available | 69 | SS 110/10 kV Pishchevaya* | 40+25 | 0.036471 | 5.7365 | 2.22 | 60 | 3.5165 | 0 | 26.25 | 22.7335 | 22.7335 | available
70 | SS 35/10 kV Ryzhkovo | 2,5+2,5 | 0.39 | 0.65 | 90 | -0.26 | 0 | 2.625 | 2.885 | 2.885 | available | 70 | SS 35/10 kV Ryzhkovo | 2,5+2,5 | 0.041176 | 0.43118 | 0.65 | 90 | -0.21882 | 0 | 2.625 | 2.8438 | 2.8438 | available
71 | SS 110/35/10 kV Sverdlovskaya | 10+10 | 2.81 | 1.98 | 45 | 0.83 | 0 | 10.5 | 9.67 | 9.43 | available | 71 | SS 110/35/10 kV Sverdlovskaya | 10+10 | 0.73065 | 3.5406 | 1.98 | 45 | 1.5606 | 0 | 10.5 | 8.9394 | 8.9394 | available
| Nom. capacity MV, MVA | 10+10 | 1.17 | 1.41 | 45 | -0.24 | 0 | 10.5 | 10.74 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.097647 | 1.2676 | 1.41 | 45 | -0.14235 | 0 | 10.5 | 10.6424
| Nom. capacity LV, MVA | 10+10 | 1.64 | 0.57 | 45 | 1.07 | 0 | 10.5 | 9.43 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.633 | 2.273 | 0.57 | 45 | 1.703 | 0 | 10.5 | 8.797
72 | SS 35/10 kV Streletskaya | 4+4 | 1.42 | 0.91 | 90 | 0.51 | 0 | 4.2 | 3.69 | 3.69 | available | 72 | SS 35/10 kV Streletskaya | 4+4 | 2.679 | 4.099 | 0.91 | 90 | 3.189 | 0 | 4.2 | 1.011 | 1.011 | available
73 | SS 110/35/10/6 kV Sovetskaya | 20+20+25+40 | 26.53 | 3.86 | 180 | 22.67 | 0 | 68.25 | 45.58 | 20.34 | available | 73 | SS 110/35/10/6 kV Sovetskaya | 20+20+25+40 | 9.2296 | 26.8496 | 3.86 | 180 | 22.9896 | 0 | 68.25 | 45.2604 | 17.8286 | available
| Nom. capacity MV -35kV; MVA | 20+20 | 4.57 | 6.74 | 90 | -2.17 | 0 | 21 | 23.17 |  |  |  | Nom. capacity MV -35kV; MVA | 20+20 | 5.3414 | 9.9114 | 6.74 | 90 | 3.1714 | 0 | 21 | 17.8286
| Nom. capacity LV-10kV; MVA | 25+40 | 8.91 | 3 | 180 | 5.91 | 0 | 26.25 | 20.34 |  |  |  | Nom. capacity LV-10kV; MVA | 25+40 | 0 | 8.91 | 3 | 180 | 5.91 | 0 | 26.25 | 20.34
| Nom. capacity LV-6kV; MVA | 20+20+40 | 13.05 | 3.86 | 180 | 9.19 | 0 | 42 | 32.81 |  |  |  | Nom. capacity LV-6kV; MVA | 20+20+40 | 3.8882 | 16.9382 | 3.86 | 180 | 13.0782 | 0 | 42 | 28.9218
74 | SS 35/10 kV Soskovskaya | 4+3,2 | 1.02 | 0.64 | 90 | 0.38 | 0 | 3.36 | 2.98 | 2.98 | available | 74 | SS 35/10 kV Soskovskaya | 4+3,2 | 0.014118 | 1.0341 | 0.64 | 90 | 0.39412 | 0 | 3.36 | 2.9659 | 2.9659 | available
75 | SS 35/10 kV Trosna | 5,6+3,2 | 0.76 | 1.76 | 30 | -1 | 0 | 3.36 | 4.36 | 4.36 | available | 75 | SS 35/10 kV Trosna | 5,6+3,2 | 0.049647 | 0.80965 | 1.76 | 30 | -0.95035 | 0 | 3.36 | 4.3104 | 4.3104 | available
76 | SS 110/10 kV Khimmash | 25+25 | 5.86 | 1.51 | 120 | 4.35 | 0 | 26.25 | 21.9 | 21.9 | available | 76 | SS 110/10 kV Khimmash | 25+25 | 4.1341 | 9.9941 | 1.51 | 120 | 8.4841 | 0 | 26.25 | 17.7659 | 17.7659 | available
77 | SS 35/10kV Khleboprodukty | 5,6+6,3 | 0.77 | 2.6 | 120 | -1.83 | 0 | 5.88 | 7.71 | 7.71 | available | 77 | SS 35/10kV Khleboprodukty | 5,6+6,3 | 0.014118 | 0.78412 | 2.6 | 120 | -1.8159 | 0 | 5.88 | 7.6959 | 7.6959 | available
78 | SS 35/10 kV Khotynetskaya | 4+2,5 | 2.05 | 1.49 | 80 | 0.56 | 0 | 2.625 | 2.065 | 2.065 | available | 78 | SS 35/10 kV Khotynetskaya | 4+2,5 | 0.77176 | 2.8218 | 1.49 | 80 | 1.3318 | 0 | 2.625 | 1.2932 | 1.2932 | available
79 | SS 35/10 kV Khotkovo | 1,6+1,6 | 0.47 | 1.03 | 80 | -0.56 | 0 | 1.68 | 2.24 | 2.24 | available | 79 | SS 35/10 kV Khotkovo | 1,6+1,6 | 0.0058824 | 0.47588 | 1.03 | 80 | -0.55412 | 0 | 1.68 | 2.2341 | 2.2341 | available
80 | SS 110/10/6 kV Tsentralnaya | 25+25 | 13.57 | 3.46 | 135 | 10.11 | 0 | 26.25 | 16.14 | 16.14 | available | 80 | SS 110/10/6 kV Tsentralnaya | 25+25 | 1.5294 | 15.0994 | 3.46 | 135 | 11.6394 | 0 | 26.25 | 14.6106 | 14.6106 | available
81 | SS 110/35/10 kV Shablykino | 6,3+6,3 | 2.14 | 1.36 | 30 | 0.78 | 0 | 6.615 | 5.835 | 5.835 | available | 81 | SS 110/35/10 kV Shablykino | 6,3+6,3 | 0 | 2.1935 | 1.36 | 30 | 0.83353 | 0 | 6.615 | 5.7815 | 5.7815 | available
| Nom. capacity MV, MVA | 6,3+6,3 | 0.76 | 0.54 | 30 | 0.22 | 0 | 6.615 | 6.395 |  |  |  | Nom. capacity MV, MVA | 6,3+6,3 | 0.035294 | 0.79529 | 0.54 | 30 | 0.25529 | 0 | 6.615 | 6.3597
| Nom. capacity LV, MVA | 6,3+6,3 | 1.38 | 0.82 | 30 | 0.56 | 0 | 6.615 | 6.055 |  |  |  | Nom. capacity LV, MVA | 6,3+6,3 | 0.018235 | 1.3982 | 0.82 | 30 | 0.57824 | 0 | 6.615 | 6.0368
82 | SS 110/35/10 kV Shakhovo | 10+10 | 2.48 | 2.55 | 120 | -0.07 | 0 | 10.5 | 10.57 | 10.4 | available | 82 | SS 110/35/10 kV Shakhovo | 10+10 | 5.075 | 7.555 | 2.55 | 120 | 5.005 | 0 | 10.5 | 5.495 | 5.495 | available
| Nom. capacity MV, MVA | 10+10 | 0.49 | 0.39 | 120 | 0.1 | 0 | 10.5 | 10.4 |  |  |  | Nom. capacity MV, MVA | 10+10 | 1.081 | 1.571 | 0.39 | 120 | 1.181 | 0 | 10.5 | 9.319
| Nom. capacity LV, MVA | 10+10 | 1.99 | 2.16 | 120 | -0.17 | 0 | 10.5 | 10.67 |  |  |  | Nom. capacity LV, MVA | 10+10 | 3.994 | 5.984 | 2.16 | 120 | 3.824 | 0 | 10.5 | 6.676
83 | SS 35/10 kV Shepino | 2,5+2,5 | 1.3 | 1.1 | 120 | 0.2 | 0 | 2.625 | 2.425 | 2.425 | available | 83 | SS 35/10 kV Shepino | 2,5+2,5 | 0.94765 | 2.2476 | 1.1 | 120 | 1.1476 | 0 | 2.625 | 1.4774 | 1.4774 | available
84 | SS 110/10/6 kV Yugo-Vostochnaya | 25+25 | 10.88 | 0.74 | 60 | 10.14 | 0 | 26.25 | 16.11 | 16.11 | available | 84 | SS 110/10/6 kV Yugo-Vostochnaya | 25+25 | 2.38 | 13.26 | 0.74 | 60 | 12.52 | 0 | 26.25 | 13.73 | 13.73 | available
85 | SS 110/10 kV Yuzhnaya | 10+10 | 4.61 | 1.05 | 90 | 3.56 | 0 | 10.5 | 6.94 | 6.94 | available | 85 | SS 110/10 kV Yuzhnaya | 10+10 | 3.747 | 8.357 | 1.05 | 90 | 7.307 | 0 | 10.5 | 3.193 | 3.193 | available
86 | SS 220/110/10 kV Mtsensk | 40+40 | 10.99 | 0 | - | 10.99 | 0 | 42 | 31.01 | 31.01 | available | 86 | SS 220/110/10 kV Mtsensk | 40+40 | 3.079 | 14.069 | 0 |  | 14.069 | 0 | 42 | 27.931 | 27.931 | available
87 | SS 110/35/10 kV Kommash | 10+16 | 10.46 | 4.65 | 90 | 5.81 | 0 | 10.5 | 4.69 | 4.69 | available | 87 | SS 110/35/10 kV Kommash | 10+16 | 4.461 | 14.921 | 4.65 | 90 | 10.271 | 0 | 10.5 | 0.229 | 0.229 | available
| Nom. capacity MV, MVA | 10+16 | 0 | 0 |  | 0 | 0 | 10.5 | 10.5 |  |  |  | Nom. capacity MV, MVA | 10+16 | 0 | 0 | 0 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, MVA | 10+16 | 10.46 | 4.65 | 90 | 5.81 | 0 | 10.5 | 4.69 |  |  |  | Nom. capacity LV, MVA | 10+16 | 4.461 | 14.921 | 4.65 | 90 | 10.271 | 0 | 10.5 | 0.229
88 | SS 110/35/10 kV Novosergievka | 6,3+10 | 1.6 | 4.13 | 120 | -2.53 | 0 | 6.615 | 9.145 | 7.535 | available | 88 | SS 110/35/10 kV Novosergievka | 6,3+10 | 0.33559 | 1.9356 | 4.13 | 120 | -2.1944 | 0 | 6.615 | 8.8094 | 7.1994 | available
| Nom. capacity MV, MVA | 6,3+10 | 1.48 | 2.4 | 120 | -0.92 | 0 | 6.615 | 7.535 |  |  |  | Nom. capacity MV, MVA | 6,3+10 | 0.33559 | 1.8156 | 2.4 | 120 | -0.58441 | 0 | 6.615 | 7.1994
| Nom. capacity LV, MVA | 6,3+10 | 0.12 | 1.73 | 120 | -1.61 | 0 | 6.615 | 8.225 |  |  |  | Nom. capacity LV, MVA | 6,3+10 | 0 | 0.12 | 1.73 | 120 | -1.61 | 0 | 6.615 | 8.225
89 | SS 110/10 kV 1 Voin | 6,3+6,3 | 2.14 | 1.83 | 120 | 0.31 | 0 | 6.615 | 6.305 | 6.305 | available | 89 | SS 110/10 kV 1 Voin | 6,3+6,3 | 1.6 | 3.74 | 1.83 | 120 | 1.91 | 0 | 6.615 | 4.705 | 4.705 | available
90 | SS 110/35/10 kV Zalegoshch | 10+16 | 4.87 | 3.95 | 120 | 0.92 | 0 | 10.5 | 9.58 | 9.39 | available | 90 | SS 110/35/10 kV Zalegoshch | 10+16 | 0.12824 | 4.9982 | 3.95 | 120 | 1.0482 | 0 | 10.5 | 9.4518 | 9.4518 | available
| Nom. capacity MV, MVA | 10+16 | 2.2 | 2.39 | 120 | -0.19 | 0 | 10.5 | 10.69 |  |  |  | Nom. capacity MV, MVA | 10+16 | 0.067059 | 2.2671 | 2.39 | 120 | -0.12294 | 0 | 10.5 | 10.6229
| Nom. capacity LV, MVA | 10+16 | 2.67 | 1.56 | 120 | 1.11 | 0 | 10.5 | 9.39 |  |  |  | Nom. capacity LV, MVA | 10+16 | 0.061176 | 2.7312 | 1.56 | 120 | 1.1712 | 0 | 10.5 | 9.3288
91 | SS 110/10 kV Kochety | 2,5+2,5 | 0.22 | 0.66 | 120 | -0.44 | 0 | 2.625 | 3.065 | 3.065 | available | 91 | SS 110/10 kV Kochety | 2,5+2,5 | 0.14471 | 0.36471 | 0.66 | 120 | -0.29529 | 0 | 2.625 | 2.9203 | 2.9203 | available
92 | SS 110/35/10 kV Bolkhov | 10+10 | 7.5 | 4.1 | 120 | 3.4 | 0 | 10.5 | 7.1 | 6.91 | available | 92 | SS 110/35/10 kV Bolkhov | 10+10 | 1.5206 | 9.0206 | 4.1 | 120 | 4.9206 | 0 | 10.5 | 5.5794 | 5.5794 | available
| Nom. capacity MV, MVA | 10+10 | 2.26 | 2.45 | 120 | -0.19 | 0 | 10.5 | 10.69 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.21853 | 2.4785 | 2.45 | 120 | 0.028529 | 0 | 10.5 | 10.4715
| Nom. capacity LV, MVA | 10+10 | 5.24 | 1.65 | 120 | 3.59 | 0 | 10.5 | 6.91 |  |  |  | Nom. capacity LV, MVA | 10+10 | 1.3021 | 6.5421 | 1.65 | 120 | 4.8921 | 0 | 10.5 | 5.6079
93 | SS 110/35/10 kV Novosil | 10+10 | 2.9 | 2.98 | 120 | -0.08 | 0 | 10.5 | 10.58 | 9.82 | available | 93 | SS 110/35/10 kV Novosil | 10+10 | 0.34082 | 3.2408 | 2.98 | 120 | 0.26082 | 0 | 10.5 | 10.2392 | 10.2392 | available
| Nom. capacity MV, MVA | 10+10 | 0.7 | 1.46 | 120 | -0.76 | 0 | 10.5 | 11.26 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.15882 | 0.85882 | 1.46 | 120 | -0.60118 | 0 | 10.5 | 11.1012
| Nom. capacity LV, MVA | 10+10 | 2.2 | 1.52 | 120 | 0.68 | 0 | 10.5 | 9.82 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.182 | 2.382 | 1.52 | 120 | 0.862 | 0 | 10.5 | 9.638
94 | SS 110/35/10 kV Znamenskaya | 10+10 | 1.8 | 1.78 | 120 | 0.02 | 0 | 10.5 | 10.48 | 10.32 | available | 94 | SS 110/35/10 kV Znamenskaya | 10+10 | 0 | 1.8 | 1.78 | 120 | 0.02 | 0 | 10.5 | 10.48 | 10.48 | available
| Nom. capacity MV, MVA | 10+10 | 0.52 | 0.34 | 120 | 0.18 | 0 | 10.5 | 10.32 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0 | 0.52 | 0.34 | 120 | 0.18 | 0 | 10.5 | 10.32
| Nom. capacity LV, MVA | 10+10 | 1.28 | 1.44 | 120 | -0.16 | 0 | 10.5 | 10.66 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0 | 1.28 | 1.44 | 120 | -0.16 | 0 | 10.5 | 10.66
95 | SS 35/10 kV Apalkovo | 1,8+1,8 | 0.51 | 0.48 | 120 | 0.03 | 0 | 1.89 | 1.86 | 1.86 | available | 95 | SS 35/10 kV Apalkovo | 1,8+1,8 | 0.021176 | 0.53118 | 0.48 | 120 | 0.051176 | 0 | 1.89 | 1.8388 | 1.8388 | available
96 | SS 35/10 kV Podberyozovo | 4+1 | 0.16 | 0.59 | 120 | -0.43 | 0 | 1.05 | 1.48 | 1.48 | available | 96 | SS 35/10 kV Podberyozovo | 4+1 | 0 | 0.16 | 0.59 | 120 | -0.43 | 0 | 1.05 | 1.48 | 1.48 | available
97 | SS 35/10 kV Protasovo | 2,5+1,6 | 1 | 0 |  | 1 | 0 | 1.68 | 0.68 | 0.68 | available | 97 | SS 35/10 kV Protasovo | 2,5+1,6 | 0 | 1 | 0 |  | 1 | 0 | 1.68 | 0.68 | 0.68 | available
98 | SS 35/10 kV Alyoshnya | 1+1 | 0.27 | 0.24 | 120 | 0.03 | 0 | 1.05 | 1.02 | 1.02 | available | 98 | SS 35/10 kV Alyoshnya | 1+1 | 0 | 0.27 | 0.24 | 120 | 0.03 | 0 | 1.05 | 1.02 | 1.02 | available
99 | SS 35/10 kV Lomovoe | 2,5+2,5 | 0.89 | 0 | - | 0.89 | 0 | 2.625 | 1.735 | 1.735 | available | 99 | SS 35/10 kV Lomovoe | 2,5+2,5 | 0 | 0.89 | 0 |  | 0.89 | 0 | 2.625 | 1.735 | 1.735 | available
100 | SS 35/10 kV Mokhovoe | 2,5+4 | 0.82 | 0.63 | 120 | 0.19 |  | 2.625 | 2.435 | 2.435 | available | 100 | SS 35/10 kV Mokhovoe | 2,5+4 | 0.054118 | 0.87412 | 0.63 | 120 | 0.24412 | 0 | 2.625 | 2.3809 | 2.3809 | available
101 | SS 35/10 kV Mishkovo 2 | 1,6+1,6 | 0.22 | 0.47 | 120 | -0.25 | 0 | 1.68 | 1.93 | 1.93 | available | 101 | SS 35/10 kV Mishkovo 2 | 1,6+1,6 | 0.012941 | 0.23294 | 0.47 | 120 | -0.23706 | 0 | 1.68 | 1.9171 | 1.9171 | available
102 | SS 35/10 kV Vyazovoe | 2,5+2,5 | 0.24 | 0 | - | 0.24 | 0 | 2.625 | 2.385 | 2.385 | available | 102 | SS 35/10 kV Vyazovoe | 2,5+2,5 | 0.0070588 | 0.24706 | 0 |  | 0.24706 | 0 | 2.625 | 2.3779 | 2.3779 | available
103 | SS 35/10 kV Krasnoznamenka | 2,5+2,5 | 0.67 | 0.67 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | available | 103 | SS 35/10 kV Krasnoznamenka | 2,5+2,5 | 0.045882 | 0.71588 | 0.67 | 120 | 0.045882 | 0 | 2.625 | 2.5791 | 2.5791 | available
104 | SS 35/10 kV Fatnevo | 1,6+1,6 | 0.35 | 0.37 | 120 | -0.02 | 0 | 1.68 | 1.7 | 1.7 | available | 104 | SS 35/10 kV Fatnevo | 1,6+1,6 | 0.0070588 | 0.35706 | 0.37 | 120 | -0.012941 | 0 | 1.68 | 1.6929 | 1.6929 | available
105 | SS 35/10 kV Varvarinka | 2,5+2,5 | 0.44 | 0.69 | 120 | -0.25 | 0 | 2.625 | 2.875 | 2.875 | available | 105 | SS 35/10 kV Varvarinka | 2,5+2,5 | 0.029412 | 0.46941 | 0.69 | 120 | -0.22059 | 0 | 2.625 | 2.8456 | 2.8456 | available
106 | SS 35/10 kV Odinok | 1,6+1,6 | 0.28 | 0 | - | 0.28 | 0 | 1.68 | 1.4 | 1.4 | available | 106 | SS 35/10 kV Odinok | 1,6+1,6 | 0.06 | 0.34 | 0 |  | 0.34 | 0 | 1.68 | 1.34 | 1.34 | available
107 | SS 35/10 kV Uzkoe | 1,6+1 | 0.23 | 0.25 | 120 | -0.02 | 0 | 1.05 | 1.07 | 1.07 | available | 107 | SS 35/10 kV Uzkoe | 1,6+1 | 0 | 0.23 | 0.25 | 120 | -0.02 | 0 | 1.05 | 1.07 | 1.07 | available
108 | SS 35/10 kV Korsakovo | 2,5+4 | 0.92 | 0.69 | 120 | 0.23 | 0 | 2.625 | 2.395 | 2.395 | available | 108 | SS 35/10 kV Korsakovo | 2,5+4 | 0.36235 | 1.2824 | 0.69 | 120 | 0.59235 | 0 | 2.625 | 2.0326 | 2.0326 | available
109 | SS 35/10 kV Paramonovo | 4+2,5 | 0.81 | 0.76 | 120 | 0.05 | 0 | 2.625 | 2.575 | 2.575 | available | 109 | SS 35/10 kV Paramonovo | 4+2,5 | 0.069412 | 0.87941 | 0.76 | 120 | 0.11941 | 0 | 2.625 | 2.5056 | 2.5056 | available
110 | SS 35/10 kV Speshnevo | 1,6+1,6 | 0.16 | 0 | - | 0.16 | 0 | 1.68 | 1.52 | 1.52 | available | 110 | SS 35/10 kV Speshnevo | 1,6+1,6 | 0.031765 | 0.19176 | 0 |  | 0.19176 | 0 | 1.68 | 1.4882 | 1.4882 | available
111 | SS 110/35/10 kV Verkhovye I | 16+10 | 7.3 | 3.65 | 120 | 3.65 | 0 | 10.5 | 6.85 | 6.85 | available | 111 | SS 110/35/10 kV Verkhovye I | 16+10 | 0.37276 | 7.6728 | 3.65 | 120 | 4.0228 | 0 | 10.5 | 6.4772 | 6.4772 | available
| Nom. capacity MV, MVA | 16+10 | 2.47 | 2.05 | 120 | 0.42 | 0 | 10.5 | 10.08 |  |  |  | Nom. capacity MV, MVA | 16+10 | 0.31394 | 2.7839 | 2.05 | 120 | 0.73394 | 0 | 10.5 | 9.7661
| Nom. capacity LV, MVA | 16+10 | 4.83 | 1.6 | 120 | 3.23 | 0 | 10.5 | 7.27 |  |  |  | Nom. capacity LV, MVA | 16+10 | 0.058824 | 4.8888 | 1.6 | 120 | 3.2888 | 0 | 10.5 | 7.2112
112 | SS 110/35/10 kV Verkhovye II | 40+40 | 10.32 | 0.3 | - | 10.02 | 0 | 42 | 31.98 | 31.98 | available | 112 | SS 110/35/10 kV Verkhovye II | 40+40 | 0.014118 | 10.3341 | 0.3 |  | 10.0341 | 0 | 42 | 31.9659 | 31.9659 | available
| Nom. capacity MV, MVA | 40+40 | 0.38 | 0.3 | - | 0.08 | 0 | 42 | 41.92 |  |  |  | Nom. capacity MV, MVA | 40+40 | 0.014118 | 0.39412 | 0.3 |  | 0.094118 | 0 | 42 | 41.9059
| Nom. capacity LV, MVA | 40+40 | 9.94 | 0 | - | 9.94 | 0 | 42 | 32.06 |  |  |  | Nom. capacity LV, MVA | 40+40 | 0 | 9.94 | 0 |  | 9.94 | 0 | 42 | 32.06
113 | SS 110/35/10 kV Dolgoe | 16+10 | 4.83 | 3.38 | 120 | 1.45 | 0 | 10.5 | 9.05 | 8.78 | available | 113 | SS 110/35/10 kV Dolgoe | 16+10 | 0.51476 | 5.3448 | 3.38 | 120 | 1.9648 | 0 | 10.5 | 8.5352 | 8.3229 | available
| Nom. capacity MV, MVA | 16+10 | 2.11 | 2.38 | 120 | -0.27 | 0 | 10.5 | 10.77 |  |  |  | Nom. capacity MV, MVA | 16+10 | 0.057647 | 2.1676 | 2.38 | 120 | -0.21235 | 0 | 10.5 | 10.7124
| Nom. capacity LV, MVA | 16+10 | 2.72 | 1 | 120 | 1.72 | 0 | 10.5 | 8.78 |  |  |  | Nom. capacity LV, MVA | 16+10 | 0.45712 | 3.1771 | 1 | 120 | 2.1771 | 0 | 10.5 | 8.3229
114 | SS 110/35/10 kV Kolpny-110 | 10+16 | 4.6 | 2.79 | 120 | 1.81 | 0 | 10.5 | 8.69 | 8.69 | available | 114 | SS 110/35/10 kV Kolpny-110 | 10+16 | 0.28824 | 4.8882 | 2.79 | 120 | 2.0982 | 0 | 10.5 | 8.4018 | 8.8565 | available
| Nom. capacity MV, MVA | 10+16 | 2.75 | 2.46 | 120 | 0.29 | 0 | 10.5 | 10.21 |  |  |  | Nom. capacity MV, MVA | 10+16 | 0.16471 | 2.9147 | 2.46 | 120 | 0.45471 | 0 | 10.5 | 10.0453
| Nom. capacity LV, MVA | 10+16 | 1.85 | 0.33 | 120 | 1.52 | 0 | 10.5 | 8.98 |  |  |  | Nom. capacity LV, MVA | 10+16 | 0.12353 | 1.9735 | 0.33 | 120 | 1.6435 | 0 | 10.5 | 8.8565
115 | SS 110/35/10 kV Kr. Zarya | 10+10 | 4.18 | 1.54 | 120 | 2.64 | 0 | 10.5 | 7.86 | 7.86 | available | 115 | SS 110/35/10 kV Kr. Zarya | 10+10 | 0 | 4.18 | 1.54 | 120 | 2.64 | 0 | 10.5 | 7.86 | 7.86 | available
| Nom. capacity MV, MVA | 10+10 | 1.54 | 1.29 | 120 | 0.25 | 0 | 10.5 | 10.25 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0 | 1.54 | 1.29 | 120 | 0.25 | 0 | 10.5 | 10.25
| Nom. capacity LV, MVA | 10+10 | 2.64 | 0.25 | 120 | 2.39 | 0 | 10.5 | 8.11 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0 | 2.64 | 0.25 | 120 | 2.39 | 0 | 10.5 | 8.11
116 | SS 110/35/10 kV Pokrovskaya | 10+10 | 5.52 | 2.84 | 120 | 2.68 | 0 | 10.5 | 7.82 | 7.82 | available | 116 | SS 110/35/10 kV Pokrovskaya | 10+10 | 2.2577 | 7.7777 | 2.84 | 120 | 4.9377 | 0 | 10.5 | 5.5623 | 5.5623 | available
| Nom. capacity MV, MVA | 10+10 | 2.73 | 2.12 | 120 | 0.61 | 0 | 10.5 | 9.89 |  |  |  | Nom. capacity MV, MVA | 10+10 | 0.16971 | 2.8997 | 2.12 | 120 | 0.77971 | 0 | 10.5 | 9.7203
| Nom. capacity LV, MVA | 10+10 | 2.79 | 0.72 | 120 | 2.07 | 0 | 10.5 | 8.43 |  |  |  | Nom. capacity LV, MVA | 10+10 | 2.088 | 4.878 | 0.72 | 120 | 4.158 | 0 | 10.5 | 6.342
117 | SS 110/35/6 kV Cherkasskaya | 40+25 | 27.05 | 13.39 | 120 | 13.66 | 0 | 26.25 | 12.59 | 12.59 | available | 117 | SS 110/35/6 kV Cherkasskaya | 40+25 | 2.3801 | 29.4301 | 13.39 | 120 | 16.0401 | 0 | 26.25 | 10.2099 | 10.2099 | available
| Nom. capacity MV, MVA | 40+25 | 19.55 | 10.84 | 120 | 8.71 | 0 | 26.25 | 17.54 |  |  |  | Nom. capacity MV, MVA | 40+25 | 2.3801 | 21.9301 | 10.84 | 120 | 11.0901 | 0 | 26.25 | 15.1599
| Nom. capacity LV, MVA | 40+25 | 7.5 | 2.55 | 120 | 4.95 | 0 | 26.25 | 21.3 |  |  |  | Nom. capacity LV, MVA | 40+25 | 0 | 7.5 | 2.55 | 120 | 4.95 | 0 | 26.25 | 21.3
118 | SS 110/6 kV Plastmass | 16+16 | 9.76 | 0 | - | 9.76 | 0 | 16.8 | 7.04 | 7.04 | available | 118 | SS 110/6 kV Plastmass | 16+16 | 0 | 9.76 | 0 |  | 9.76 | 0 | 16.8 | 7.04 | 7.04 | available
119 | SS 110/10 kV PM | 10+10 | 5.02 | 0 | - | 5.02 | 0 | 10.5 | 5.48 | 5.48 | available | 119 | SS 110/10 kV PM | 10+10 | 1.4118 | 6.4318 | 0 |  | 6.4318 | 0 | 10.5 | 4.0682 | 4.0682 | available
120 | SS 110/10 kV Rechitsa | 6,3+6,3 | 0.99 | 1.85 | 120 | -0.86 | 0 | 6.615 | 7.475 | 7.475 | available | 120 | SS 110/10 kV Rechitsa | 6,3+6,3 | 0.052 | 1.042 | 1.85 | 120 | -0.808 | 0 | 6.615 | 7.423 | 7.423 | available
121 | SS 110/10 kV R.Brod | 5,6+10 | 1.34 | 0.29 | 120 | 1.05 | 0 | 5.88 | 4.83 | 4.83 | available | 121 | SS 110/10 kV R.Brod | 5,6+10 | 0.038824 | 1.3788 | 0.29 | 120 | 1.0888 | 0 | 5.88 | 4.7912 | 4.7912 | available
122 | SS 35/10 kV Alekseevskaya | 1,6+1,6 | 0.67 | 0.13 | 120 | 0.54 | 0 | 1.68 | 1.14 | 1.14 | available | 122 | SS 35/10 kV Alekseevskaya | 1,6+1,6 | 0.054706 | 0.72471 | 0.13 | 120 | 0.59471 | 0 | 1.68 | 1.0853 | 1.0853 | available
123 | SS 35/10 kV V.Dubrava | 2,5+2,5 | 1.33 | 0.65 | 120 | 0.68 | 0 | 2.625 | 1.945 | 1.945 | available | 123 | SS 35/10 kV V.Dubrava | 2,5+2,5 | 0.06 | 1.39 | 0.65 | 120 | 0.74 | 0 | 2.625 | 1.885 | 1.885 | available
124 | SS 35/10 kV V.Olshanoe | 4+2,5 | 0.46 | 0.43 | 120 | 0.03 | 0 | 2.625 | 2.595 | 2.595 | available | 124 | SS 35/10 kV V.Olshanoe | 4+2,5 | 0.0082353 | 0.46824 | 0.43 | 120 | 0.038235 | 0 | 2.625 | 2.5868 | 2.5868 | available
125 | SS 35/10 kV Vvedenskoe | 1,6+1,8 | 0.55 | 0.56 | 120 | -0.01 | 0 | 1.68 | 1.69 | 1.69 | available | 125 | SS 35/10 kV Vvedenskoe | 1,6+1,8 | 0.0058824 | 0.55588 | 0.56 | 120 | -0.0041176 | 0 | 1.68 | 1.6841 | 1.6841 | available
126 | SS 35/10 kV Droskovo | 4+2,5 | 1.44 | 0 | - | 1.44 | 0 | 2.625 | 1.185 | 1.185 | available | 126 | SS 35/10 kV Droskovo | 4+2,5 | 0.115 | 1.555 | 0 |  | 1.555 | 0 | 2.625 | 1.07 | 1.07 | available
127 | SS 35/10 kV Kolpny-35 | 6,3+6,3 | 1.03 | 0.39 | 120 | 0.64 | 0 | 6.615 | 5.975 | 5.975 | available | 127 | SS 35/10 kV Kolpny-35 | 6,3+6,3 | 0.017647 | 1.0476 | 0.39 | 120 | 0.65765 | 0 | 6.615 | 5.9574 | 5.9574 | available
128 | SS 35/10 kV Krutoe | 2,5+2,5 | 1.84 | 0.87 | 120 | 0.97 | 0 | 2.625 | 1.655 | 1.655 | available | 128 | SS 35/10 kV Krutoe | 2,5+2,5 | 0.088 | 1.928 | 0.87 | 120 | 1.058 | 0 | 2.625 | 1.567 | 1.567 | available
129 | SS 35/10 kV Mezentsevo | 4+6,3 | 2.13 | 1.11 | 80 | 1.02 | 0 | 4.2 | 3.18 | 3.18 | available | 129 | SS 35/10 kV Mezentsevo | 4+6,3 | 0.12588 | 2.2559 | 1.11 | 80 | 1.1459 | 0 | 4.2 | 3.0541 | 3.0541 | available
130 | SS 35/10 kV N.Zhernovets | 1,6+1,6 | 0.11 | 0 | - | 0.11 | 0 | 1.68 | 1.57 | 1.57 | available | 130 | SS 35/10 kV N.Zhernovets | 1,6+1,6 | 0 | 0.11 | 0 |  | 0.11 | 0 | 1.68 | 1.57 | 1.57 | available
131 | SS 35/10 kV Netrubezh | 2,5+2,5 | 0.46 | 0.39 | - | 0.07 | 0 | 2.625 | 2.555 | 2.555 | available | 131 | SS 35/10 kV Netrubezh | 2,5+2,5 | 0.0094118 | 0.46941 | 0.39 |  | 0.079412 | 0 | 2.625 | 2.5456 | 2.5456 | available
132 | SS 35/10 kV Nikolskaya | 2,5+3,2 | 1.48 | 0.54 | 80 | 0.94 | 0 | 2.625 | 1.685 | 1.685 | available | 132 | SS 35/10 kV Nikolskaya | 2,5+3,2 | 0.052941 | 1.5329 | 0.54 | 80 | 0.99294 | 0 | 2.625 | 1.6321 | 1.6321 | available
133 | SS 35/10 kV Pesochnaya | 3,2+3,2 | 0.38 | 1.67 | 120 | -1.29 | 0 | 3.36 | 4.65 | 4.65 | available | 133 | SS 35/10 kV Pesochnaya | 3,2+3,2 | 0.014118 | 0.39412 | 1.67 | 120 | -1.2759 | 0 | 3.36 | 4.6359 | 4.6359 | available
134 | SS 35/6 kV Pushkarskaya | 4+4 | 5.35 | 0 |  | 5.35 | 0 | 4.2 | -1.15 | -1.15 | unavailable | 134 | SS 35/6 kV Pushkarskaya | 4+4 | 0 | 5.35 | 0 |  | 5.35 | 0 | 4.2 | -1.15 | -1.15 | unavailable
135 | SS 35/10 kV Rakhmanovo | 2,5+2,5 | 0.43 | 0.25 | 120 | 0.18 | 0 | 2.625 | 2.445 | 2.445 | available | 135 | SS 35/10 kV Rakhmanovo | 2,5+2,5 | 0 | 0.43 | 0.25 | 120 | 0.18 | 0 | 2.625 | 2.445 | 2.445 | available
136 | SS 35/10 kV Rosstani | 2,5+2,5 | 1.44 | 0.7 | 80 | 0.74 | 0 | 2.625 | 1.885 | 1.885 | available | 136 | SS 35/10 kV Rosstani | 2,5+2,5 | 0.04 | 1.48 | 0.7 | 80 | 0.78 | 0 | 2.625 | 1.845 | 1.845 | available
137 | SS 35/10 kV Sergievskaya | 4+2,5 | 1.24 | 1.5 | 120 | -0.26 | 0 | 2.625 | 2.885 | 2.885 | available | 137 | SS 35/10 kV Sergievskaya | 4+2,5 | 0.612 | 1.852 | 1.5 | 120 | 0.352 | 0 | 2.625 | 2.273 | 2.273 | available
138 | SS 35/10 kV Skorodnoe | 1,6+1,6 | 0.59 | 0.33 | 120 | 0.26 | 0 | 1.68 | 1.42 | 1.42 | available | 138 | SS 35/10 kV Skorodnoe | 1,6+1,6 | 0.021 | 0.611 | 0.33 | 120 | 0.281 | 0 | 1.68 | 1.399 | 1.399 | available
139 | SS 35/10 kV Spasskaya | 2,5+1,6 | 0.34 | 0 | 120 | 0.34 | 0 | 1.68 | 1.34 | 1.34 | available | 139 | SS 35/10 kV Spasskaya | 2,5+1,6 | 0.017647 | 0.35765 | 0 |  | 0.35765 | 0 | 1.68 | 1.3224 | 1.3224 | available
140 | SS 35/10 kV SSK | 1,6+1,6 | 0.09 | 0 |  | 0.09 | 0 | 1.68 | 1.59 | 1.59 | available | 140 | SS 35/10 kV SSK | 1,6+1,6 | 0 | 0.09 | 0 |  | 0.09 | 0 | 1.68 | 1.59 | 1.59 | available
141 | SS 35/10 kV Urynok | 1,6+1,6 | 1.08 | 0.52 | 20 | 0.56 | 0 | 1.68 | 1.12 | 1.12 | available | 141 | SS 35/10 kV Urynok | 1,6+1,6 | 0.029412 | 1.1094 | 0.52 | 20 | 0.58941 | 0 | 1.68 | 1.0906 | 1.0906 | available
142 | SS 35/10 kV Khomutovo | 4+4 | 1.89 | 0.31 | 80 | 1.58 | 0 | 4.2 | 2.62 | 2.62 | available | 142 | SS 35/10 kV Khomutovo | 4+4 | 0.29294 | 2.1829 | 0.31 | 80 | 1.8729 | 0 | 4.2 | 2.3271 | 2.3271 | available
| Total: | [10 empty] | 2: Total:; 4: 127.5024; 5: 678.9921
| deficit | [8 empty] | -1.95 |  | 2: deficit; Min 12: -10.0694
| proficit | [8 empty] | 628.35 |  | 2: proficit; Min 12: 487.2743
* | Substations are not assets of the division, but IDGC of Center - Orelenergo issues technical specifications for customer connections.
SWG-10kV SS Mtsensk is in sublease, and SS Pischevaya is actually ownerless.

## Total current deficit
The list of closed supply centers of IDGC of Centre - Orelenergo division in winter 2010 (current deficit of capacity).
Item # | Name of supply center, voltage class | [7 empty] | Current deficit, MVA
Orelenergo
1 | SS 110/35/10 kV Novopolevo | 16 | [6 empty] | -0.4
| Nom. capacity MV, MVA | 16
| Nom. capacity LV, MVA | 16
2 | SS 110/35/10 kV Trosna | 16 | [6 empty] | -0.02
| Nom. capacity MV, MVA | 16
| Nom. capacity LV, MVA | 16
3 | SS 110/10 kV Telchye | 3.2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | -0.17
4 | SS 35/6 kV Pushkarskaya | 4+4 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | -1.15
5 | SS 110/35/10 kV Shatilovo | 10 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | -0.21
| Nom. capacity MV, MVA | 10 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Nom. capacity LV, MVA | 10 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Total current deficit |  | 53.2 | [6 empty] | -1.95

## Total expected deficit
The list of closed supply centers of IDGC of Centre - Orelenergo with expected load taking into account new connections and other development of the electical networks.
Item # | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number provided that technical requirements at connections or other measures performed for reconstruction of the supply center, pcs/ MVA | Дополнительная мощность по выданным ТУ на ТП, МВА | Ожидаемая нагрузка ЦП, МВА | Полная перераспределяемая мощность в перспективе с учетом выполнения мероприятий ТУ или других мероприятий по реконструкции сети инвестпрограмм и др. |  | Полная мощность с учётом перераспределения, МВА | Ограничивающие факторы, МВА | Допустимая нагрузка расчётная в режиме n-1, МВА | Пропускная способность ЦП, МВА | Current deficit/proficit, MVA
[5 empty] | МВА | Мин.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 4 | 5
Orelenergo
1 | SS 110/35/10 kV Maloarkhangelskaya | 10 | [6 empty] | #REF! |  | -1.0765 | unavailable
| Nom. capacity MV, MVA | 10
| Nom. capacity LV, MVA | 10
2 | SS 110/35/10 kV Novopolevo | 16 | [6 empty] | #REF! |  | -0.27265 | unavailable
| Nom. capacity MV, MVA | 16
| Nom. capacity LV, MVA | 16
3 | SS 110/10 kV Pishchevaya | 6.3 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | -0.766 | unavailable
4 | SS 110/10 kV Telchye | 3.2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | -0.39353 | unavailable
5 | SS 110/35/10 kV Shatilovo | 10 | [6 empty] | #REF! |  | -0.31471 | unavailable
| Nom. capacity MV, MVA | 10
| Nom. capacity LV, MVA | 10
6 | SS 110/10 kV Volodarskaya | 2,5+6,3 | [8 empty] | -5.141 | unavailable
7 | SS 35/6 kV Pushkarskaya | 4+4 | [8 empty] | -1.15 | unavailable
8 | SS 110/35/10 kV Trosna | 16 | [8 empty] | -0.132 | unavailable
| Nom. capacity MV, MVA | 16
| Nom. capacity LV, MVA | 16
9 | SS 35/10 kV Zvyaginki | 2,5+2,5 | [8 empty] | -0.823 | unavailable
10 | SS 110/35/10 kV Kulikovskaya | 10+10 | [8 empty] | -0.27365 | unavailable
| Total: | 83.3 | [8 empty] | -10.343