## Yaroslavl
Transmission capacity of supply centres of IDGC of Center - Yarenergo following the winter peak load measurements in 2010
[13 empty] | table 1 | [13 empty] | table 2
No. | Name of supply center, voltage class | Current deficit | [12 empty] | Note | No. | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Установленная мощность первого трансформатора. МВА | Установленная мощность второго трансформатора. МВА | Summary total capacity of supply centers following the results of measurements of load maximal Sмаx, MVA | ячейки скрыть |  | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Supply Center deficit/proficit, MVA |  |  |  |  | Installed power capacity of transformers Sinst. including their number, when performing retrofit at the TS or other activities to retrofit the Supply Center pcs./ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load of Supply Center, MVA | Total redistributed power capacity of transformers Sinst. including their number, when performing retrofit at the TS or other activities |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Supply Center deficit/proficit, MVA
[5 empty] | MVA |  |  | MVA | Min | [11 empty] | MVA | Min
1 | 2 | 3 |  |  | 4 | Т-1 | Т-2 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | SS 35/10 Matveevo | 1.6 | 1.6 |  | 0.26 | 0.26 |  | 0.779 | 1 day and night | 0.26 | 0 | 0.779 | 0.519 | 0.519 | available | 1 | SS 35/10 Matveevo | 1.6 | 0.025 | 0.285 | 0.779 | 1 day and night | 0.285 | 0 | 0.779 | 0.494 | 0.494 | available
2 | SS 35/10 Mikhailovskoe | 6.3 | 6.3 |  | 1.11 | 1.11 |  | 6.62 | 1 day and night | 1.11 | 0 | 6.62 | 5.51 | 5.51 | available | 2 | SS 35/10 Mikhailovskoe | 6.3 | 0.003 | 1.113 | 6.62 | 1 day and night | 1.113 | 0 | 6.62 | 5.507 | 5.507 | available
3 | SS 35/10 Shirinye | 2.5 | 2.5 |  | 2.15 |  | 2.15 | 1.68 | 1 day and night | 2.15 | 0 | 1.68 | -0.47 | -0.47 | unavailable | 3 | SS 35/10 Shirinye | 2.5 | 0.356 | 2.506 | 1.68 | 1 day and night | 2.506 | 0 | 1.68 | -0.826 | -0.826 | unavailable
4 | SS 110/10 Pokrov | 2.5 | 2.5 |  | 0.27 | 0.27 |  | 1.282 | 1 day and night | 0.27 | 0 | 1.282 | 1.012 | 1.012 | available | 4 | SS 110/10 Pokrov | 2.5 | 0.036 | 0.306 | 1.282 | 1 day and night | 0.306 | 0 | 1.282 | 0.976 | 0.976 | available
5 | SS 35/10 Obnora | 1.6 | 1.6 |  | 0.2 | 0.2 |  | 1.212 | 1 day and night | 0.2 | 0 | 1.212 | 1.012 | 1.012 | available | 5 | SS 35/10 Obnora | 1.6 | 0.063 | 0.263 | 1.212 | 1 day and night | 0.263 | 0 | 1.212 | 0.949 | 0.949 | available
6 | SS 110/35/10 Abbakumtsevo | 10+10 | 10 | 10 | 10.09 |  |  |  |  | 10.09 | 0 | 10.5 | 0.41 | 0.41 | available | 6 | SS 110/35/10 Abbakumtsevo | 10+10 |  | 22.7631 |  |  | 22.7631 | 0 | 10.5 | -12.2631 | -12.2631 | unavailable
| Nom. capacity MV, МVА | 10+10 |  |  | 8.12 | 2.26 | 5.86 |  |  | 8.12 | 0 | 10.5 | 2.38 |  |  |  | Nom. capacity MV, МVА | 10+10 |  | 18.4206 |  |  | 18.4206 | 0 | 10.5 | -7.9206
| Nom. capacity LV, МVА | 10+10 |  |  | 1.97 | 0.7 | 1.27 |  |  | 1.97 | 0 | 10.5 | 8.53 |  |  |  | Nom. capacity LV, МVА | 10+10 | 2.3725 | 4.3425 |  |  | 4.3425 | 0 | 10.5 | 6.1575
7 | SS 35/10 Ananyino | 1,6+1,6 | 1.6 | 1.6 | 1.31 | 0.82 | 0.49 |  |  | 1.31 | 0 | 1.68 | 0.37 | 0.37 | available | 7 | SS 35/10 Ananyino | 1,6+1,6 | 1.142 | 2.452 |  |  | 2.452 | 0 | 1.68 | -0.772 | -0.772 | unavailable
8 | SS 110/10/10 Bragino | 40+40 | 40 | 40 | 34.91 | 15.54 | 19.37 | 2.338 | 120 | 32.572 | 0 | 42 | 9.428 | 9.428 | available | 8 | SS 110/10/10 Bragino | 40+40 | 4.074 | 38.984 | 2.338 | 120 | 36.646 | 0 | 42 | 5.354 | 5.354 | available
9 | SS 35/10 Burmakino-1 | 4,0+4,0 | 4 | 4 | 2.03 | 0.75 | 1.28 | 0.554 | 120 | 1.476 | 0 | 4.2 | 2.724 | 2.724 | available | 9 | SS 35/10 Burmakino-1 | 4,0+4,0 | 1.209 | 3.239 | 0.554 | 120 | 2.685 | 0 | 4.2 | 1.515 | 1.515 | available
10 | SS 35/10 Vatolino | 4,0+4,0 | 4 | 4 | 3.42 | 1.62 | 1.8 |  |  | 3.42 | 0 | 4.2 | 0.78 | 0.78 | available | 10 | SS 35/10 Vatolino | 4,0+4,0 | 4.75 | 8.17 |  |  | 8.17 | 0 | 4.2 | -3.97 | -3.97 | unavailable
11 | SS 35/6 Vederniki | 6,3+6,3 | 6.3 | 6.3 | 4.12 | 1.46 | 2.66 |  |  | 4.12 | 0 | 6.62 | 2.5 | 2.5 | available | 11 | SS 35/6 Vederniki | 6,3+6,3 | 0.091258 | 4.2113 |  |  | 4.2113 | 0 | 6.62 | 2.4087 | 2.4087 | available
12 | SS 35/10 Velikovskaya | 4,0+4,0 | 4 | 4 | 1.97 | 1.13 | 0.84 |  |  | 1.97 | 0 | 4.2 | 2.23 | 2.23 | available | 12 | SS 35/10 Velikovskaya | 4,0+4,0 | 0.139 | 2.109 |  |  | 2.109 | 0 | 4.2 | 2.091 | 2.091 | available
13 | SS 35/10 Velikoe Selo | 1,6+1,6 | 1.6 | 1.6 | 0.71 | 0.61 | 0.1 |  |  | 0.71 | 0 | 1.68 | 0.97 | 0.97 | available | 13 | SS 35/10 Velikoe Selo | 1,6+1,6 | 0.077 | 0.787 |  |  | 0.787 | 0 | 1.68 | 0.893 | 0.893 | available
14 | SS 35/10 Vozrozhdenie | 4,0+4,0 | 4 | 4 | 1.17 | 0.36 | 0.81 |  |  | 1.17 | 0 | 4.2 | 3.03 | 3.03 | available | 14 | SS 35/10 Vozrozhdenie | 4,0+4,0 | 3.2144 | 4.3844 |  |  | 4.3844 | 0 | 4.2 | -0.1844 | -0.1844 | unavailable
15 | SS 35/10 Volna | 4,0+2,5 | 4 | 2.5 | 2.53 | 1.21 | 1.32 |  |  | 2.53 | 0 | 2.63 | 0.1 | 0.1 | available | 15 | SS 35/10 Volna | 4,0+2,5 | 0.066 | 2.596 |  |  | 2.596 | 0 | 2.63 | 0.034 | 0.034 | available
16 | SS 35/10 Vyatskoe | 2,5+2,5 | 2.5 | 2.5 | 2.21 | 1.04 | 1.17 | 0.139 | 120 | 2.071 | 0 | 2.63 | 0.559 | 0.559 | available | 16 | SS 35/10 Vyatskoe | 2,5+2,5 | 0.339 | 2.549 | 0.139 | 120 | 2.41 | 0 | 2.63 | 0.22 | 0.22 | available
17 | SS 35/10 Gorinskaya | 2,5+2,5 | 2.5 | 2.5 | 0.66 | 0.34 | 0.32 | 0.329 | 120 | 0.331 | 0 | 2.63 | 2.299 | 2.299 | available | 17 | SS 35/10 Gorinskaya | 2,5+2,5 | 0.102 | 0.762 | 0.329 | 120 | 0.433 | 0 | 2.63 | 2.197 | 2.197 | available
18 | SS 35/10 Grigoryevskoe | 4,0+4,0 | 4 | 4 | 2.61 | 1.11 | 1.5 | 0.312 | 120 | 2.298 | 0 | 4.2 | 1.902 | 1.902 | available | 18 | SS 35/10 Grigoryevskoe | 4,0+4,0 | 1.0095 | 3.6195 | 0.312 | 120 | 3.3075 | 0 | 4.2 | 0.8925 | 0.8925 | available
19 | SS 35/10 Guzitsino | 4,0+4,0 | 4 | 4 | 2.87 | 1.2 | 1.67 | 0.866 | 120 | 2.004 | 0 | 4.2 | 2.196 | 2.196 | available | 19 | SS 35/10 Guzitsino | 4,0+4,0 | 5.6609 | 8.5309 | 0.866 | 120 | 7.6649 | 0 | 4.2 | -3.4649 | -3.4649 | unavailable
20 | SS 35/10 State Fire-Fighting Service Yaroslavl | 6,3+6,3 | 6.3 | 6.3 | 2.56 | 2.25 | 0.31 |  |  | 2.56 | 0 | 6.62 | 4.06 | 4.06 | available | 20 | SS 35/10 State Fire-Fighting Service Yaroslavl | 6,3+6,3 | 0 | 2.56 |  |  | 2.56 | 0 | 6.62 | 4.06 | 4.06 | available
21 | SS 110/6 Depo | 16+16 | 16 | 16 | 7.07 | 4.28 | 2.79 |  |  | 7.07 | 0 | 16.8 | 9.73 | 9.73 | available | 21 | SS 110/6 Depo | 16+16 | 2.7285 | 9.7985 |  |  | 9.7985 | 0 | 16.8 | 7.0015 | 7.0015 | available
22 | SS 35/10 Dorozhaevo | 1,6+1,6 | 1.6 | 1.6 | 1.59 | 0.56 | 1.03 | 1.039 | 120 | 0.551 | 0 | 1.68 | 1.129 | 1.129 | available | 22 | SS 35/10 Dorozhaevo | 1,6+1,6 | 1.976 | 3.566 | 1.039 | 120 | 2.527 | 0 | 1.68 | -0.847 | -0.847 | unavailable
23 | SS 110/10 Druzhba | 16+16 | 16 | 16 | 5.51 | 1.77 | 3.74 | 1.932 | 120 | 3.578 | 0 | 16.8 | 13.222 | 13.222 | available | 23 | SS 110/10 Druzhba | 16+16 | 0.8133 | 6.3233 | 1.932 | 120 | 4.3913 | 0 | 16.8 | 12.4087 | 12.4087 | available
24 | SS 35/10 Dubki | 6,3+6,3 | 6.3 | 6.3 | 4.87 | 2.91 | 1.96 | 1.386 | 120 | 3.484 | 0 | 6.62 | 3.136 | 3.136 | available | 24 | SS 35/10 Dubki | 6,3+6,3 | 1.4935 | 6.3635 | 1.386 | 120 | 4.9775 | 0 | 6.62 | 1.6425 | 1.6425 | available
25 | SS 35/10 Dybino | 2,5+2,5 | 2.5 | 2.5 | 1.23 | 0.7 | 0.53 |  |  | 1.23 | 0 | 2.63 | 1.4 | 1.4 | available | 25 | SS 35/10 Dybino | 2,5+2,5 | 0.557 | 1.787 |  |  | 1.787 | 0 | 2.63 | 0.843 | 0.843 | available
26 | SS 35/6 Zavolzhskaya | 10+10 | 10 | 10 | 9.72 | 2.85 | 6.87 |  |  | 9.72 | 0 | 10.5 | 0.78 | 0.78 | available | 26 | SS 35/6 Zavolzhskaya | 10+10 | 0.7921 | 10.5121 |  |  | 10.5121 | 0 | 10.5 | -0.012098 | -0.012098 | unavailable
27 | SS 110/6/6 Institutskaya | 40+40 | 40 | 40 | 31.83 | 18.69 | 13.14 |  |  | 31.83 | 0 | 42 | 10.17 | 10.17 | available | 27 | SS 110/6/6 Institutskaya | 40+40 | 2.5747 | 34.4047 |  |  | 34.4047 | 0 | 42 | 7.5953 | 7.5953 | available
28 | SS 35/10 Koza | 1,6+1,6 | 1.6 | 1.6 | 0.3 | 0.07 | 0.23 | 0.052 | 120 | 0.248 | 0 | 1.68 | 1.432 | 1.432 | available | 28 | SS 35/10 Koza | 1,6+1,6 | 0.063 | 0.363 | 0.052 | 120 | 0.311 | 0 | 1.68 | 1.369 | 1.369 | available
29 | SS 110/35/6 Konstantinovo | 20+16 | 20 | 16 | 10.56 |  |  | 0.021 | 120 | 10.539 | 0 | 16.8 | 6.261 | 6.261 | available | 29 | SS 110/35/6 Konstantinovo | 20+16 |  | 13.2267 | 0.021 | 120 | 13.2057 | 0 | 16.8 | 3.5943 | 3.5943 | available
| Nom. capacity MV, МVА | 20+16 |  |  | 7.47 | 3.95 | 3.52 |  |  | 7.47 | 0 | 16.8 | 9.33 |  |  |  | Nom. capacity MV, МVА | 20+16 |  | 9.6647 |  |  | 9.6647 | 0 | 16.8 | 7.1353
| Nom. capacity LV, МVА | 20+16 |  |  | 3.09 | 2.1 | 0.99 | 0.021 | 120 | 3.069 | 0 | 16.8 | 13.731 |  |  |  | Nom. capacity LV, МVА | 20+16 | 0.472 | 3.562 | 0.021 | 120 | 3.541 | 0 | 16.8 | 13.259
30 | SS 35/10 Kurba | 2,5+2,5 | 2.5 | 2.5 | 2.48 | 0.68 | 1.8 | 0.242 | 120 | 2.238 | 0 | 2.63 | 0.392 | 0.392 | available | 30 | SS 35/10 Kurba | 2,5+2,5 | 0.471 | 2.951 | 0.242 | 120 | 2.709 | 0 | 2.63 | -0.079 | -0.079 | unavailable
31 | SS 35/10 Lesnye Polyany | 10+10 | 10 | 10 | 7.08 | 4.29 | 2.79 | 1.212 | 120 | 5.868 | 0 | 10.5 | 4.632 | 4.632 | available | 31 | SS 35/10 Lesnye Polyany | 10+10 | 1.553 | 8.633 | 1.212 | 120 | 7.421 | 0 | 10.5 | 3.079 | 3.079 | available
32 | SS 35/10 Modelovo-2 | 6,3+6,3 | 6.3 | 6.3 | 5.85 | 2.1 | 3.75 | 2.338 | 120 | 3.512 | 0 | 6.62 | 3.108 | 3.108 | available | 32 | SS 35/10 Modelovo-2 | 6,3+6,3 | 7.3007 | 13.1507 | 2.338 | 120 | 10.8127 | 0 | 6.62 | -4.1927 | -4.1927 | unavailable
33 | SS 35/10 Nekrasovo | 10+10 | 10 | 10 | 11.17 | 5.47 | 5.7 |  |  | 11.17 | 0 | 10.5 | -0.67 | -0.67 | unavailable | 33 | SS 35/10 Nekrasovo | 10+10 | 3.7904 | 14.9604 |  |  | 14.9604 | 0 | 10.5 | -4.4604 | -4.4604 | unavailable
34 | SS 35/10 Nikolskoe | 2,5+2,5 | 2.5 | 2.5 | 0.73 | 0.69 | 0.04 | 0.398 | 120 | 0.332 | 0 | 2.63 | 2.298 | 2.298 | available | 34 | SS 35/10 Nikolskoe | 2,5+2,5 | 0.104 | 0.834 | 0.398 | 120 | 0.436 | 0 | 2.63 | 2.194 | 2.194 | available
35 | SS 110/35/6 Oil refinary plant | 25+25 | 25 | 25 | 15.58 |  |  |  |  | 15.58 | 0 | 26.25 | 10.67 | 10.67 | available | 35 | SS 110/35/6 Oil refinary plant | 25+25 |  | 22.9713 |  |  | 22.9713 | 0 | 26.25 | 3.2787 | 3.2787 | available
| Nom. capacity MV, МVА | 25+25 |  |  | 8.31 | 4.92 | 3.39 |  |  | 8.31 | 0 | 26.25 | 17.94 |  |  |  | Nom. capacity MV, МVА | 25+25 |  | 8.4013 |  |  | 8.4013 | 0 | 26.25 | 17.8487
| Nom. capacity LV, МVА | 25+25 |  |  | 7.27 | 2.92 | 4.35 |  |  | 7.27 | 0 | 26.25 | 18.98 |  |  |  | Nom. capacity LV, МVА | 25+25 | 7.3 | 14.57 |  |  | 14.57 | 0 | 26.25 | 11.68
36 | SS 110/6/6 Orion | 40+40 | 40 | 40 | 14.71 | 8.56 | 6.15 |  |  | 14.71 | 0 | 42 | 27.29 | 27.29 | available | 36 | SS 110/6/6 Orion | 40+40 | 0.67533 | 15.3853 |  |  | 15.3853 | 0 | 42 | 26.6147 | 26.6147 | available
37 | SS 110/35/6 Pavlovskaya | 20+25 | 20 | 25 | 23.56 |  |  |  |  | 23.56 | 0 | 21 | -2.56 | -2.56 | unavailable | 37 | SS 110/35/6 Pavlovskaya | 20+25 |  | 24.1115 |  |  | 24.1115 | 0 | 21 | -3.1115 | -3.1115 | unavailable
| Nom. capacity MV, МVА | 20+25 |  |  | 5.71 | 0.93 | 4.78 |  |  | 5.71 | 0 | 21 | 15.29 |  |  |  | Nom. capacity MV, МVА | 20+25 |  | 6.2148 |  |  | 6.2148 | 0 | 21 | 14.7852
| Nom. capaity LV, МVА | 20+25 |  |  | 17.85 | 5.7 | 12.15 |  |  | 17.85 | 0 | 21 | 3.15 |  |  |  | Nom. capaity LV, МVА | 20+25 | 0.046702 | 17.8967 |  |  | 17.8967 | 0 | 21 | 3.1033
38 | SS 110/10 Pereval | 16+16 | 16 | 16 | 8.51 | 3.93 | 4.58 |  |  | 8.51 | 0 | 16.8 | 8.29 | 8.29 | available | 38 | SS 110/10 Pereval | 16+16 | 7.8703 | 16.3803 |  |  | 16.3803 | 0 | 16.8 | 0.41968 | 0.41968 | available
39 | SS 110/6/6 Perekop | 25+25 | 25 | 25 | 10.33 | 6.29 | 4.04 |  |  | 10.33 | 0 | 26.25 | 15.92 | 15.92 | available | 39 | SS 110/6/6 Perekop | 25+25 | 0.3882 | 10.7182 |  |  | 10.7182 | 0 | 26.25 | 15.5318 | 15.5318 | available
40 | SS 110/6/6 Poligraf | 40+40 | 40 | 40 | 33.97 | 18.83 | 15.14 |  |  | 33.97 | 0 | 42 | 8.03 | 8.03 | available | 40 | SS 110/6/6 Poligraf | 40+40 | 2.2719 | 36.2419 |  |  | 36.2419 | 0 | 42 | 5.7581 | 5.7581 | available
41 | SS 110/35/10 Prechistoe | 10+10 | 10 | 10 | 3.82 |  |  | 0.52 | 120 | 3.3 | 0 | 10.5 | 7.2 | 7.2 | available | 41 | SS 110/35/10 Prechistoe | 10+10 |  | 4.6771 | 0.52 | 120 | 4.1571 | 0 | 10.5 | 6.3429 | 6.3429 | available
| Nom. capacity MV, МVА | 10+10 |  |  | 1 | 0.06 | 0.94 |  |  | 1 | 0 | 10.5 | 9.5 |  |  |  | Nom. capacity MV, МVА | 10+10 |  | 1.1525 |  |  | 1.1525 | 0 | 10.5 | 9.3475
| Nom. capacity LV, МVА | 10+10 |  |  | 2.82 | 1.36 | 1.46 | 0.52 | 120 | 2.3 | 0 | 10.5 | 8.2 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.7046 | 3.5246 | 0.52 | 120 | 3.0046 | 0 | 10.5 | 7.4954
42 | SS 35/10 Preventorium | 2,5+2,5 | 2.5 | 2.5 | 1.05 | 0.35 | 0.7 | 0.26 | 120 | 0.79 | 0 | 2.63 | 1.84 | 1.84 | available | 42 | SS 35/10 Preventorium | 2,5+2,5 | 2.7893 | 3.8393 | 0.26 | 120 | 3.5793 | 0 | 2.63 | -0.9493 | -0.9493 | unavailable
43 | SS 35/10 Rozhdestveno | 2,5+2,5 | 2.5 | 2.5 | 0.23 | 0.03 | 0.2 | 0.052 | 120 | 0.178 | 0 | 2.63 | 2.452 | 2.452 | available | 43 | SS 35/10 Rozhdestveno | 2,5+2,5 | 0.045 | 0.275 | 0.052 | 120 | 0.223 | 0 | 2.63 | 2.407 | 2.407 | available
44 | SS 110/6/6 Severnaya | 63+63 | 63 | 63 | 37.99 | 17.94 | 20.05 |  |  | 37.99 | 0 | 66.15 | 28.16 | 28.16 | available | 44 | SS 110/6/6 Severnaya | 63+63 | 4.662 | 42.652 |  |  | 42.652 | 0 | 66.15 | 23.498 | 23.498 | available
45 | SS 35/10 Sereda | 2,5+2,5 | 2.5 | 2.5 | 1.34 | 0.48 | 0.86 | 0.987 | 120 | 0.353 | 0 | 2.63 | 2.277 | 2.277 | available | 45 | SS 35/10 Sereda | 2,5+2,5 | 0.712 | 2.052 | 0.987 | 120 | 1.065 | 0 | 2.63 | 1.565 | 1.565 | available
46 | SS 110/6 Tormoznaya | 16+16 | 16 | 16 | 14.508 | 9.098 | 5.41 |  |  | 14.508 | 0 | 16.8 | 2.292 | 2.292 | available | 46 | SS 110/6 Tormoznaya | 16+16 | 0.18757 | 14.6956 |  |  | 14.6956 | 0 | 16.8 | 2.1044 | 2.1044 | available
47 | SS 110/6 Petrol station pump | 16+16 | 16 | 16 | 4.59 | 2.47 | 2.12 |  |  | 4.59 | 0 | 16.8 | 12.21 | 12.21 | available | 47 | SS 110/6 Petrol station pump | 16+16 | 0 | 4.59 |  |  | 4.59 | 0 | 16.8 | 12.21 | 12.21 | available
48 | SS 35/10 Troitsa | 2,5+2,5 | 2.5 | 2.5 | 0.34 | 0.27 | 0.07 | 0.277 | 120 | 0.063 | 0 | 2.63 | 2.567 | 2.567 | available | 48 | SS 35/10 Troitsa | 2,5+2,5 | 0.02 | 0.36 | 0.277 | 120 | 0.083 | 0 | 2.63 | 2.547 | 2.547 | available
49 | SS 35/10 Tunoshna | 2,5+2,5 | 2.5 | 2.5 | 0.69 | 0.31 | 0.38 | 0.191 | 120 | 0.499 | 0 | 2.63 | 2.131 | 2.131 | available | 49 | SS 35/10 Tunoshna | 2,5+2,5 | 0.539 | 1.229 | 0.191 | 120 | 1.038 | 0 | 2.63 | 1.592 | 1.592 | available
50 | SS 35/10 Tutaev-35 | 6,3+6,3 | 6.3 | 6.3 | 7.26 | 3.54 | 3.72 |  |  | 7.26 | 0 | 6.62 | -0.64 | -0.64 | unavailable | 50 | SS 35/10 Tutaev-35 | 6,3+6,3 | 0.39 | 7.65 |  |  | 7.65 | 0 | 6.62 | -1.03 | -1.03 | unavailable
51 | SS 110/10 Tufanovo | 2,5+2,5 | 2.5 | 2.5 | 0.72 | 0.59 | 0.13 |  |  | 0.72 | 0 | 2.63 | 1.91 | 1.91 | available | 51 | SS 110/10 Tufanovo | 2,5+2,5 | 0.3434 | 1.0634 |  |  | 1.0634 | 0 | 2.63 | 1.5666 | 1.5666 | available
52 | SS 35/10 Urozhay | 4,0+4,0 | 4 | 4 | 1.58 | 0.65 | 0.93 | 0.346 | 120 | 1.234 | 0 | 4.2 | 2.966 | 2.966 | available | 52 | SS 35/10 Urozhay | 4,0+4,0 | 1.197 | 2.777 | 0.346 | 120 | 2.431 | 0 | 4.2 | 1.769 | 1.769 | available
53 | SS 110/35/10 Khaldeevo | 3,2+6,3 | 3.2 | 6.3 | MVA 4: 2.92; Min 11: 2.83; Min 12: available | 53 | SS 110/35/10 Khaldeevo | 3,2+6,3 |  | 0.8525 |  |  |  | 0 |  |  | 2.7675 | available
| Nom. capacity MV, МVА | 0+6,3 |  |  | MVA 4: 2.13; MVA Т-2: 2.13 |  | Nom. capacity MV, МVА | 0+6,3
| Nom. capacity LV, МVА | 3.2+6.3 |  |  | 0.79 | 0.67 | 0.12 | 0.26 | 120 | 0.53 | 0 | 3.36 | 2.83 |  |  |  | Nom. capacity LV, МVА | 3.2+6.3 | 0.0625 | 0.8525 | 0.26 | 120 | 0.5925 | 0 | 3.36 | 2.7675
54 | SS 110/10 Chayka | 25+25 | 25 | 25 | 19.38 | 9.91 | 9.47 |  |  | 19.38 | 0 | 26.25 | 6.87 | 6.87 | available | 54 | SS 110/10 Chayka | 25+25 | 2.0503 | 21.4303 |  |  | 21.4303 | 0 | 26.25 | 4.8197 | 4.8197 | available
55 | SS 35/6 Chebakovo | 2,5+2,5 | 2.5 | 2.5 | 1.57 | 0.97 | 0.6 | 0.156 | 120 | 1.414 | 0 | 2.63 | 1.216 | 1.216 | available | 55 | SS 35/6 Chebakovo | 2,5+2,5 | 1.624 | 3.194 | 0.156 | 120 | 3.038 | 0 | 2.63 | -0.408 | -0.408 | unavailable
56 | SS 35/10 Shchedrino | 4,0+4,0 | 4 | 4 | 1.43 | 0.19 | 1.24 |  |  | 1.43 | 0 | 4.2 | 2.77 | 2.77 | available | 56 | SS 35/10 Shchedrino | 4,0+4,0 | 1.2055 | 2.6355 |  |  | 2.6355 | 0 | 4.2 | 1.5645 | 1.5645 | available
57 | SS 110/6 /6 Yuzhnaya | 40+40 | 40 | 40 | 31.98 | 12.79 | 19.19 |  |  | 31.98 | 0 | 42 | 10.02 | 10.02 | available | 57 | SS 110/6 /6 Yuzhnaya | 40+40 | 4.3716 | 36.3516 |  |  | 36.3516 | 0 | 42 | 5.6484 | 5.6484 | available
58 | SS 110/10/6 Yartsevo | 25+25 | 25 | 25 | 6.88 | 4.58 | 2.3 |  |  | 6.88 | 0 | 26.25 | 19.37 | 19.37 | available | 58 | SS 110/10/6 Yartsevo | 25+25 | 0.9325 | 7.8125 |  |  | 7.8125 | 0 | 26.25 | 18.4375 | 18.4375 | available
59 | ПС 110/6/6 Kotorosl | 25+25 | 25 | 25 | 6.04 | 3.72 | 2.32 |  |  | 6.04 | 0 | 26.25 | 20.21 | 20.21 | available | 59 | ПС 110/6/6 Kotorosl | 25+25 | 0.71255 | 6.7525 |  |  | 6.7525 |  | 26.25 | 19.4975 | 19.4975 | available
60 | SS 35/6 Kelnot | 4 | 4 |  | 0.29 | 0.29 |  | 4.2 | 1 day and night | 0.29 | 0 | 4.2 | 3.91 | 3.91 | available | 60 | SS 35/6 Kelnot | 4 | 0 | 0.29 | 4.2 | 1 day and night | 0.29 |  | 4.2 | 3.91 | 3.91 | available
61 | SS 110/10 Altynovo | 6,3+6,3 | 6.3 | 6.3 | 3.3 | 1.51 | 1.79 |  |  | 3.3 | 0 | 6.62 | 3.32 | 3.32 | available | 61 | SS 110/10 Altynovo | 6,3+6,3 | 1.7733 | 5.0733 |  |  | 5.0733 | 0 | 6.62 | 1.5467 | 1.5467 | available
62 | SS 110/35/10 Borisogleb | 16+10 | 16 | 10 | 7.8 |  |  |  |  | 7.8 | 0 | 10.5 | 2.7 | 2.7 | available | 62 | SS 110/35/10 Borisogleb | 16+10 |  | 10.9677 |  |  | 10.9677 | 0 | 10.5 | -0.46775 | -0.46775 | unavailable
| Nom. capacity MV, МVА | 16+10 |  |  | 3.35 | 1.36 | 1.99 |  |  | 3.35 | 0 | 10.5 | 7.15 |  |  |  | Nom. capacity MV, МVА | 16+10 |  | 4.6255 |  |  | 4.6255 | 0 | 10.5 | 5.8745
| Nom. capacity LV, МVА | 16+10 |  |  | 4.45 | 2.13 | 2.32 |  |  | 4.45 | 0 | 10.5 | 6.05 |  |  |  | Nom. capacity LV, МVА | 16+10 | 1.8922 | 6.3422 |  |  | 6.3422 | 0 | 10.5 | 4.1578
63 | SS 110/35/10 Vasilkovo | 10+10 | 10 | 10 | 3.4 |  |  | 0.537 | 120 | 2.863 | 0 | 10.5 | 7.637 | 7.637 | available | 63 | SS 110/35/10 Vasilkovo | 10+10 |  | 4.275 | 0.537 | 120 | 3.738 | 0 | 10.5 | 6.762 | 6.762 | available
| Nom. capacity MV, МVА | 10+10 |  |  | 2.1 | 0 | 2.1 |  |  | 2.1 | 0 | 10.5 | 8.4 |  |  |  | Nom. capacity MV, МVА | 10+10 |  | 2.304 |  |  | 2.304 | 0 | 10.5 | 8.196
| Nom. capacity LV, МVА | 10+10 |  |  | 1.3 | 0.45 | 0.85 | 0.537 | 120 | 0.763 | 0 | 10.5 | 9.737 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.671 | 1.971 | 0.537 | 120 | 1.434 | 0 | 10.5 | 9.066
64 | SS 110/10 Vakhrushevo | 6,3+6,3 | 6.3 | 6.3 | 0.29 | 0.04 | 0.25 | 0.087 | 120 | 0.203 | 0 | 6.62 | 6.417 | 6.417 | available | 64 | SS 110/10 Vakhrushevo | 6,3+6,3 | 0.015 | 0.305 | 0.087 | 120 | 0.218 | 0 | 6.62 | 6.402 | 6.402 | available
65 | SS 110/6 Gavrilov Yam | 16+16 | 16 | 16 | 12.24 | 5.05 | 7.19 |  |  | 12.24 | 0 | 16.8 | 4.56 | 4.56 | available | 65 | SS 110/6 Gavrilov Yam | 16+16 | 0 | 12.24 |  |  | 12.24 | 0 | 16.8 | 4.56 | 4.56 | available
66 | SS 110/6 Kinoplyonka | 6,3+10 | 6.3 | 10 | 9.9 | 5.64 | 4.26 |  |  | 9.9 | 0 | 6.62 | -3.28 | -3.28 | unavailable | 66 | SS 110/6 Kinoplyonka | 6,3+10 | 2.854 | 12.754 |  |  | 12.754 | 0 | 6.62 | -6.134 | -6.134 | unavailable
67 | SS 110/35/10 Klimatino | 6,3+6,3 | 6.3 | 6.3 | 1.7 |  |  |  |  | 1.7 | 0 | 6.62 | 4.92 | 4.92 | available | 67 | SS 110/35/10 Klimatino | 6,3+6,3 |  | 1.795 |  |  | 1.795 | 0 | 6.62 | 4.825 | 4.825 | available
| Nom. capacity MV, МVА | 0+6,3 |  |  | MVA 4: 0.36; MVA Т-2: 0.36; Min 7: 0.36; Min 8: 0; Min 9: 6.62; Min 10: 6.26 |  | Nom. capacity MV, МVА | 0+6,3 |  | 0.391 |  |  | 0.391 | 0 | 6.62 | 6.229
| Nom. capacity LV, МVА | 6,3+6,3 |  |  | 1.34 | 0 | 1.34 |  |  | 1.34 | 0 | 6.62 | 5.28 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.064 | 1.404 |  |  | 1.404 | 0 | 6.62 | 5.216
68 | SS 110/35/10 Nila | 6,3+6,3 | 6.3 | 6.3 | 10.35 |  |  | 0.97 | 120 | 9.38 | 0 | 6.62 | -2.76 | -2.76 | unavailable | 68 | SS 110/35/10 Nila | 6,3+6,3 |  | 27.4837 | 0.97 | 120 | 26.5137 | 0 | 6.62 | -19.8937 | -19.8937 | unavailable
| Nom. capacity MV, МVА | 6,3+6,3 |  |  | 7.66 | 5.76 | 1.9 |  |  | 7.66 | 0 | 6.62 | -1.04 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 |  | 11.5772 |  |  | 11.5772 | 0 | 6.62 | -4.9572
| Nom. capacity LV, МVА | 6,3+6,3 |  |  | 2.69 | 1.06 | 1.63 | 0.97 | 120 | 1.72 | 0 | 6.62 | 4.9 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 13.2165 | 15.9065 | 0.97 | 120 | 14.9365 | 0 | 6.62 | -8.3165
69 | SS 110/35/6 Pereslavl | 25+25 | 25 | 25 | 24.89 |  |  |  |  | 24.89 | 0 | 26.25 | 1.36 | 1.36 | available | 69 | SS 110/35/6 Pereslavl | 25+25 |  | 36.7195 |  |  | 36.7195 | 0 | 26.25 | -10.4695 | -10.4695 | unavailable
| Nom. capacity MV, МVА | 25+25 |  |  | 10.56 | 3.77 | 6.79 |  |  | 10.56 | 0 | 26.25 | 15.69 |  |  |  | Nom. capacity MV, МVА | 25+25 |  | 22.1185 |  |  | 22.1185 | 0 | 26.25 | 4.1315
| Nom. capacity LV, МVА | 25+25 |  |  | 14.33 | 4.85 | 9.48 |  |  | 14.33 | 0 | 26.25 | 11.92 |  |  |  | Nom. capacity LV, МVА | 25+25 | 0.271 | 14.601 |  |  | 14.601 | 0 | 26.25 | 11.649
70 | SS 110/10 Ploski | 2,5+2,5 | 2.5 | 2.5 | 1.76 | 1.09 | 0.67 |  |  | 1.76 | 0 | 2.63 | 0.87 | 0.87 | available | 70 | SS 110/10 Ploski | 2,5+2,5 | 0.6385 | 2.3985 |  |  | 2.3985 | 0 | 2.63 | 0.2315 | 0.2315 | available
71 | SS 110/35/10 Rostov | 20+25 | 20 | 25 | 21.21 |  |  |  |  | 21.21 | 0 | 21 | -0.21 | -0.21 | unavailable | 71 | SS 110/35/10 Rostov | 20+25 |  | 24.688 |  |  | 24.688 | 0 | 21 | -3.688 | -3.688 | unavailable
| Nom. capacity MV, МVА | 20+25 |  |  | 1.66 | 0 | 1.66 |  |  | 1.66 | 0 | 21 | 19.34 |  |  |  | Nom. capacity MV, МVА | 20+25 |  | 2.242 |  |  | 2.242 | 0 | 21 | 18.758
| Nom. Capacity LV, МVА | 20+25 |  |  | 19.55 | 8.08 | 11.47 |  |  | 19.55 | 0 | 21 | 1.45 |  |  |  | Nom. Capacity LV, МVА | 20+25 | 2.896 | 22.446 |  |  | 22.446 | 0 | 21 | -1.446
72 | SS 110/35/10 Technical school | 6,3+6,3 | 6.3 | 6.3 | 7.62 |  |  |  |  | 7.62 | 0 | 6.62 | -1 | -1 | unavailable | 72 | SS 110/35/10 Technical school | 6,3+6,3 |  | 13.2147 |  |  | 13.2147 | 0 | 6.62 | -6.5947 | -6.5947 | unavailable
| Nom. capacity MV, МVА | 6,3+6,3 |  |  | 4.13 | 4.13 | 0 |  |  | 4.13 | 0 | 6.62 | 2.49 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 |  | 7.5857 |  |  | 7.5857 | 0 | 6.62 | -0.96575
| Nom. capacity LV, МVА | 6,3+6,3 |  |  | 3.49 | 2.2 | 1.29 |  |  | 3.49 | 0 | 6.62 | 3.13 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 2.139 | 5.629 |  |  | 5.629 | 0 | 6.62 | 0.991
73 | SS 110/35/10 Uglich | 25+25 | 25 | 25 | 23.08 |  |  |  |  | 23.08 | 0 | 26.25 | 3.17 | 3.17 | available | 73 | SS 110/35/10 Uglich | 25+25 |  | 31.826 |  |  | 31.826 | 0 | 26.25 | -5.576 | -5.576 | unavailable
| Nom. capacidty MV, МVА | 25+25 |  |  | 18.49 | 3.59 | 14.9 |  |  | 18.49 | 0 | 26.25 | 7.76 |  |  |  | Nom. capacidty MV, МVА | 25+25 |  | 22.894 |  |  | 22.894 | 0 | 26.25 | 3.356
| Nom. capacity LV, МVА | 25+25 |  |  | 4.59 | 2.47 | 2.12 |  |  | 4.59 | 0 | 26.25 | 21.66 |  |  |  | Nom. capacity LV, МVА | 25+25 | 4.342 | 8.932 |  |  | 8.932 | 0 | 26.25 | 17.318
74 | SS 110/10 Ustye | 10+10 | 10 | 10 | 4.35 | 2.67 | 1.68 | 0.797 | 120 | 3.553 | 0 | 10.5 | 6.947 | 6.947 | available | 74 | SS 110/10 Ustye | 10+10 | 0.391 | 4.741 | 0.797 | 120 | 3.944 | 0 | 10.5 | 6.556 | 6.556 | available
75 | SS 110/10 Shurskol | 10+10 | 10 | 10 | 1.34 | 0.89 | 0.45 | 0.97 | 120 | 0.37 | 0 | 10.5 | 10.13 | 10.13 | available | 75 | SS 110/10 Shurskol | 10+10 | 0.096 | 1.436 | 0.97 | 120 | 0.466 | 0 | 10.5 | 10.034 | 10.034 | available
76 | SS 110/10 Yur.Sloboda | 10+10 | 10 | 10 | 7.17 | 3.94 | 3.23 | 0.866 | 120 | 6.304 | 0 | 10.5 | 4.196 | 4.196 | available | 76 | SS 110/10 Yur.Sloboda | 10+10 | 1.2672 | 8.4372 | 0.866 | 120 | 7.5712 | 0 | 10.5 | 2.9288 | 2.9288 | available
77 | SS 35/10 Aleshkino | 2,5+2,5 | 2.5 | 2.5 | 0.93 | 0.81 | 0.12 |  |  | 0.93 | 0 | 2.63 | 1.7 | 1.7 | available | 77 | SS 35/10 Aleshkino | 2,5+2,5 | 0.114 | 1.044 |  |  | 1.044 | 0 | 2.63 | 1.586 | 1.586 | available
78 | SS 35/6 Batki | 1,6+1,6 | 1.6 | 1.6 | 1.14 | 1.13 | 0.01 |  |  | 1.14 | 0 | 1.68 | 0.54 | 0.54 | available | 78 | SS 35/6 Batki | 1,6+1,6 | 0.773 | 1.913 |  |  | 1.913 | 0 | 1.68 | -0.233 | -0.233 | unavailable
79 | SS 35/10 Beregovaya | 1,6 | 1.6 |  | 0.18 | 0.18 |  | 3.031 | 1 day and night | 0.18 | 0 | 3.031 | 2.851 | 2.851 | available | 79 | SS 35/10 Beregovaya | 1,6 | 0.013 | 0.193 | 3.031 | 1 day and night | 0.193 | 0 | 3.031 | 2.838 | 2.838 | available
80 | SS 35/10 Berendeevo | 2,5+2,5 | 2.5 | 2.5 | 1.76 | 1.11 | 0.65 | 0.225 |  | 1.535 | 0 | 2.63 | 1.095 | 1.095 | available | 80 | SS 35/10 Berendeevo | 2,5+2,5 | 0.013 | 1.773 | 0.225 |  | 1.548 | 0 | 2.63 | 1.082 | 1.082 | available
81 | SS 35/10 Vorzha | 1,8+1,6 | 1.8 | 1.6 | 0.5 | 0.33 | 0.17 | 0.087 | 120 | 0.413 | 0 | 1.68 | 1.267 | 1.267 | available | 81 | SS 35/10 Vorzha | 1,8+1,6 | 0.026 | 0.526 | 0.087 | 120 | 0.439 | 0 | 1.68 | 1.241 | 1.241 | available
82 | SS 35/10 Voshchazhnikovo | 1,6+2,5 | 1.6 | 2.5 | 0.75 | 0.36 | 0.39 | 0.52 | 120 | 0.23 | 0 | 1.68 | 1.45 | 1.45 | available | 82 | SS 35/10 Voshchazhnikovo | 1,6+2,5 | 0.39 | 1.14 | 0.52 | 120 | 0.62 | 0 | 1.68 | 1.06 | 1.06 | available
83 | SS 35/10 Glebovo | 2,5+2,5 | 2.5 | 2.5 | 2.08 | 0.24 | 1.84 |  |  | 2.08 | 0 | 2.63 | 0.55 | 0.55 | available | 83 | SS 35/10 Glebovo | 2,5+2,5 | 4.45 | 6.53 |  |  | 6.53 | 0 | 2.63 | -3.9 | -3.9 | unavailable
84 | SS 35/10 Gorki | 2,5+2,5 | 2.5 | 2.5 | 0.93 | 0.32 | 0.61 |  |  | 0.93 | 0 | 2.63 | 1.7 | 1.7 | available | 84 | SS 35/10 Gorki | 2,5+2,5 | 0.384 | 1.314 |  |  | 1.314 | 0 | 2.63 | 1.316 | 1.316 | available
85 | SS 35/10 Dmitrianovo | 1,6+1,6 | 1.6 | 1.6 | 1.11 | 0.61 | 0.5 |  |  | 1.11 | 0 | 1.68 | 0.57 | 0.57 | available | 85 | SS 35/10 Dmitrianovo | 1,6+1,6 | 0.15 | 1.26 |  |  | 1.26 | 0 | 1.68 | 0.42 | 0.42 | available
86 | SS 35/10 Zaozerye | 2,5+1,6 | 2.5 | 1.6 | 1.54 | 0.63 | 0.91 |  |  | 1.54 | 0 | 1.68 | 0.14 | 0.14 | available | 86 | SS 35/10 Zaozerye | 2,5+1,6 | 0.142 | 1.682 |  |  | 1.682 | 0 | 1.68 | -0.002 | -0.002 | unavailable
87 | SS 35/10 Ilyinskoe | 2,5+2,5 | 2.5 | 2.5 | 1.49 | 1.07 | 0.42 |  |  | 1.49 | 0 | 2.63 | 1.14 | 1.14 | available | 87 | SS 35/10 Ilyinskoe | 2,5+2,5 | 0.1515 | 1.6415 |  |  | 1.6415 | 0 | 2.63 | 0.9885 | 0.9885 | available
88 | SS 35/10 Kibernetik | 6,3+6,3 | 6.3 | 6.3 | 2.24 | 0.76 | 1.48 |  |  | 2.24 | 0 | 6.62 | 4.38 | 4.38 | available | 88 | SS 35/10 Kibernetik | 6,3+6,3 | 1.322 | 3.562 |  |  | 3.562 | 0 | 6.62 | 3.058 | 3.058 | available
89 | SS 35/10 Klementyevo | 1,6 | 1.6 |  | 0.32 | 0.32 |  | 0.485 | 1 day and night | 0.32 | 0 | 0.485 | 0.165 | 0.165 | available | 89 | SS 35/10 Klementyevo | 1,6 | 0.016 | 0.336 | 0.485 | 1 day and night | 0.336 | 0 | 0.485 | 0.149 | 0.149 | available
90 | SS 35/10 Krasnoe | 4,0+4,0 | 4 | 4 | 1.73 | 0.67 | 1.06 | 0.953 | 120 | 0.777 | 0 | 4.2 | 3.423 | 3.423 | available | 90 | SS 35/10 Krasnoe | 4,0+4,0 | 1.617 | 3.347 | 0.953 | 120 | 2.394 | 0 | 4.2 | 1.806 | 1.806 | available
91 | SS 35/10 Kulakovo | 2,5+2,5 | 2.5 | 2.5 | 1.35 | 0.91 | 0.44 |  |  | 1.35 | 0 | 2.63 | 1.28 | 1.28 | available | 91 | SS 35/10 Kulakovo | 2,5+2,5 | 0.45275 | 1.8028 |  |  | 1.8028 | 0 | 2.63 | 0.82725 | 0.82725 | available
92 | SS 35/6 Kupan | 2,5+2,5 | 2.5 | 2.5 | 2.58 | 1.55 | 1.03 |  |  | 2.58 | 0 | 2.63 | 0.05 | 0.05 | available | 92 | SS 35/6 Kupan | 2,5+2,5 | 1.2977 | 3.8777 |  |  | 3.8777 | 0 | 2.63 | -1.2477 | -1.2477 | unavailable
93 | SS 35/10 Markovo | 2,5+2,5 | 2.5 | 2.5 | 0.99 | 0.65 | 0.34 | 0.502 | 120 | 0.488 | 0 | 2.63 | 2.142 | 2.142 | available | 93 | SS 35/10 Markovo | 2,5+2,5 | 0.372 | 1.362 | 0.502 | 120 | 0.86 | 0 | 2.63 | 1.77 | 1.77 | available
94 | SS 35/10 Nagorye | 4,0+4,0 | 4 | 4 | 3.49 | 1.85 | 1.64 |  |  | 3.49 | 0 | 4.2 | 0.71 | 0.71 | available | 94 | SS 35/10 Nagorye | 4,0+4,0 | 2.005 | 5.495 |  |  | 5.495 | 0 | 4.2 | -1.295 | -1.295 | unavailable
95 | SS 35/10 Porechye | 4,0+4,0 | 4 | 4 | 2.13 | 0.84 | 1.29 | 0.087 | 120 | 2.043 | 0 | 4.2 | 2.157 | 2.157 | available | 95 | SS 35/10 Porechye | 4,0+4,0 | 0.33 | 2.46 | 0.087 | 120 | 2.373 | 0 | 4.2 | 1.827 | 1.827 | available
96 | SS 35/10 Pruzhinino | 2,5+2,5 | 2.5 | 2.5 | 1.11 | 0.88 | 0.23 |  |  | 1.11 | 0 | 2.63 | 1.52 | 1.52 | available | 96 | SS 35/10 Pruzhinino | 2,5+2,5 | 0.5265 | 1.6365 |  |  | 1.6365 | 0 | 2.63 | 0.9935 | 0.9935 | available
97 | SS 35/10 Ramenye | 2,5+2,5 | 2.5 | 2.5 | 0.91 | 0.37 | 0.54 | 0.035 | 120 | 0.875 | 0 | 2.63 | 1.755 | 1.755 | available | 97 | SS 35/10 Ramenye | 2,5+2,5 | 0.052 | 0.962 | 0.035 | 120 | 0.927 | 0 | 2.63 | 1.703 | 1.703 | available
98 | SS 35/10 Ryazantsevo | 2,5+2,5 | 2.5 | 2.5 | 1.28 | 0.86 | 0.42 |  |  | 1.28 | 0 | 2.63 | 1.35 | 1.35 | available | 98 | SS 35/10 Ryazantsevo | 2,5+2,5 | 0.124 | 1.404 |  |  | 1.404 | 0 | 2.63 | 1.226 | 1.226 | available
99 | SS 35/10 Saraevo | 1+1,6 | 1 | 1.6 | 1.32 | 0.37 | 0.95 |  |  | 1.32 | 0 | 1.05 | -0.27 | -0.27 | unavailable | 99 | SS 35/10 Saraevo | 1+1,6 | 0.553 | 1.873 |  |  | 1.873 | 0 | 1.05 | -0.823 | -0.823 | unavailable
100 | SS 35/10 Selifontovo | 2,5+2,5 | 2.5 | 2.5 | 1.45 | 0.91 | 0.54 | 0.953 | 120 | 0.497 | 0 | 2.63 | 2.133 | 2.133 | available | 100 | SS 35/10 Selifontovo | 2,5+2,5 | 1.752 | 3.202 | 0.953 | 120 | 2.249 | 0 | 2.63 | 0.381 | 0.381 | available
101 | SS 35/10 Semibratovo | 4,0+4,0 | 4 | 4 | 0.62 | 0.43 | 0.19 | 0.052 | 120 | 0.568 | 0 | 4.2 | 3.632 | 3.632 | available | 101 | SS 35/10 Semibratovo | 4,0+4,0 | 0.322 | 0.942 | 0.052 | 120 | 0.89 | 0 | 4.2 | 3.31 | 3.31 | available
102 | SS 35/10 Skomorokhovo | 1,6+1,6 | 1.6 | 1.6 | 1.1 | 0.04 | 1.06 |  |  | 1.1 | 0 | 1.68 | 0.58 | 0.58 | available | 102 | SS 35/10 Skomorokhovo | 1,6+1,6 | 1.2191 | 2.3191 |  |  | 2.3191 | 0 | 1.68 | -0.6391 | -0.6391 | unavailable
103 | SS 35/10 Solomidino | 2.5 | 2.5 |  | 1.2 | 1.2 |  | 0.866 | 1 day and night | 1.2 | 0 | 0.866 | -0.334 | -0.334 | unavailable | 103 | SS 35/10 Solomidino | 2.5 | 2.394 | 3.594 | 0.866 | 1 day and night | 3.594 | 0 | 0.866 | -2.728 | -2.728 | unavailable
104 | SS 35/10 Stavotino | 4,0+4,0 | 4 | 4 | 1.47 | 0.54 | 0.93 | 0.346 | 120 | 1.124 | 0 | 4.2 | 3.076 | 3.076 | available | 104 | SS 35/10 Stavotino | 4,0+4,0 | 1.452 | 2.922 | 0.346 | 120 | 2.576 | 0 | 4.2 | 1.624 | 1.624 | available
105 | SS 35/10 Urusovo | 2,5+2,5 | 2.5 | 2.5 | 0.4 | 0.31 | 0.09 | 0.052 | 120 | 0.348 | 0 | 2.63 | 2.282 | 2.282 | available | 105 | SS 35/10 Urusovo | 2,5+2,5 | 0.049 | 0.449 | 0.052 | 120 | 0.397 | 0 | 2.63 | 2.233 | 2.233 | available
106 | SS 35/10 Filimonovo | 2,5+2,5 | 2.5 | 2.5 | 0.85 | 0.13 | 0.72 |  |  | 0.85 | 0 | 2.63 | 1.78 | 1.78 | available | 106 | SS 35/10 Filimonovo | 2,5+2,5 | 1.002 | 1.852 |  |  | 1.852 | 0 | 2.63 | 0.778 | 0.778 | available
107 | SS 35/10 Choporovo | 2,5+2,5 | 2.5 | 2.5 | 0.38 | 0.19 | 0.19 |  |  | 0.38 | 0 | 2.63 | 2.25 | 2.25 | available | 107 | SS 35/10 Choporovo | 2,5+2,5 | 0.304 | 0.684 |  |  | 0.684 | 0 | 2.63 | 1.946 | 1.946 | available
108 | SS 35/10 Shchurovo | 2,5+2,5 | 2.5 | 2.5 | 1.11 | 0.57 | 0.54 | 0.242 | 120 | 0.868 | 0 | 2.63 | 1.762 | 1.762 | available | 108 | SS 35/10 Shchurovo | 2,5+2,5 | 0.087 | 1.197 | 0.242 | 120 | 0.955 | 0 | 2.63 | 1.675 | 1.675 | available
109 | SS 35/10 Neksans | 10+10 | 10 | 10 | 1.93 | 0.85 | 1.08 |  |  | 1.93 | 0 | 10.5 | 8.57 | 8.57 | available | 109 | SS 35/10 Neksans | 10+10 | 3.5 | 5.43 |  |  | 5.43 | 0 | 10.5 | 5.07 | 5.07 | available
110 | SS 35/6 Pribrezhnaya | 10+10 | 10 | 10 | 10.7 | 6.51 | 4.19 |  |  | 10.7 | 0 | 10.5 | -0.2 | -0.2 | unavailable | 110 | SS 35/6 Pribrezhnaya | 10+10 | 0.5945 | 11.2945 |  |  | 11.2945 | 0 | 10.5 | -0.7945 | -0.7945 | unavailable
111 | SS 110/10 Tishino | 25+25 | 25 | 25 | 18.25 | 11.44 | 6.81 |  |  | 18.25 | 0 | 26.25 | 8 | 8 | available | 111 | SS 110/10 Tishino | 25+25 | 0.188 | 18.438 |  |  | 18.438 | 0 | 26.25 | 7.812 | 7.812 | available
112 | SS 110/10 Product pipeline | 6,3+6,3 | 6.3 | 6.3 | 1.2 | 0.93 | 0.27 |  |  | 1.2 | 0 | 6.62 | 5.42 | 5.42 | available | 112 | SS 110/10 Product pipeline | 6,3+6,3 | 0 | 1.2 |  |  | 1.2 | 0 | 6.62 | 5.42 | 5.42 | available
113 | SS 110/10 Nekouz | 6,3+6,3 | 6.3 | 6.3 | 2.36 | 0.94 | 1.42 | 0.069 | 120 | 2.291 | 0 | 6.62 | 4.329 | 4.329 | available | 113 | SS 110/10 Nekouz | 6,3+6,3 | 0.042 | 2.402 | 0.069 | 120 | 2.333 | 0 | 6.62 | 4.287 | 4.287 | available
114 | SS 110/6 Yuzhnaya | 25+25 | 25 | 25 | 20.03 | 10.89 | 9.14 |  |  | 20.03 | 0 | 26.25 | 6.22 | 6.22 | available | 114 | SS 110/6 Yuzhnaya | 25+25 | 0.12302 | 20.153 |  |  | 20.153 | 0 | 26.25 | 6.097 | 6.097 | available
115 | SS 110/10 Optika | 10+10 | 10 | 10 | 5.39 | 3.49 | 1.9 | 0.26 | 120 | 5.13 | 0 | 10.5 | 5.37 | 5.37 | available | 115 | SS 110/10 Optika | 10+10 | 0.456 | 5.846 | 0.26 | 120 | 5.586 | 0 | 10.5 | 4.914 | 4.914 | available
116 | SS 110/6 Poligrafmash | 16+16 | 16 | 16 | 7.76 | 3.14 | 4.62 |  |  | 7.76 | 0 | 16.8 | 9.04 | 9.04 | available | 116 | SS 110/6 Poligrafmash | 16+16 | 0.024 | 7.784 |  |  | 7.784 | 0 | 16.8 | 9.016 | 9.016 | available
117 | SS 110/6/6 Zapadnaya | 63+63 | 63 | 63 | 27.9 | 14.65 | 13.25 |  |  | 27.9 | 0 | 66.15 | 38.25 | 38.25 | available | 117 | SS 110/6/6 Zapadnaya | 63+63 | 2.557 | 30.457 |  |  | 30.457 | 0 | 66.15 | 35.693 | 35.693 | available
118 | SS 110/35/6 Volzhskaya | 40+40 | 40 | 40 | 10.75 |  |  |  |  | 10.75 | 0 | 42 | 31.25 | 31.25 | available | 118 | SS 110/35/6 Volzhskaya | 40+40 |  | 10.973 |  |  | 10.973 | 0 | 42 | 31.027 | 31.027 | available
| Nom. capacity MV, МVА | 40+40 |  |  | MVA 4: 0; MVA Т-1: 0; MVA Т-2: 0 |  | Nom. capacity MV, МVА | 40+40
| Nom. capacity LV, МVА | 40+40 |  |  | 10.75 | 0 | 10.75 |  |  | 10.75 | 0 | 42 | 31.25 |  |  |  | Nom. capacity LV, МVА | 40+40 | 0.223 | 10.973 |  |  | 10.973 | 0 | 42 | 31.027
119 | SS 110/35/6 Levoberezhnaya | 16+16 | 16 | 16 | 14.06 |  |  |  |  | 14.06 | 0 | 16.8 | 2.74 | 2.74 | available | 119 | SS 110/35/6 Levoberezhnaya | 16+16 |  | 15.418 |  |  | 15.418 | 0 | 16.8 | 1.382 | 1.382 | available
| Nom. capacity MV, МVА | 16+16 |  |  | 9.1 | 2.68 | 6.42 |  |  | 9.1 | 0 | 16.8 | 7.7 |  |  |  | Nom. capacity MV, МVА | 16+16 |  | 10.414 |  |  | 10.414 | 0 | 16.8 | 6.386
| Nom. capacity LV, МVА | 16+16 |  |  | 4.96 | 3.25 | 1.71 |  |  | 4.96 | 0 | 16.8 | 11.84 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.044 | 5.004 |  |  | 5.004 | 0 | 16.8 | 11.796
120 | SS 110/35/10 Pishchalkino | 7,5+7,5 | 7.5 | 7.5 | 1.96 |  |  |  |  | 1.96 | 0 | 7.88 | 5.92 | 5.92 | available | 120 | SS 110/35/10 Pishchalkino | 7,5+7,5 |  | 1.96 |  |  | 1.96 | 0 | 7.88 | 5.92 | 5.92 | available
| Nom. capacity MV, МVА | 7,5+7,5 |  |  | 1.18 | 1.18 | 0 |  |  | 1.18 | 0 | 7.88 | 6.7 |  |  |  | Nom. capacity MV, МVА | 7,5+7,5 |  | 1.18 |  |  | 1.18 | 0 | 7.88 | 6.7
| Nom. capacity LV, МVА | 7,5+7,5 |  |  | 0.78 | 0.65 | 0.13 |  |  | 0.78 | 0 | 7.88 | 7.1 |  |  |  | Nom. capacity LV, МVА | 7,5+7,5 | 0 | 0.78 |  |  | 0.78 | 0 | 7.88 | 7.1
121 | SS 110/6 Dock yard | 10+10 | 10 | 10 | 5.32 | 3.71 | 1.61 |  |  | 5.32 | 0 | 10.5 | 5.18 | 5.18 | available | 121 | SS 110/6 Dock yard | 10+10 | 0.159 | 5.479 |  |  | 5.479 | 0 | 10.5 | 5.021 | 5.021 | available
122 | SS 110/6 Selekhovo | 6,3+6,3 | 6.3 | 6.3 | 3.42 | 1.14 | 2.28 |  |  | 3.42 | 0 | 6.62 | 3.2 | 3.2 | available | 122 | SS 110/6 Selekhovo | 6,3+6,3 | 0.862 | 4.282 |  |  | 4.282 | 0 | 6.62 | 2.338 | 2.338 | available
123 | SS 35/6 Kamenniki | 4,0+4,0 | 4 | 4 | 2.3 | 1.19 | 1.11 |  |  | 2.3 | 0 | 4.2 | 1.9 | 1.9 | available | 123 | SS 35/6 Kamenniki | 4,0+4,0 | 0.164 | 2.464 |  |  | 2.464 | 0 | 4.2 | 1.736 | 1.736 | available
124 | SS 35/10 Shashkovo | 1,6+1,6 | 1.6 | 1.6 | 0.68 | 0.52 | 0.16 |  |  | 0.68 | 0 | 1.68 | 1 | 1 | available | 124 | SS 35/10 Shashkovo | 1,6+1,6 | 0.355 | 1.035 |  |  | 1.035 | 0 | 1.68 | 0.645 | 0.645 | available
125 | SS 110/6 Veretye | 25+25 | 25 | 25 | 21.36 | 10.73 | 10.63 |  |  | 21.36 | 0 | 26.25 | 4.89 | 4.89 | available | 125 | SS 110/6 Veretye | 25+25 | 0.62916 | 21.9892 |  |  | 21.9892 | 0 | 26.25 | 4.2608 | 4.2608 | available
126 | SS 35/10 Nikolo-Korma | 4,0+4,0 | 4 | 4 | 2.8 | 1.8 | 1 | 0.554 | 120 | 2.246 | 0 | 4.2 | 1.954 | 1.954 | available | 126 | SS 35/10 Nikolo-Korma | 4,0+4,0 | 2.2488 | 5.0488 | 0.554 | 120 | 4.4948 | 0 | 4.2 | -0.2948 | -0.2948 | unavailable
127 | SS 35/10 Arefino | 2,5+2,5 | 2.5 | 2.5 | 1.2 | 0.64 | 0.56 | 0.017 | 120 | 1.183 | 0 | 2.63 | 1.447 | 1.447 | available | 127 | SS 35/10 Arefino | 2,5+2,5 | 0.037 | 1.237 | 0.017 | 120 | 1.22 | 0 | 2.63 | 1.41 | 1.41 | available
128 | SS 35/10 Knyazevo | 1,6+2,5 | 1.6 | 2.5 | 0.82 | 0.1 | 0.72 |  |  | 0.82 | 0 | 1.68 | 0.86 | 0.86 | available | 128 | SS 35/10 Knyazevo | 1,6+2,5 | 0.101 | 0.921 |  |  | 0.921 | 0 | 1.68 | 0.759 | 0.759 | available
129 | SS 35/10 Pokrov | 1,6+1,6 | 1.6 | 1.6 | 0.59 | 0.34 | 0.25 | 0.294 | 120 | 0.296 | 0 | 1.68 | 1.384 | 1.384 | available | 129 | SS 35/10 Pokrov | 1,6+1,6 | 0.017 | 0.607 | 0.294 | 120 | 0.313 | 0 | 1.68 | 1.367 | 1.367 | available
130 | SS 35/10 Anikovo | 2,5+2,5 | 2.5 | 2.5 | 0.83 | 0.64 | 0.19 | 0.017 | 120 | 0.813 | 0 | 2.63 | 1.817 | 1.817 | available | 130 | SS 35/10 Anikovo | 2,5+2,5 | 0.035 | 0.865 | 0.017 | 120 | 0.848 | 0 | 2.63 | 1.782 | 1.782 | available
131 | SS 35/10 Novoe selo | 2,5+2,5 | 2.5 | 2.5 | 1.31 | 0.63 | 0.68 |  |  | 1.31 | 0 | 2.63 | 1.32 | 1.32 | available | 131 | SS 35/10 Novoe selo | 2,5+2,5 | 0.595 | 1.905 |  |  | 1.905 | 0 | 2.63 | 0.725 | 0.725 | available
132 | SS 35/10 Bolshoe selo | 6,3+6,3 | 6.3 | 6.3 | 4.31 | 2.38 | 1.93 |  |  | 4.31 | 0 | 6.62 | 2.31 | 2.31 | available | 132 | SS 35/10 Bolshoe selo | 6,3+6,3 | 1.0789 | 5.3889 |  |  | 5.3889 | 0 | 6.62 | 1.2311 | 1.2311 | available
133 | SS 35/10 Breytovo | 6,3+4,0 | 6.3 | 4 | 4.6 | 2.55 | 2.05 |  |  | 4.6 | 0 | 4.2 | -0.4 | -0.4 | unavailable | 133 | SS 35/10 Breytovo | 6,3+4,0 | 1.577 | 6.177 |  |  | 6.177 | 0 | 4.2 | -1.977 | -1.977 | unavailable
134 | SS 35/10 Stanilovo | 1,6+1,6 | 1.6 | 1.6 | 1.06 | 0.35 | 0.71 | 0.208 | 120 | 0.852 | 0 | 1.68 | 0.828 | 0.828 | available | 134 | SS 35/10 Stanilovo | 1,6+1,6 | 0.028 | 1.088 | 0.208 | 120 | 0.88 | 0 | 1.68 | 0.8 | 0.8 | available
135 | SS 35/10 Znamovo | 2,5+2,5 | 2.5 | 2.5 | 0.91 | 0.3 | 0.61 | 0.173 | 120 | 0.737 | 0 | 2.63 | 1.893 | 1.893 | available | 135 | SS 35/10 Znamovo | 2,5+2,5 | 0.016 | 0.926 | 0.173 | 120 | 0.753 | 0 | 2.63 | 1.877 | 1.877 | available
136 | SS 35/10 Rozhdestvenno | 2,5+2,5 | 2.5 | 2.5 | 0.96 | 0.47 | 0.49 |  |  | 0.96 | 0 | 2.63 | 1.67 | 1.67 | available | 136 | SS 35/10 Rozhdestvenno | 2,5+2,5 | 0.062 | 1.022 |  |  | 1.022 | 0 | 2.63 | 1.608 | 1.608 | available
137 | SS 35/10 Zapolye | 2,5+2,5 | 2.5 | 2.5 | 0.54 | 0.23 | 0.31 |  |  | 0.54 | 0 | 2.63 | 2.09 | 2.09 | available | 137 | SS 35/10 Zapolye | 2,5+2,5 | 0.202 | 0.742 |  |  | 0.742 | 0 | 2.63 | 1.888 | 1.888 | available
138 | SS 35/10 Tikhmenevo | 1,6+1,6 | 1.6 | 1.6 | 1.4 | 0.68 | 0.72 | 0.364 | 120 | 1.036 | 0 | 1.68 | 0.644 | 0.644 | available | 138 | SS 35/10 Tikhmenevo | 1,6+1,6 | 0.181 | 1.581 | 0.364 | 120 | 1.217 | 0 | 1.68 | 0.463 | 0.463 | available
139 | SS 35/10 Latskoe | 1,6+2,5 | 1.6 | 2.5 | 0.22 | 0.13 | 0.09 | 0.017 | 120 | 0.203 | 0 | 1.68 | 1.477 | 1.477 | available | 139 | SS 35/10 Latskoe | 1,6+2,5 | 0.02 | 0.24 | 0.017 | 120 | 0.223 | 0 | 1.68 | 1.457 | 1.457 | available
140 | SS 35/10 Borok | 2,5+4,0 | 2.5 | 4 | 1.56 | 1.15 | 0.41 | 0.277 | 120 | 1.283 | 0 | 2.63 | 1.347 | 1.347 | available | 140 | SS 35/10 Borok | 2,5+4,0 | 0.423 | 1.983 | 0.277 | 120 | 1.706 | 0 | 2.63 | 0.924 | 0.924 | available
141 | SS 35/10 Myshkin | 6,3+6,3 | 6.3 | 6.3 | 3.76 | 2.47 | 1.29 |  |  | 3.76 | 0 | 6.62 | 2.86 | 2.86 | available | 141 | SS 35/10 Myshkin | 6,3+6,3 | 0.804 | 4.564 |  |  | 4.564 | 0 | 6.62 | 2.056 | 2.056 | available
142 | SS 110/10 Volga | 5,6+6,3 | 5.6 | 6.3 | 2.13 | 0.73 | 1.4 |  |  | 2.13 | 0 | 5.88 | 3.75 | 3.75 | available | 142 | SS 110/10 Volga | 5,6+6,3 | 0.19 | 2.32 |  |  | 2.32 | 0 | 5.88 | 3.56 | 3.56 | available
143 | SS 35/10 Krasnaya Gorka | 4,0+2,5 | 4 | 2.5 | 2.09 | 1.14 | 0.95 | 0.104 | 120 | 1.986 | 0 | 2.63 | 0.644 | 0.644 | available | 143 | SS 35/10 Krasnaya Gorka | 4,0+2,5 | 0.783 | 2.873 | 0.104 | 120 | 2.769 | 0 | 2.63 | -0.139 | -0.139 | unavailable
144 | SS 110/35/6 Vostochnaya | 25+25 | 25 | 25 | 20.08 |  |  |  |  | 20.08 | 0 | 26.25 | 6.17 | 6.17 | available | 144 | SS 110/35/6 Vostochnaya | 25+25 |  | 22.5878 |  |  | 22.5878 | 0 | 26.25 | 3.6622 | 3.6622 | available
| Nom. capacity MV, МVА | 25+25 |  |  | 3.67 | 3.67 | 0 |  |  | 3.67 | 0 | 26.25 | 22.58 |  |  |  | Nom. capacity MV, МVА | 25+25 |  | 5.7794 |  |  | 5.7794 | 0 | 26.25 | 20.4706
| Nom. capacity LV, МVА | 25+25 |  |  | 16.41 | 8.03 | 8.38 |  |  | 16.41 | 0 | 26.25 | 9.84 |  |  |  | Nom. capacity LV, МVА | 25+25 | 0.39842 | 16.8084 |  |  | 16.8084 | 0 | 26.25 | 9.4416
145 | SS 110/35/10 Zalesye | 10+10 | 10 | 10 | 8.03 |  |  | 1.212 | 120 | 6.818 | 0 | 10.5 | 3.682 | 3.682 | available | 145 | SS 110/35/10 Zalesye | 10+10 |  | 8.131 | 1.212 | 120 | 6.919 | 0 | 10.5 | 3.581 | 3.581 | available
| Nom. capacity MV, МVА | 10+10 |  |  | 0.78 | 0.44 | 0.34 |  |  | 0.78 | 0 | 10.5 | 9.72 |  |  |  | Nom. capacity MV, МVА | 10+10 |  | 0.796 |  |  | 0.796 | 0 | 10.5 | 9.704
| Nom. capacity LV, МVА | 10+10 |  |  | 7.25 | 4.57 | 2.68 | 1.212 | 120 | 6.038 | 0 | 10.5 | 4.462 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.085 | 7.335 | 1.212 | 120 | 6.123 | 0 | 10.5 | 4.377
146 | SS 110/10 Lugovaya | 6,3+6,3 | 6.3 | 6.3 | 2.85 | 1.18 | 1.67 |  |  | 2.85 | 0 | 6.62 | 3.77 | 3.77 | available | 146 | SS 110/10 Lugovaya | 6,3+6,3 | 0.374 | 3.224 |  |  | 3.224 | 0 | 6.62 | 3.396 | 3.396 | available
147 | SS 110/35/10 Lom | 10+10 | 10 | 10 | 7.55 |  |  | 1.368 | 120 | 6.182 | 0 | 10.5 | 4.318 | 4.318 | available | 147 | SS 110/35/10 Lom | 10+10 |  | 10.0351 | 1.368 | 120 | 8.6671 | 0 | 10.5 | 1.8329 | 1.8329 | available
| Nom. capacity MV, МVА | 10+10 |  |  | 6.07 | 4.03 | 2.04 |  |  | 6.07 | 0 | 10.5 | 4.43 |  |  |  | Nom. capacity MV, МVА | 10+10 |  | 8.0425 |  |  | 8.0425 | 0 | 10.5 | 2.4575
| Nom. capacity LV, МVА | 10+10 |  |  | 1.48 | 1.08 | 0.4 | 1.368 | 120 | 0.112 | 0 | 10.5 | 10.388 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.5126 | 1.9926 | 1.368 | 120 | 0.6246 | 0 | 10.5 | 9.8754
148 | SS 35/10 Varegovo | 1,6+2,5 | 1.6 | 2.5 | 0.8 | 0.52 | 0.28 |  |  | 0.8 | 0 | 1.68 | 0.88 | 0.88 | available | 148 | SS 35/10 Varegovo | 1,6+2,5 | 0.2986 | 1.0986 |  |  | 1.0986 | 0 | 1.68 | 0.5814 | 0.5814 | available
149 | SS 110/35/10 Shestikhino | 10+10 | 10 | 10 | 7.78 |  |  | 0.242 | 120 | 7.538 | 0 | 10.5 | 2.962 | 2.962 | available | 149 | SS 110/35/10 Shestikhino | 10+10 |  | 10.2595 | 0.242 | 120 | 10.0175 | 0 | 10.5 | 0.4825 | 0.4825 | available
| Nom. capacity MV, МVА | 10+10 |  |  | 7.16 | 2.2 | 4.96 |  |  | 7.16 | 0 | 10.5 | 3.34 |  |  |  | Nom. capacity MV, МVА | 10+10 |  | 9.4065 |  |  | 9.4065 | 0 | 10.5 | 1.0935
| Nom. capacity LV, МVА | 10+10 |  |  | 0.62 | 0.27 | 0.35 | 0.242 | 120 | 0.378 | 0 | 10.5 | 10.122 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.233 | 0.853 | 0.242 | 120 | 0.611 | 0 | 10.5 | 9.889
150 | SS 110/35/10 Kryukovo | 6.3 | 6.3 |  | MVA 4: 3.21; Min 11: 1.432; Min 12: available | 150 | SS 110/35/10 Kryukovo | 6.3 |  | 3.627 |  |  |  | 0 |  |  | 1.417 | available
| Nom. capacidty MV, МVА | 6.3 |  |  | MVA 4: 2.91; MVA Т-1: 2.91 |  | Nom. capacidty MV, МVА | 6.3 |  | 3.312 |  |  |  | 0
| Nom. capacity LV, МVА | 6.3 |  |  | 0.3 | 0.3 |  | 1.732 | 1 day and night | 0.3 | 0 | 1.732 | 1.432 |  |  |  | Nom. capacity LV, МVА | 6.3 | 0.015 | 0.315 | 1.732 | 1 day and night | 0.315 | 0 | 1.732 | 1.417
151 | SS 35/10 Beloe | 2.5 | 2.5 |  | 0.71 | 0.71 |  | 1.472 | 1 day and night | 0.71 | 0 | 1.472 | 0.762 | 0.762 | available | 151 | SS 35/10 Beloe | 2.5 | 0.065 | 0.775 | 1.472 | 1 day and night | 0.775 | 0 | 1.472 | 0.697 | 0.697 | available
152 | SS 110/35/10 Glebovo | 10 | 10 |  | MVA 4: 6.05; Min 11: -2.505; Min 12: unavailable | 152 | SS 110/35/10 Glebovo | 10 |  | 9.2924 |  |  |  | 0 |  |  | -4.442 | unavailable
| Nom. capacity MV, МVА | 10 |  |  | MVA 4: 2.87; MVA Т-1: 2.87 |  | Nom. capacity MV, МVА | 10 |  | 4.1754 |  |  |  | 0
| Nom. capacity LV, МVА | 10 |  |  | 3.18 | 3.18 |  | 0.675 | 1 day and night | 3.18 | 0 | 0.675 | -2.505 |  |  |  | Nom. capacity LV, МVА | 10 | 1.937 | 5.117 | 0.675 | 1 day and night | 5.117 | 0 | 0.675 | -4.442
153 | SS 35/6 Pesochnoye | 1,8+1,8 | 1.8 | 1.8 | 1.59 | 0.79 | 0.8 |  |  | 1.59 | 0 | 1.89 | 0.3 | 0.3 | available | 153 | SS 35/6 Pesochnoye | 1,8+1,8 | 0 | 1.59 |  |  | 1.59 |  | 1.89 | 0.3 | 0.3 | available
154 | SS 35/10 Demino | 2,5+2,5 | 2.5 | 2.5 | 0.72 | 0.18 | 0.54 | 0.052 |  | 0.668 | 0 | 2.63 | 1.962 | 1.962 | available | 154 | SS 35/10 Demino | 2,5+2,5 | 0 | 0.72 | 0.052 |  | 0.668 |  | 2.63 | 1.962 | 1.962 | available
155 | SS 110/6 KS-18 | 63+63 | 63 | 63 | 23.71 | 8.29 | 15.42 |  |  | 23.71 | 0 | 66.15 | 42.44 | 42.44 | available | 155 | SS 110/6 KS-18 | 63+63 | 0 | 23.71 |  |  | 23.71 | 0 | 66.15 | 42.44 | 42.44 | available
156 | SS 35/6 Makeikha | 1.6 | 1.6 |  | 0.31 | 0.31 |  | 1.68 | 1 day and night | 0.31 | 0 | 1.68 | 1.37 | 1.37 | available | 156 | SS 35/6 Makeikha | 1.6 | 0 | 0.31 | 1.68 | 1 day and night | 0.31 |  | 1.68 | 1.37 | 1.37 | available
157 | SS 35/10 Ermakovo | 1.6 | 1.6 |  | 1.02 | 1.02 |  | 1.212 | 1 day and night | 1.02 | 0 | 1.212 | 0.192 | 0.192 | available | 157 | SS 35/10 Ermakovo | 1.6 | 0.24 | 1.26 | 1.212 | 1 day and night | 1.26 | 0 | 1.212 | -0.048 | -0.048 | unavailable
158 | SS 35/10 Milyushino | 1.6 | 1.6 |  | 0.84 | 0.84 |  | 0.918 | 1 day and night | 0.84 | 0 | 0.918 | 0.078 | 0.078 | available | 158 | SS 35/10 Milyushino | 1.6 | 0.727 | 1.567 | 0.918 | 1 day and night | 1.567 | 0 | 0.918 | -0.649 | -0.649 | unavailable
159 | SS 35/10 Sutka | 2.5 | 2.5 |  | 0.74 | 0.74 |  | 0.554 | 1 day and night | 0.74 | 0 | 0.554 | -0.186 | -0.186 | unavailable | 159 | SS 35/10 Sutka | 2.5 | 0.039 | 0.779 | 0.554 | 1 day and night | 0.779 | 0 | 0.554 | -0.225 | -0.225 | unavailable
160 | SS 35/10 Sit | 1.6 | 1.6 |  | 0.67 | 0.67 |  | 0.68 | 1 day and night | 0.67 | 0 | 0.68 | 0.01 | 0.01 | available | 160 | SS 35/10 Sit | 1.6 | 0.236 | 0.906 | 0.68 | 1 day and night | 0.906 | 0 | 0.68 | -0.226 | -0.226 | unavailable
161 | SS 35/10 Gorelovo | 1.6 | 1.6 |  | 1.2 | 1.2 |  | 0.901 | 1 day and night | 1.2 | 0 | 0.901 | -0.299 | -0.299 | unavailable | 161 | SS 35/10 Gorelovo | 1.6 | 0.588 | 1.788 | 0.901 | 1 day and night | 1.788 | 0 | 0.901 | -0.887 | -0.887 | unavailable
162 | SS 35/6 Pishchalkino | 1.6 | 1.6 |  | 0.74 | 0.74 |  | 1.68 | 1 day and night | 0.74 | 0 | 1.68 | 0.94 | 0.94 | available | 162 | SS 35/6 Pishchalkino | 1.6 | 0 | 0.74 | 1.68 | 1 day and night | 0.74 | 0 | 1.68 | 0.94 | 0.94 | available
163 | SS 35/6 Varegovo | 1.6 | 1.6 |  | 0.02 | 0.02 |  | 1.68 | 1 day and night | 0.02 | 0 | 1.68 | 1.66 | 1.66 | available | 163 | SS 35/6 Varegovo | 1.6 | 0 | 0.02 | 1.68 | 1 day and night | 0.02 | 0 | 1.68 | 1.66 | 1.66 | available
164 | SS 35/10 Levoberezhnaya | 4 | 4 |  | 1.31 | 1.31 |  | 1.334 | 1 day and night | 1.31 | 0 | 1.334 | 0.024 | 0.024 | available | 164 | SS 35/10 Levoberezhnaya | 4 | 1.0356 | 2.3456 | 1.334 | 1 day and night | 2.3456 |  | 1.334 | -1.0116 | -1.0116 | unavailable
| Total: | 2858.7 | 1456.3 | 1402.4 | MVA 4: 885.648 |  | Total: | 2857.9 | а | 1049.4056
| deficit |  |  |  | Min 11: -15.784 |  | deficit | [9 empty] | -93.702
| proficit |  |  |  | Min 11: 650.045 |  | proficit | [9 empty] | 539.685
|  | -0.55214 | [15 empty] | -3.2787
|  | 22.7392 | [15 empty] | 18.884
Deputy division director for technical issues
[17 empty] | - Chief Engineer | [8 empty] | E.V. Turapin
Note on G216: Т3
Note on G214: Т3
Note on G194: Т2
Note on H194: Т3