## Yaroslavl
Calculation of transmission capacity of supply centres of IDGC of Center - Yarenergo following the winter peak load measurements in 2011
[13 empty] | table 1 | [14 empty] | table 2
No. | Name of supply center, voltage class | Current deficit | [12 empty] | Note | cosφ | No. | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | ячейки скрыть |  | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Supply Center deficit/proficit, MVA | [5 empty] | Installed power capacity of transformers Sinst. including their number provided that technical requirements at connections or other measures performed for reconstruction of the supply center, pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load of Supply Center, MVA | Total capacity redistributed according to operating rules, MVA for the time period provided that technical requirements at connections or other measures performed for reconstruction of the grid investment programs and etc. |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Expected deficit/proficit, MVA
|  |  | MVA |  | MVA |  |  | MVA | Min | [12 empty] | MVA | Min
1 | 2 | 3 |  |  | 4 | Т-1 | Т-2 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | SS 35/10 Matveevo | 1.6 | 1.6 |  | 0.28 | 0.28 |  | 0.883 | 1 day and night | 0.28 | 0 | 0.883 | 0.603 | 0.603 | available | 0.99 | 1 | SS 35/10 Matveevo | 1.6 | 0.194 | 0.474 | 0.883 | 1 day and night | 0.474 | 0 | 0.883 | 0.409 | 0.409 | available
2 | SS 35/10 Mikhailovskoe | 6.3 | 6.3 |  | 1.24 | 1.24 |  | 0 | 1 day and night | 1.24 | 0 | 0 | -1.24 | -1.24 | unavailable | 0.97 | 2 | SS 35/10 Mikhailovskoe | 6.3 | 0.003 | 1.243 | 0 | 1 day and night | 1.243 | 0 | 0 | -1.243 | -1.243 | unavailable
3 | SS 35/10 Shirinye | 4 | 4 |  | 1.85 |  | 1.85 | 2.095 | 1 day and night | 1.85 | 0 | 2.095 | 0.245 | 0.245 | available | 0.95 | 3 | SS 35/10 Shirinye | 4 | 0.437 | 2.287 | 2.095 | 1 day and night | 2.287 | 0 | 2.095 | -0.192 | -0.192 | unavailable
4 | SS 110/10 Pokrov | 2.5 | 2.5 |  | 0.3 | 0.3 |  | 1.273 | 1 day and night | 0.3 | 0 | 1.273 | 0.973 | 0.973 | available | 0.8 | 4 | SS 110/10 Pokrov | 2.5 | 0.048 | 0.348 | 1.273 | 1 day and night | 0.348 | 0 | 1.273 | 0.925 | 0.925 | available
5 | SS 35/10 Obnora | 1.6 | 1.6 |  | 0.2 | 0.2 |  | 1.212 | 1 day and night | 0.2 | 0 | 1.212 | 1.012 | 1.012 | available | 0.91 | 5 | SS 35/10 Obnora | 1.6 | 0.093 | 0.293 | 1.212 | 1 day and night | 0.293 | 0 | 1.212 | 0.919 | 0.919 | available
6 | SS 110/35/10 Abbakumtsevo | 10+10 | 10 | 10 | 8.3 |  |  |  |  | 8.3 | 0 | 10.5 | 2.2 | 2.2 | available | 0.97 | 6 | SS 110/35/10 Abbakumtsevo | 10+10 |  | 24.312 |  |  | 24.312 | 0 | 10.5 | -13.812 | -13.812 | unavailable
| Nom. capacity MV, МVА | 10+10 |  |  | 7.1 | Т-1: 1.82; Т-2: 5.28; Min 7: 7.1; Min 8: 0; Min 9: 10.5; Min 10: 3.4 |  | Nom. capacity MV, МVА | 10+10 |  | 19.408 |  |  | 19.408 | 0 | 10.5 | -8.908
| Nom. capacity LV, МVА | 10+10 |  |  | 1.2 | Т-1: 0.58; Т-2: 0.62; Min 7: 1.2; Min 8: 0; Min 9: 10.5; Min 10: 9.3 |  | Nom. capacity LV, МVА | 10+10 | 3.704 | 4.904 |  |  | 4.904 | 0 | 10.5 | 5.596
7 | SS 35/10 Ananyino | 2,5+2,5 | 2.5 | 2.5 | 1.15 | 0.86 | 0.29 |  |  | 1.15 | 0 | 2.63 | 1.48 | 1.48 | available | 0.97 | 7 | SS 35/10 Ananyino | 2,5+2,5 | 1.278 | 2.428 |  |  | 2.428 | 0 | 2.63 | 0.202 | 0.202 | available
8 | SS 110/10/10 Bragino | 40+40 | 40 | 40 | 26.79 | 12.53 | 14.26 | 2.252 | 120 | 24.538 | 0 | 42 | 17.462 | 17.462 | available | 0.97 | 8 | SS 110/10/10 Bragino | 40+40 | 4.58 | 31.37 | 2.252 | 120 | 29.118 | 0 | 42 | 12.882 | 12.882 | available
9 | SS 35/10 Burmakino-1 | 4,0+4,0 | 4 | 4 | 1.73 | 0.68 | 1.05 | 0.52 | 120 | 1.21 | 0 | 4.2 | 2.99 | 2.99 | available | 0.97 | 9 | SS 35/10 Burmakino-1 | 4,0+4,0 | 1.301 | 3.031 | 0.52 | 120 | 2.511 | 0 | 4.2 | 1.689 | 1.689 | available
10 | SS 35/10 Vatolino | 4,0+4,0 | 4 | 4 | 3.14 | 1.7 | 1.44 |  |  | 3.14 | 0 | 4.2 | 1.06 | 1.06 | available | 0.96 | 10 | SS 35/10 Vatolino | 4,0+4,0 | 5.076 | 8.216 |  |  | 8.216 | 0 | 4.2 | -4.016 | -4.016 | unavailable
11 | SS 35/6 Vederniki | 6,3+6,3 | 6.3 | 6.3 | 4.55 | 1.55 | 3 |  |  | 4.55 | 0 | 6.62 | 2.07 | 2.07 | available | 0.92 | 11 | SS 35/6 Vederniki | 6,3+6,3 | 0.091 | 4.641 |  |  | 4.641 | 0 | 6.62 | 1.979 | 1.979 | available
12 | SS 35/10 Velikovskaya | 4,0+4,0 | 4 | 4 | 1.78 | 1.27 | 0.51 |  |  | 1.78 | 0 | 4.2 | 2.42 | 2.42 | available | 0.82 | 12 | SS 35/10 Velikovskaya | 4,0+4,0 | 0.226 | 2.006 |  |  | 2.006 | 0 | 4.2 | 2.194 | 2.194 | available
13 | SS 35/10 Velikoe Selo | 1,6+1,6 | 1.6 | 1.6 | 0.62 | 0.52 | 0.1 |  |  | 0.62 | 0 | 1.68 | 1.06 | 1.06 | available | 0.93 | 13 | SS 35/10 Velikoe Selo | 1,6+1,6 | 0.077 | 0.697 |  |  | 0.697 | 0 | 1.68 | 0.983 | 0.983 | available
14 | SS 35/10 Vozrozhdenie | 4,0+4,0 | 4 | 4 | 1.23 | 0.36 | 0.87 |  |  | 1.23 | 0 | 4.2 | 2.97 | 2.97 | available | 0.96 | 14 | SS 35/10 Vozrozhdenie | 4,0+4,0 | 3.385 | 4.615 |  |  | 4.615 | 0 | 4.2 | -0.415 | -0.415 | unavailable
15 | SS 35/10 Volna | 4,0+2,5 | 4 | 2.5 | 2.64 | 1.51 | 1.13 |  |  | 2.64 | 0 | 2.63 | -0.01 | -0.01 | unavailable | 0.88 | 15 | SS 35/10 Volna | 4,0+2,5 | 0.066 | 2.706 |  |  | 2.706 | 0 | 2.63 | -0.076 | -0.076 | unavailable
16 | SS 35/10 Vyatskoe | 2,5+2,5 | 2.5 | 2.5 | 1.75 | 0.89 | 0.86 | 0.139 | 120 | 1.611 | 0 | 2.63 | 1.019 | 1.019 | available | 0.93 | 16 | SS 35/10 Vyatskoe | 2,5+2,5 | 0.414 | 2.164 | 0.139 | 120 | 2.025 | 0 | 2.63 | 0.605 | 0.605 | available
17 | SS 35/10 Gorinskaya | 2,5+2,5 | 2.5 | 2.5 | 0.64 | 0.32 | 0.32 | 0.277 | 120 | 0.363 | 0 | 2.63 | 2.267 | 2.267 | available | 0.93 | 17 | SS 35/10 Gorinskaya | 2,5+2,5 | 0.186 | 0.826 | 0.277 | 120 | 0.549 | 0 | 2.63 | 2.081 | 2.081 | available
18 | SS 35/10 Grigoryevskoe | 4,0+4,0 | 4 | 4 | 2.18 | 1.76 | 0.42 | 0.294 | 120 | 1.886 | 0 | 4.2 | 2.314 | 2.314 | available | 0.96 | 18 | SS 35/10 Grigoryevskoe | 4,0+4,0 | 1.104 | 3.284 | 0.294 | 120 | 2.99 | 0 | 4.2 | 1.21 | 1.21 | available
19 | SS 35/10 Guzitsino | 4,0+4,0 | 4 | 4 | 3.41 | 1.27 | 2.14 | 1.316 | 120 | 2.094 | 0 | 4.2 | 2.106 | 2.106 | available | 0.97 | 19 | SS 35/10 Guzitsino | 4,0+4,0 | 7.088 | 10.498 | 1.316 | 120 | 9.182 | 0 | 4.2 | -4.982 | -4.982 | unavailable
20 | SS 35/10 State Fire-Fighting Service Yaroslavl | 6,3+6,3 | 6.3 | 6.3 | 2.04 | 1.74 | 0.3 |  |  | 2.04 | 0 | 6.62 | 4.58 | 4.58 | available | 0.99 | 20 | SS 35/10 State Fire-Fighting Service Yaroslavl | 6,3+6,3 | 0.011 | 2.051 |  |  | 2.051 | 0 | 6.62 | 4.569 | 4.569 | available
21 | SS 110/6 Depo | 16+16 | 16 | 16 | 8.56 | 5.24 | 3.32 |  |  | 8.56 | 0 | 16.8 | 8.24 | 8.24 | available | 0.97 | 21 | SS 110/6 Depo | 16+16 | 2.729 | 11.289 |  |  | 11.289 | 0 | 16.8 | 5.511 | 5.511 | unavailable
22 | SS 35/10 Dorozhaevo | 1,6+1,6 | 1.6 | 1.6 | 1.31 | 0.61 | 0.7 | 0.675 | 120 | 0.635 | 0 | 1.68 | 1.045 | 1.045 | available | 0.96 | 22 | SS 35/10 Dorozhaevo | 1,6+1,6 | 2.231 | 3.541 | 0.675 | 120 | 2.866 | 0 | 1.68 | -1.186 | -1.186 | unavailable
23 | SS 110/10 Druzhba | 16+16 | 16 | 16 | 5.17 | 1.63 | 3.54 | 1.706 | 120 | 3.464 | 0 | 16.8 | 13.336 | 13.336 | available | 0.91 | 23 | SS 110/10 Druzhba | 16+16 | 1.078 | 6.248 | 1.706 | 120 | 4.542 | 0 | 16.8 | 12.258 | 12.258 | available
24 | SS 35/10 Dubki | 6,3+6,3 | 6.3 | 6.3 | 3.8 | 2.58 | 1.22 | 1.083 | 120 | 2.717 | 0 | 6.62 | 3.903 | 3.903 | available | 0.91 | 24 | SS 35/10 Dubki | 6,3+6,3 | 1.565 | 5.365 | 1.083 | 120 | 4.282 | 0 | 6.62 | 2.338 | 2.338 | available
25 | SS 35/10 Dybino | 2,5+2,5 | 2.5 | 2.5 | 0.96 | 0.5 | 0.46 |  |  | 0.96 | 0 | 2.63 | 1.67 | 1.67 | available | 0.91 | 25 | SS 35/10 Dybino | 2,5+2,5 | 0.676 | 1.636 |  |  | 1.636 | 0 | 2.63 | 0.994 | 0.994 | available
26 | SS 35/6 Zavolzhskaya | 10+10 | 10 | 10 | 11.04 | 2.92 | 8.12 |  |  | 11.04 | 0 | 10.5 | -0.54 | -0.54 | unavailable | 0.97 | 26 | SS 35/6 Zavolzhskaya | 10+10 | 0.792 | 11.832 |  |  | 11.832 | 0 | 10.5 | -1.332 | -1.332 | unavailable
27 | SS 110/6/6 Institutskaya | 40+40 | 40 | 40 | 34.35 | 18.11 | 16.24 |  |  | 34.35 | 0 | 42 | 7.65 | 7.65 | available | 0.95 | 27 | SS 110/6/6 Institutskaya | 40+40 | 2.579 | 36.929 |  |  | 36.929 | 0 | 42 | 5.071 | 5.071 | available
28 | SS 35/10 Koza | 1,6+1,6 | 1.6 | 1.6 | 0.33 | 0.1 | 0.23 | 0.07 | 120 | 0.26 | 0 | 1.68 | 1.42 | 1.42 | available | 0.98 | 28 | SS 35/10 Koza | 1,6+1,6 | 0.086 | 0.416 | 0.07 | 120 | 0.346 | 0 | 1.68 | 1.334 | 1.334 | available
29 | SS 110/35/6 Konstantinovo | 15+16 | 15 | 16 | 8.83 |  |  | 0.021 | 120 | 8.809 | 0 | 15.75 | 6.941 | 6.941 | available | 0.91 | 29 | SS 110/35/6 Konstantinovo | 15+16 |  | 12.981 | 0.021 | 120 | 12.96 | 0 | 15.75 | 2.79 | 2.79 | available
| Nom. capacity MV, МVА | 15+16 |  |  | 6.13 | Т-1: 4.14; Т-2: 1.99; Min 7: 6.13; Min 8: 0; Min 9: 15.75; Min 10: 9.62 |  | Nom. capacity MV, МVА | 15+16 |  | 8.762 |  |  | 8.762 | 0 | 15.75 | 6.988
| Nom. capacity LV, МVА | 15+16 |  |  | 2.7 | 1.94 | 0.76 | 0.021 | 120 | 2.679 | 0 | 15.75 | 13.071 |  |  |  |  | Nom. capacity LV, МVА | 15+16 | 1.519 | 4.219 | 0.021 | 120 | 4.198 | 0 | 15.75 | 11.552
30 | SS 35/10 Kurba | 2,5+2,5 | 2.5 | 2.5 | 2.35 | 0.47 | 1.88 | 0.277 | 120 | 2.073 | 0 | 2.63 | 0.557 | 0.557 | available | 0.96 | 30 | SS 35/10 Kurba | 2,5+2,5 | 0.6 | 2.95 | 0.277 | 120 | 2.673 | 0 | 2.63 | -0.043 | -0.043 | unavailable
31 | SS 35/10 Lesnye Polyany | 10+10 | 10 | 10 | 6.52 | 3.43 | 3.09 | 1.212 | 120 | 5.308 | 0 | 10.5 | 5.192 | 5.192 | available | 0.91 | 31 | SS 35/10 Lesnye Polyany | 10+10 | 2.943 | 9.463 | 1.212 | 120 | 8.251 | 0 | 10.5 | 2.249 | 2.249 | available
32 | SS 35/10 Modelovo-2 | 6,3+6,3 | 6.3 | 6.3 | 5.43 | 1.52 | 3.91 | 1.905 | 120 | 3.525 | 0 | 6.62 | 3.095 | 3.095 | available | 0.98 | 32 | SS 35/10 Modelovo-2 | 6,3+6,3 | 8.557 | 13.987 | 1.905 | 120 | 12.082 | 0 | 6.62 | -5.462 | -5.462 | unavailable
33 | SS 35/10 Nekrasovo | 16+16 | 16 | 16 | 9.99 | 3.8 | 6.19 |  |  | 9.99 | 0 | 16.8 | 6.81 | 6.81 | available | 0.96 | 33 | SS 35/10 Nekrasovo | 16+16 | 4.296 | 14.286 |  |  | 14.286 | 0 | 16.8 | 2.514 | 2.514 | available
34 | SS 35/10 Nikolskoe | 2,5+2,5 | 2.5 | 2.5 | 0.77 | 0.37 | 0.4 | 0.416 | 120 | 0.354 | 0 | 2.63 | 2.276 | 2.276 | available | 0.94 | 34 | SS 35/10 Nikolskoe | 2,5+2,5 | 0.135 | 0.905 | 0.416 | 120 | 0.489 | 0 | 2.63 | 2.141 | 2.141 | available
35 | SS 110/35/6 Oil refinary plant | 25+25 | 25 | 25 | 16.7 |  |  |  |  | 16.7 | 0 | 26.25 | 9.55 | 9.55 | available | 0.95 | 35 | SS 110/35/6 Oil refinary plant | 25+25 |  | 24.102 |  |  | 24.102 | 0 | 26.25 | 2.148 | 2.148 | available
| Nom. capacity MV, МVА | 25+25 |  |  | 8.79 | Т-1: 5.2; Т-2: 3.59; Min 7: 8.79; Min 8: 0; Min 9: 26.25; Min 10: 17.46 |  | Nom. capacity MV, МVА | 25+25 |  | 8.892 |  |  | 8.892 | 0 | 26.25 | 17.358
| Nom. capacity LV, МVА | 25+25 |  |  | 7.91 | Т-1: 3.72; Т-2: 4.19; Min 7: 7.91; Min 8: 0; Min 9: 26.25; Min 10: 18.34 |  | Nom. capacity LV, МVА | 25+25 | 7.3 | 15.21 |  |  | 15.21 | 0 | 26.25 | 11.04
36 | SS 110/6/6 Orion | 40+40 | 40 | 40 | 17.27 | 7.44 | 9.83 |  |  | 17.27 | 0 | 42 | 24.73 | 24.73 | available | 0.83 | 36 | SS 110/6/6 Orion | 40+40 | 0.555 | 17.825 |  |  | 17.825 | 0 | 42 | 24.175 | 24.175 | available
37 | SS 110/35/6 Pavlovskaya | 20+25 | 20 | 25 | 25.52 |  |  |  |  | 25.52 | 0 | 21 | -4.52 | -4.52 | unavailable | 0.92 | 37 | SS 110/35/6 Pavlovskaya | 20+25 |  | 26.119 |  |  | 26.119 | 0 | 21 | -5.119 | -5.119 | unavailable
| Nom. capacity MV, МVА | 20+25 |  |  | 8.98 | Т-1: 0; Т-2: 8.98; Min 7: 8.98; Min 8: 0; Min 9: 21; Min 10: 12.02 |  | Nom. capacity MV, МVА | 20+25 |  | 9.532 |  |  | 9.532 | 0 | 21 | 11.468
| Nom. capaity LV, МVА | 20+25 |  |  | 16.54 | Т-1: 8.57; Т-2: 7.97; Min 7: 16.54; Min 8: 0; Min 9: 21; Min 10: 4.46 |  | Nom. capaity LV, МVА | 20+25 | 0.047 | 16.587 |  |  | 16.587 | 0 | 21 | 4.413
38 | SS 110/10 Pereval | 16+16 | 16 | 16 | 8.04 | 3.87 | 4.17 |  |  | 8.04 | 0 | 16.8 | 8.76 | 8.76 | available | 0.99 | 38 | SS 110/10 Pereval | 16+16 | 7.952 | 15.992 |  |  | 15.992 | 0 | 16.8 | 0.808 | 0.808 | available
39 | SS 110/6/6 Perekop | 25+25 | 25 | 25 | 9.59 | 4.68 | 4.91 |  |  | 9.59 | 0 | 26.25 | 16.66 | 16.66 | available | 0.95 | 39 | SS 110/6/6 Perekop | 25+25 | 0.539 | 10.129 |  |  | 10.129 | 0 | 26.25 | 16.121 | 16.121 | available
40 | SS 110/6/6 Poligraf | 40+40 | 40 | 40 | 30.75 | 18.47 | 12.28 |  |  | 30.75 | 0 | 42 | 11.25 | 11.25 | available | 0.98 | 40 | SS 110/6/6 Poligraf | 40+40 | 2.466 | 33.216 |  |  | 33.216 | 0 | 42 | 8.784 | 8.784 | available
41 | SS 110/35/10 Prechistoe | 10+10 | 10 | 10 | 4.44 |  |  | 0.52 | 120 | 3.92 | 0 | 10.5 | 6.58 | 6.58 | available | 0.93 | 41 | SS 110/35/10 Prechistoe | 10+10 |  | 5.608 | 0.52 | 120 | 5.088 | 0 | 10.5 | 5.412 | 5.412 | available
| Nom. capacity MV, МVА | 10+10 |  |  | 1.64 | Т-1: 0.07; Т-2: 1.57; Min 7: 1.64; Min 8: 0; Min 9: 10.5; Min 10: 8.86 |  | Nom. capacity MV, МVА | 10+10 |  | 1.874 |  |  | 1.874 | 0 | 10.5 | 8.626
| Nom. capacity LV, МVА | 10+10 |  |  | 2.8 | 1.34 | 1.46 | 0.52 | 120 | 2.28 | 0 | 10.5 | 8.22 |  |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.934 | 3.734 | 0.52 | 120 | 3.214 | 0 | 10.5 | 7.286
42 | SS 35/10 Preventorium | 2,5+2,5 | 2.5 | 2.5 | 0.93 | 0.36 | 0.57 | 0.346 | 120 | 0.584 | 0 | 2.63 | 2.046 | 2.046 | available | 0.96 | 42 | SS 35/10 Preventorium | 2,5+2,5 | 2.855 | 3.785 | 0.346 | 120 | 3.439 | 0 | 2.63 | -0.809 | -0.809 | unavailable
43 | SS 35/10 Rozhdestveno | 2,5+2,5 | 2.5 | 2.5 | 0.23 | 0.03 | 0.2 | 0.052 | 120 | 0.178 | 0 | 2.63 | 2.452 | 2.452 | available | 0.77 | 43 | SS 35/10 Rozhdestveno | 2,5+2,5 | 0.045 | 0.275 | 0.052 | 120 | 0.223 | 0 | 2.63 | 2.407 | 2.407 | available
44 | SS 110/6/6 Severnaya | 63+63 | 63 | 63 | 36.14 | 16.37 | 19.77 |  |  | 36.14 | 0 | 66.15 | 30.01 | 30.01 | available | 0.97 | 44 | SS 110/6/6 Severnaya | 63+63 | 4.573 | 40.713 |  |  | 40.713 | 0 | 66.15 | 25.437 | 25.437 | available
45 | SS 35/10 Sereda | 2,5+2,5 | 2.5 | 2.5 | 1.31 | 0.5 | 0.81 | 0.831 | 120 | 0.479 | 0 | 2.63 | 2.151 | 2.151 | available | 0.89 | 45 | SS 35/10 Sereda | 2,5+2,5 | 0.728 | 2.038 | 0.831 | 120 | 1.207 | 0 | 2.63 | 1.423 | 1.423 | available
46 | SS 110/6 Tormoznaya | 16+16 | 16 | 16 | 12.84 | 9.59 | 3.25 |  |  | 12.84 | 0 | 16.8 | 3.96 | 3.96 | available | 0.96 | 46 | SS 110/6 Tormoznaya | 16+16 | 0.188 | 13.028 |  |  | 13.028 | 0 | 16.8 | 3.772 | 3.772 | available
47 | SS 110/6 Petrol station pump | 16+16 | 16 | 16 | 4.89 | 2.47 | 2.42 |  |  | 4.89 | 0 | 16.8 | 11.91 | 11.91 | available | 0.98 | 47 | SS 110/6 Petrol station pump | 16+16 | 0 | 4.89 |  |  | 4.89 | 0 | 16.8 | 11.91 | 11.91 | available
48 | SS 35/10 Troitsa | 2,5+2,5 | 2.5 | 2.5 | 0.41 | 0.32 | 0.09 | 0.277 | 120 | 0.133 | 0 | 2.63 | 2.497 | 2.497 | available | 0.89 | 48 | SS 35/10 Troitsa | 2,5+2,5 | 0.035 | 0.445 | 0.277 | 120 | 0.168 | 0 | 2.63 | 2.462 | 2.462 | available
49 | SS 35/10 Tunoshna | 2,5+2,5 | 2.5 | 2.5 | 0.9 | 0.37 | 0.53 | 0.173 | 120 | 0.727 | 0 | 2.63 | 1.903 | 1.903 | available | 0.97 | 49 | SS 35/10 Tunoshna | 2,5+2,5 | 0.614 | 1.514 | 0.173 | 120 | 1.341 | 0 | 2.63 | 1.289 | 1.289 | available
50 | SS 35/10 Tutaev-35 | 10+10 | 10 | 10 | 6.35 | 3.11 | 3.24 |  |  | 6.35 | 0 | 10.5 | 4.15 | 4.15 | available | 0.96 | 50 | SS 35/10 Tutaev-35 | 10+10 | 0.598 | 6.948 |  |  | 6.948 | 0 | 10.5 | 3.552 | 3.552 | available
51 | SS 110/10 Tufanovo | 2,5+2,5 | 2.5 | 2.5 | 0.75 | 0.62 | 0.13 |  |  | 0.75 | 0 | 2.63 | 1.88 | 1.88 | available | 0.96 | 51 | SS 110/10 Tufanovo | 2,5+2,5 | 0.378 | 1.128 |  |  | 1.128 | 0 | 2.63 | 1.502 | 1.502 | available
52 | SS 35/10 Urozhay | 4,0+4,0 | 4 | 4 | 1.61 | 0.73 | 0.88 | 0.346 | 120 | 1.264 | 0 | 4.2 | 2.936 | 2.936 | available | 0.98 | 52 | SS 35/10 Urozhay | 4,0+4,0 | 1.359 | 2.969 | 0.346 | 120 | 2.623 | 0 | 4.2 | 1.577 | 1.577 | available
53 | SS 110/35/10 Khaldeevo | 3,2+6,3 | 3.2 | 6.3 | 2.69 | Min 8: 0; Min 11: 2.813; Min 12: available; Min 13: 0.92 | 53 | SS 110/35/10 Khaldeevo | 3,2+6,3 |  | 0.788 |  |  |  | 0 |  |  | 2.745 | available
| Nom. capacity MV, МVА | 0+6,3 |  |  | 1.97 | Т-2: 1.97; Min 8: 0 |  | Nom. capacity MV, МVА | 0+6,3 | [5 empty] | 0
| Nom. capacity LV, МVА | 3.2+6.3 |  |  | 0.72 | 0.57 | 0.15 | 0.173 | 120 | 0.547 | 0 | 3.36 | 2.813 |  |  |  |  | Nom. capacity LV, МVА | 3.2+6.3 | 0.068 | 0.788 | 0.173 | 120 | 0.615 | 0 | 3.36 | 2.745
54 | SS 110/10 Chayka | 25+25 | 25 | 25 | 17.51 | 10.5 | 7.01 |  |  | 17.51 | 0 | 26.25 | 8.74 | 8.74 | available | 0.98 | 54 | SS 110/10 Chayka | 25+25 | 2.545 | 20.055 |  |  | 20.055 | 0 | 26.25 | 6.195 | 6.195 | available
55 | SS 35/6 Chebakovo | 2,5+2,5 | 2.5 | 2.5 | 1.55 | 0.97 | 0.58 | 0.139 | 120 | 1.411 | 0 | 2.63 | 1.219 | 1.219 | available | 0.93 | 55 | SS 35/6 Chebakovo | 2,5+2,5 | 2.014 | 3.564 | 0.139 | 120 | 3.425 | 0 | 2.63 | -0.795 | -0.795 | unavailable
56 | SS 35/10 Shchedrino | 4,0+4,0 | 4 | 4 | 1.31 | 0.23 | 1.08 |  |  | 1.31 | 0 | 4.2 | 2.89 | 2.89 | available | 0.94 | 56 | SS 35/10 Shchedrino | 4,0+4,0 | 1.271 | 2.581 |  |  | 2.581 | 0 | 4.2 | 1.619 | 1.619 | available
57 | SS 110/6 /6 Yuzhnaya | 40+40 | 40 | 40 | 29.6 | 12.7 | 16.9 |  |  | 29.6 | 0 | 42 | 12.4 | 12.4 | available | 0.96 | 57 | SS 110/6 /6 Yuzhnaya | 40+40 | 4.341 | 33.941 |  |  | 33.941 | 0 | 42 | 8.059 | 8.059 | available
58 | SS 110/10/6 Yartsevo | 25+25 | 25 | 25 | 6.39 | 4.55 | 1.84 |  |  | 6.39 | 0 | 26.25 | 19.86 | 19.86 | available | 0.998 | 58 | SS 110/10/6 Yartsevo | 25+25 | 0.943 | 7.333 |  |  | 7.333 | 0 | 26.25 | 18.917 | 18.917 | available
59 | ПС 110/6/6 Kotorosl | 25+25 | 25 | 25 | 6.89 | 2.73 | 4.16 |  |  | 6.89 | 0 | 26.25 | 19.36 | 19.36 | available | 0.98 | 59 | ПС 110/6/6 Kotorosl | 25+25 | 0.713 | 7.603 |  |  | 7.603 | 0 | 26.25 | 18.647 | 18.647
60 | SS 35/6 Kelnot | 4,0 | 4 |  | 0.16 | 0.16 |  | 0 | 1 day and night | 0.16 | 0 | 0 | -0.16 | -0.16 | unavailable | 0.89 | 60 | SS 35/6 Kelnot | 4,0 | 0 | 0.16 | 0 | 1 day and night | 0.16 | 0 | 0 | -0.16 | -0.16
61 | SS 35/10 Ceramic | 10+10 | 10 | 10 | 6.19 | 2.77 | 3.42 |  |  | 6.19 | 0 | 10.5 | 4.31 | 4.31 | available | 0.97 | 61 | SS 35/10 Ceramic | 10+10 | 0 | 6.19 |  |  | 6.19 | 0 | 10.5 | 4.31 | 4.31
62 | SS 110/10 Altynovo | 6,3+6,3 | 6.3 | 6.3 | 2.96 | 1.15 | 1.81 |  |  | 2.96 | 0 | 6.62 | 3.66 | 3.66 | available | 0.95 | 62 | SS 110/10 Altynovo | 6,3+6,3 | 2.33 | 5.29 |  |  | 5.29 | 0 | 6.62 | 1.33 | 1.33 | available
63 | SS 110/35/10 Borisogleb | 16+10 | 16 | 10 | 7.83 |  |  |  |  | 7.83 | 0 | 10.5 | 2.67 | 2.67 | available | 0.94 | 63 | SS 110/35/10 Borisogleb | 16+10 |  | 14.364 |  |  | 14.364 | 0 | 10.5 | -3.864 | -3.864 | unavailable
| Nom. capacity MV, МVА | 16+10 |  |  | 3.13 | Т-1: 1.6; Т-2: 1.53; Min 7: 3.13; Min 8: 0; Min 9: 10.5; Min 10: 7.37 |  | Nom. capacity MV, МVА | 16+10 |  | 5.988 |  |  | 5.988 | 0 | 10.5 | 4.512
| Nom. capacity LV, МVА | 16+10 |  |  | 4.7 | Т-1: 2.45; Т-2: 2.25; Min 7: 4.7; Min 8: 0; Min 9: 10.5; Min 10: 5.8 |  | Nom. capacity LV, МVА | 16+10 | 3.676 | 8.376 |  |  | 8.376 | 0 | 10.5 | 2.124
64 | SS 110/35/10 Vasilkovo | 10+10 | 10 | 10 | 3.09 |  |  | 0.52 | 120 | 2.57 | 0 | 10.5 | 7.93 | 7.93 | available | 0.95 | 64 | SS 110/35/10 Vasilkovo | 10+10 |  | 4.595 | 0.52 | 120 | 4.075 | 0 | 10.5 | 6.425 | 6.425 | available
| Nom. capacity MV, МVА | 10+10 |  |  | 2.14 | Т-1: 0; Т-2: 2.14; Min 7: 2.14; Min 8: 0; Min 9: 10.5; Min 10: 8.36 |  | Nom. capacity MV, МVА | 10+10 |  | 2.406 |  |  | 2.406 | 0 | 10.5 | 8.094
| Nom. capacity LV, МVА | 10+10 |  |  | 0.95 | 0.28 | 0.67 | 0.52 | 120 | 0.43 | 0 | 10.5 | 10.07 |  |  |  |  | Nom. capacity LV, МVА | 10+10 | 1.239 | 2.189 | 0.52 | 120 | 1.669 | 0 | 10.5 | 8.831
65 | SS 110/10 Vakhrushevo | 6,3+6,3 | 6.3 | 6.3 | 0.32 | 0.07 | 0.25 | 0.052 | 120 | 0.268 | 0 | 6.62 | 6.352 | 6.352 | available | 0.96 | 65 | SS 110/10 Vakhrushevo | 6,3+6,3 | 0.015 | 0.335 | 0.052 | 120 | 0.283 | 0 | 6.62 | 6.337 | 6.337 | available
66 | SS 110/6 Gavrilov Yam | 16+16 | 16 | 16 | 13.31 | 5.78 | 7.53 |  |  | 13.31 | 0 | 16.8 | 3.49 | 3.49 | available | 0.81 | 66 | SS 110/6 Gavrilov Yam | 16+16 | 0 | 13.31 |  |  | 13.31 | 0 | 16.8 | 3.49 | 3.49 | available
67 | SS 110/6 Kinoplyonka | 6,3+10 | 6.3 | 10 | 10.47 | 4.84 | 5.63 |  |  | 10.47 | 0 | 6.62 | -3.85 | -3.85 | unavailable | 0.94 | 67 | SS 110/6 Kinoplyonka | 6,3+10 | 2.854 | 13.324 |  |  | 13.324 | 0 | 6.62 | -6.704 | -6.704 | unavailable
68 | SS 110/35/10 Klimatino | 6,3+6,3 | 6.3 | 6.3 | 1.23 |  |  |  |  | 1.23 | 0 | 6.62 | 5.39 | 5.39 | available | 0.98 | 68 | SS 110/35/10 Klimatino | 6,3+6,3 |  | 1.345 |  |  | 1.345 | 0 | 6.62 | 5.275 | 5.275 | available
| Nom. capacity MV, МVА | 0+6,3 |  |  | 0.24 | Т-2: 0.24; Min 7: 0.24; Min 8: 0; Min 9: 6.62; Min 10: 6.38 |  | Nom. capacity MV, МVА | 0+6,3 |  | 0.299 |  |  | 0.299 | 0 | 6.62 | 6.321
| Nom. capacity LV, МVА | 6,3+6,3 |  |  | 0.99 | Т-1: 0; Т-2: 0.99; Min 7: 0.99; Min 8: 0; Min 9: 6.62; Min 10: 5.63 |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.056 | 1.046 |  |  | 1.046 | 0 | 6.62 | 5.574
69 | SS 110/35/10 Nila | 6,3+6,3 | 6.3 | 6.3 | 8.12 |  |  | 0.52 | 120 | 7.6 | 0 | 6.62 | -0.98 | -0.98 | unavailable | 0.95 | 69 | SS 110/35/10 Nila | 6,3+6,3 |  | 27.397 | 0.52 | 120 | 26.877 | 0 | 6.62 | -20.257 | -20.257 | unavailable
| Nom. capacity MV, МVА | 6,3+6,3 |  |  | 6.01 | Т-1: 3.06; Т-2: 2.95; Min 7: 6.01; Min 8: 0; Min 9: 6.62; Min 10: 0.61 |  | Nom. capacity MV, МVА | 6,3+6,3 |  | 11.068 |  |  | 11.068 | 0 | 6.62 | -4.448
| Nom. capacity LV, МVА | 6,3+6,3 |  |  | 2.11 | 1.08 | 1.03 | 0.52 | 120 | 1.59 | 0 | 6.62 | 5.03 |  |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 14.219 | 16.329 | 0.52 | 120 | 15.809 | 0 | 6.62 | -9.189
70 | SS 110/35/6 Pereslavl | 25+25 | 25 | 25 | 23.82 |  |  |  |  | 23.82 | 0 | 26.25 | 2.43 | 2.43 | available | 0.94 | 70 | SS 110/35/6 Pereslavl | 25+25 |  | 38.756 |  |  | 38.756 | 0 | 26.25 | -12.506 | -12.506 | unavailable
| Nom. capacity MV, МVА | 25+25 |  |  | 10.23 | Т-1: 3.58; Т-2: 6.65; Min 7: 10.23; Min 8: 0; Min 9: 26.25; Min 10: 16.02 |  | Nom. capacity MV, МVА | 25+25 |  | 24.61 |  |  | 24.61 | 0 | 26.25 | 1.64
| Nom. capacity LV, МVА | 25+25 |  |  | 13.59 | Т-1: 5.97; Т-2: 7.62; Min 7: 13.59; Min 8: 0; Min 9: 26.25; Min 10: 12.66 |  | Nom. capacity LV, МVА | 25+25 | 0.556 | 14.146 |  |  | 14.146 | 0 | 26.25 | 12.104
71 | SS 110/10 Ploski | 2,5+2,5 | 2.5 | 2.5 | 1.68 | 1.01 | 0.67 |  |  | 1.68 | 0 | 2.63 | 0.95 | 0.95 | available | 0.97 | 71 | SS 110/10 Ploski | 2,5+2,5 | 0.656 | 2.336 |  |  | 2.336 | 0 | 2.63 | 0.294 | 0.294 | available
72 | SS 110/35/10 Rostov | 20+25 | 20 | 25 | 20.85 |  |  |  |  | 20.85 | 0 | 21 | 0.15 | 0.15 | available | 0.95 | 72 | SS 110/35/10 Rostov | 20+25 |  | 25.291 |  |  | 25.291 | 0 | 21 | -4.291 | -4.291 | unavailable
| Nom. capacity MV, МVА | 20+25 |  |  | 1.67 | Т-1: 0; Т-2: 1.67; Min 7: 1.67; Min 8: 0; Min 9: 21; Min 10: 19.33 |  | Nom. capacity MV, МVА | 20+25 |  | 2.346 |  |  | 2.346 | 0 | 21 | 18.654
| Nom. Capacity LV, МVА | 20+25 |  |  | 19.18 | Т-1: 9.95; Т-2: 9.23; Min 7: 19.18; Min 8: 0; Min 9: 21; Min 10: 1.82 |  | Nom. Capacity LV, МVА | 20+25 | 3.765 | 22.945 |  |  | 22.945 | 0 | 21 | -1.945
73 | SS 110/35/10 Technical school | 6,3+6,3 | 6.3 | 6.3 | 7.66 |  |  |  |  | 7.66 | 0 | 6.62 | -1.04 | -1.04 | unavailable | 0.94 | 73 | SS 110/35/10 Technical school | 6,3+6,3 |  | 13.673 |  |  | 13.673 | 0 | 6.62 | -7.053 | -7.053 | unavailable
| Nom. capacity MV, МVА | 6,3+6,3 |  |  | 4.45 | Т-1: 4.45; Т-2: 0; Min 7: 4.45; Min 8: 0; Min 9: 6.62; Min 10: 2.17 |  | Nom. capacity MV, МVА | 6,3+6,3 |  | 8.113 |  |  | 8.113 | 0 | 6.62 | -1.493
| Nom. capacity LV, МVА | 6,3+6,3 |  |  | 3.21 | Т-1: 1.68; Т-2: 1.53; Min 7: 3.21; Min 8: 0; Min 9: 6.62; Min 10: 3.41 |  | Nom. capacity LV, МVА | 6,3+6,3 | 2.35 | 5.56 |  |  | 5.56 | 0 | 6.62 | 1.06
74 | SS 110/35/10 Uglich | 25+25 | 25 | 25 | 22.29 |  |  |  |  | 22.29 | 0 | 26.25 | 3.96 | 3.96 | available | 0.93 | 74 | SS 110/35/10 Uglich | 25+25 |  | 34.895 |  |  | 34.895 | 0 | 26.25 | -8.645 | -8.645 | unavailable
| Nom. capacidty MV, МVА | 25+25 |  |  | 18.04 | Т-1: 6.47; Т-2: 11.57; Min 7: 18.04; Min 8: 0; Min 9: 26.25; Min 10: 8.21 |  | Nom. capacidty MV, МVА | 25+25 |  | 25.672 |  |  | 25.672 | 0 | 26.25 | 0.578
| Nom. capacity LV, МVА | 25+25 |  |  | 4.25 | Т-1: 2.34; Т-2: 1.91; Min 7: 4.25; Min 8: 0; Min 9: 26.25; Min 10: 22 |  | Nom. capacity LV, МVА | 25+25 | 4.973 | 9.223 |  |  | 9.223 | 0 | 26.25 | 17.027
75 | SS 110/10 Ustye | 10+10 | 10 | 10 | 3.87 | 2.23 | 1.64 | 0.727 | 120 | 3.143 | 0 | 10.5 | 7.357 | 7.357 | available | 0.9 | 75 | SS 110/10 Ustye | 10+10 | 0.585 | 4.455 | 0.727 | 120 | 3.728 | 0 | 10.5 | 6.772 | 6.772 | available
76 | SS 110/10 Shurskol | 10+10 | 10 | 10 | 2.16 | 1.17 | 0.99 | 0.953 | 120 | 1.207 | 0 | 10.5 | 9.293 | 9.293 | available | 0.93 | 76 | SS 110/10 Shurskol | 10+10 | 0.136 | 2.296 | 0.953 | 120 | 1.343 | 0 | 10.5 | 9.157 | 9.157 | available
77 | SS 110/10 Yur.Sloboda | 10+10 | 10 | 10 | 6.84 | 3.72 | 3.12 | 0.935 | 120 | 5.905 | 0 | 10.5 | 4.595 | 4.595 | available | 0.89 | 77 | SS 110/10 Yur.Sloboda | 10+10 | 2.529 | 9.369 | 0.935 | 120 | 8.434 | 0 | 10.5 | 2.066 | 2.066 | available
78 | SS 35/10 Aleshkino | 2,5+2,5 | 2.5 | 2.5 | 0.69 | 0.09 | 0.6 |  |  | 0.69 | 0 | 2.63 | 1.94 | 1.94 | available | 0.99 | 78 | SS 35/10 Aleshkino | 2,5+2,5 | 0.117 | 0.807 |  |  | 0.807 | 0 | 2.63 | 1.823 | 1.823 | available
79 | SS 35/6 Batki | 1,6+1,6 | 1.6 | 1.6 | 1.03 | 1.03 | 0 |  |  | 1.03 | 0 | 1.68 | 0.65 | 0.65 | available | 0.98 | 79 | SS 35/6 Batki | 1,6+1,6 | 0.972 | 2.002 |  |  | 2.002 | 0 | 1.68 | -0.322 | -0.322 | unavailable
80 | SS 35/10 Beregovaya | 1,6 | 1.6 |  | 0.19 | 0.19 |  | 3.031 | 1 day and night | 0.19 | 0 | 3.031 | 2.841 | 2.841 | available | 0.95 | 80 | SS 35/10 Beregovaya | 1,6 | 0.038 | 0.228 | 3.031 | 1 day and night | 0.228 | 0 | 3.031 | 2.803 | 2.803 | available
81 | SS 35/10 Berendeevo | 2,5+2,5 | 2.5 | 2.5 | 1.35 | 1.12 | 0.23 | 0.242 |  | 1.108 | 0 | 2.63 | 1.522 | 1.522 | available | 0.96 | 81 | SS 35/10 Berendeevo | 2,5+2,5 | 0.164 | 1.514 | 0.242 |  | 1.272 | 0 | 2.63 | 1.358 | 1.358 | available
82 | SS 35/10 Vorzha | 1,8+1,6 | 1.8 | 1.6 | 0.48 | 0.24 | 0.24 | 0.329 | 120 | 0.151 | 0 | 1.68 | 1.529 | 1.529 | available | 0.997 | 82 | SS 35/10 Vorzha | 1,8+1,6 | 0.026 | 0.506 | 0.329 | 120 | 0.177 | 0 | 1.68 | 1.503 | 1.503 | available
83 | SS 35/10 Voshchazhnikovo | 1,6+2,5 | 1.6 | 2.5 | 0.8 | 0.48 | 0.32 | 0.52 | 120 | 0.28 | 0 | 1.68 | 1.4 | 1.4 | available | 0.84 | 83 | SS 35/10 Voshchazhnikovo | 1,6+2,5 | 1.168 | 1.968 | 0.52 | 120 | 1.448 | 0 | 1.68 | 0.232 | 0.232 | available
84 | SS 35/10 Glebovo | 2,5+2,5 | 2.5 | 2.5 | 2.44 | 0.3 | 2.14 |  |  | 2.44 | 0 | 2.63 | 0.19 | 0.19 | available | 0.96 | 84 | SS 35/10 Glebovo | 2,5+2,5 | 5.079 | 7.519 |  |  | 7.519 | 0 | 2.63 | -4.889 | -4.889 | unavailable
85 | SS 35/10 Gorki | 2,5+2,5 | 2.5 | 2.5 | 1.05 | 0.57 | 0.48 |  |  | 1.05 | 0 | 2.63 | 1.58 | 1.58 | available | 0.91 | 85 | SS 35/10 Gorki | 2,5+2,5 | 0.467 | 1.517 |  |  | 1.517 | 0 | 2.63 | 1.113 | 1.113 | available
86 | SS 35/10 Dmitrianovo | 1,6+1,6 | 1.6 | 1.6 | 1.19 | 0.73 | 0.46 |  |  | 1.19 | 0 | 1.68 | 0.49 | 0.49 | available | 0.98 | 86 | SS 35/10 Dmitrianovo | 1,6+1,6 | 0.171 | 1.361 |  |  | 1.361 | 0 | 1.68 | 0.319 | 0.319 | available
87 | SS 35/10 Zaozerye | 2,5+1,6 | 2.5 | 1.6 | 1.16 | 0.47 | 0.69 |  |  | 1.16 | 0 | 1.68 | 0.52 | 0.52 | available | 0.95 | 87 | SS 35/10 Zaozerye | 2,5+1,6 | 0.184 | 1.344 |  |  | 1.344 | 0 | 1.68 | 0.336 | 0.336 | available
88 | SS 35/10 Ilyinskoe | 2,5+2,5 | 2.5 | 2.5 | 1.38 | 0.95 | 0.43 |  |  | 1.38 | 0 | 2.63 | 1.25 | 1.25 | available | 0.94 | 88 | SS 35/10 Ilyinskoe | 2,5+2,5 | 0.164 | 1.544 |  |  | 1.544 | 0 | 2.63 | 1.086 | 1.086 | available
89 | SS 35/10 Kibernetik | 6,3+6,3 | 6.3 | 6.3 | 2.03 | 0.68 | 1.35 |  |  | 2.03 | 0 | 6.62 | 4.59 | 4.59 | available | 0.96 | 89 | SS 35/10 Kibernetik | 6,3+6,3 | 1.347 | 3.377 |  |  | 3.377 | 0 | 6.62 | 3.243 | 3.243 | available
90 | SS 35/10 Klementyevo | 1,6 | 1.6 |  | 0.34 | 0.34 |  | 0.588 | 1 day and night | 0.34 | 0 | 0.588 | 0.248 | 0.248 | available | 0.94 | 90 | SS 35/10 Klementyevo | 1,6 | 0.016 | 0.356 | 0.588 | 1 day and night | 0.356 | 0 | 0.588 | 0.232 | 0.232 | available
91 | SS 35/10 Krasnoe | 4,0+4,0 | 4 | 4 | 2.28 | 0.66 | 1.62 | 0.866 | 120 | 1.414 | 0 | 4.2 | 2.786 | 2.786 | available | 0.97 | 91 | SS 35/10 Krasnoe | 4,0+4,0 | 3.079 | 5.359 | 0.866 | 120 | 4.493 | 0 | 4.2 | -0.293 | -0.293 | unavailable
92 | SS 35/10 Kulakovo | 2,5+2,5 | 2.5 | 2.5 | 1.63 | 1.23 | 0.4 |  |  | 1.63 | 0 | 2.63 | 1 | 1 | available | 0.78 | 92 | SS 35/10 Kulakovo | 2,5+2,5 | 1.296 | 2.926 |  |  | 2.926 | 0 | 2.63 | -0.296 | -0.296 | unavailable
93 | SS 35/6 Kupan | 2,5+2,5 | 2.5 | 2.5 | 2.29 | 1.45 | 0.84 |  |  | 2.29 | 0 | 2.63 | 0.34 | 0.34 | available | 0.99 | 93 | SS 35/6 Kupan | 2,5+2,5 | 1.802 | 4.092 |  |  | 4.092 | 0 | 2.63 | -1.462 | -1.462 | unavailable
94 | SS 35/10 Markovo | 2,5+2,5 | 2.5 | 2.5 | 0.98 | 0.57 | 0.41 | 0.537 | 120 | 0.443 | 0 | 2.63 | 2.187 | 2.187 | available | 0.96 | 94 | SS 35/10 Markovo | 2,5+2,5 | 0.429 | 1.409 | 0.537 | 120 | 0.872 | 0 | 2.63 | 1.758 | 1.758 | available
95 | SS 35/10 Nagorye | 4,0+4,0 | 4 | 4 | 2.94 | 1.33 | 1.61 |  |  | 2.94 | 0 | 4.2 | 1.26 | 1.26 | available | 0.92 | 95 | SS 35/10 Nagorye | 4,0+4,0 | 2.5 | 5.44 |  |  | 5.44 | 0 | 4.2 | -1.24 | -1.24 | unavailable
96 | SS 35/10 Porechye | 4,0+4,0 | 4 | 4 | 1.79 | 1.14 | 0.65 | 0.07 | 120 | 1.72 | 0 | 4.2 | 2.48 | 2.48 | available | 0.94 | 96 | SS 35/10 Porechye | 4,0+4,0 | 0.404 | 2.194 | 0.07 | 120 | 2.124 | 0 | 4.2 | 2.076 | 2.076 | available
97 | SS 35/10 Pruzhinino | 2,5+2,5 | 2.5 | 2.5 | 0.98 | 0.74 | 0.24 |  |  | 0.98 | 0 | 2.63 | 1.65 | 1.65 | available | 0.98 | 97 | SS 35/10 Pruzhinino | 2,5+2,5 | 0.577 | 1.557 |  |  | 1.557 | 0 | 2.63 | 1.073 | 1.073 | available
98 | SS 35/10 Ramenye | 2,5+2,5 | 2.5 | 2.5 | 0.35 | 0.29 | 0.06 | 0.02 | 120 | 0.33 | 0 | 2.63 | 2.3 | 2.3 | available | 0.81 | 98 | SS 35/10 Ramenye | 2,5+2,5 | 0.147 | 0.497 | 0.02 | 120 | 0.477 | 0 | 2.63 | 2.153 | 2.153 | available
99 | SS 35/10 Ryazantsevo | 2,5+2,5 | 2.5 | 2.5 | 1.36 | 0.91 | 0.45 |  |  | 1.36 | 0 | 2.63 | 1.27 | 1.27 | available | 0.95 | 99 | SS 35/10 Ryazantsevo | 2,5+2,5 | 0.176 | 1.536 |  |  | 1.536 | 0 | 2.63 | 1.094 | 1.094 | available
100 | SS 35/10 Saraevo | 1+1,6 | 1 | 1.6 | 1.35 | 0.37 | 0.98 |  |  | 1.35 | 0 | 1.05 | -0.3 | -0.3 | unavailable | 0.98 | 100 | SS 35/10 Saraevo | 1+1,6 | 0.863 | 2.213 |  |  | 2.213 | 0 | 1.05 | -1.163 | -1.163 | unavailable
101 | SS 35/10 Selifontovo | 2,5+2,5 | 2.5 | 2.5 | 1.08 | 0.3 | 0.78 | 0.693 | 120 | 0.387 | 0 | 2.63 | 2.243 | 2.243 | available | 0.96 | 101 | SS 35/10 Selifontovo | 2,5+2,5 | 1.981 | 3.061 | 0.693 | 120 | 2.368 | 0 | 2.63 | 0.262 | 0.262 | available
102 | SS 35/10 Semibratovo | 4,0+4,0 | 4 | 4 | 1.12 | 0.32 | 0.8 | 0.07 | 120 | 1.05 | 0 | 4.2 | 3.15 | 3.15 | available | 0.96 | 102 | SS 35/10 Semibratovo | 4,0+4,0 | 0.342 | 1.462 | 0.07 | 120 | 1.392 | 0 | 4.2 | 2.808 | 2.808 | available
103 | SS 35/10 Skomorokhovo | 1,6+1,6 | 1.6 | 1.6 | 1.11 | 0.03 | 1.08 |  |  | 1.11 | 0 | 1.68 | 0.57 | 0.57 | available | 0.96 | 103 | SS 35/10 Skomorokhovo | 1,6+1,6 | 2.801 | 3.911 |  |  | 3.911 | 0 | 1.68 | -2.231 | -2.231 | unavailable
104 | SS 35/10 Solomidino | 2.5 | 2.5 |  | 1.16 | 1.16 |  | 0.918 | 1 day and night | 1.16 | 0 | 0.918 | -0.242 | -0.242 | unavailable | 0.93 | 104 | SS 35/10 Solomidino | 2.5 | 2.653 | 3.813 | 0.918 | 1 day and night | 3.813 | 0 | 0.918 | -2.895 | -2.895 | unavailable
105 | SS 35/10 Stavotino | 4,0+4,0 | 4 | 4 | 1.69 | 0.61 | 1.08 | 0.277 | 120 | 1.413 | 0 | 4.2 | 2.787 | 2.787 | available | 0.82 | 105 | SS 35/10 Stavotino | 4,0+4,0 | 1.417 | 3.107 | 0.277 | 120 | 2.83 | 0 | 4.2 | 1.37 | 1.37 | available
106 | SS 35/10 Urusovo | 2,5+2,5 | 2.5 | 2.5 | 0.28 | 0.25 | 0.03 | 0.02 | 120 | 0.26 | 0 | 2.63 | 2.37 | 2.37 | available | 0.97 | 106 | SS 35/10 Urusovo | 2,5+2,5 | 0.076 | 0.356 | 0.02 | 120 | 0.336 | 0 | 2.63 | 2.294 | 2.294 | available
107 | SS 35/10 Filimonovo | 2,5+2,5 | 2.5 | 2.5 | 1.63 | 0.34 | 1.29 |  |  | 1.63 | 0 | 2.63 | 1 | 1 | available | 0.93 | 107 | SS 35/10 Filimonovo | 2,5+2,5 | 1.055 | 2.685 |  |  | 2.685 | 0 | 2.63 | -0.055 | -0.055 | unavailable
108 | SS 35/10 Choporovo | 2,5+2,5 | 2.5 | 2.5 | 0.28 | 0.09 | 0.19 |  |  | 0.28 | 0 | 2.63 | 2.35 | 2.35 | available | 0.89 | 108 | SS 35/10 Choporovo | 2,5+2,5 | 0.392 | 0.672 |  |  | 0.672 | 0 | 2.63 | 1.958 | 1.958 | available
109 | SS 35/10 Shchurovo | 2,5+2,5 | 2.5 | 2.5 | 0.99 | 0.48 | 0.51 | 0.277 | 120 | 0.713 | 0 | 2.63 | 1.917 | 1.917 | available | 0.73 | 109 | SS 35/10 Shchurovo | 2,5+2,5 | 0.087 | 1.077 | 0.277 | 120 | 0.8 | 0 | 2.63 | 1.83 | 1.83 | available
110 | SS 35/10 Neksans | 10+10 | 10 | 10 | 1.9 | 0.87 | 1.03 |  |  | 1.9 | 0 | 10.5 | 8.6 | 8.6 | available | 0.8 | 110 | SS 35/10 Neksans | 10+10 | 6.5 | 8.4 |  |  | 8.4 | 0 | 10.5 | 2.1 | 2.1 | available
111 | SS 35/6 Pribrezhnaya | 10+10 | 10 | 10 | 10.67 | 5.99 | 4.68 |  |  | 10.67 | 0 | 10.5 | -0.17 | -0.17 | unavailable | 0.92 | 111 | SS 35/6 Pribrezhnaya | 10+10 | 0.768 | 11.438 |  |  | 11.438 | 0 | 10.5 | -0.938 | -0.938 | unavailable
112 | SS 110/10 Tishino | 25+25 | 25 | 25 | 20.15 | 12.46 | 7.69 |  |  | 20.15 | 0 | 26.25 | 6.1 | 6.1 | available | 0.99 | 112 | SS 110/10 Tishino | 25+25 | 0.218 | 20.368 |  |  | 20.368 | 0 | 26.25 | 5.882 | 5.882
113 | SS 110/10 Product pipeline | 6,3+6,3 | 6.3 | 6.3 | 1.6 | 0.12 | 1.48 |  |  | 1.6 | 0 | 6.62 | 5.02 | 5.02 | available | 0.99 | 113 | SS 110/10 Product pipeline | 6,3+6,3 | 0 | 1.6 |  |  | 1.6 | 0 | 6.62 | 5.02 | 5.02 | available
114 | SS 110/10 Nekouz | 6,3+6,3 | 6.3 | 6.3 | 2.16 | 0.73 | 1.43 | 0.052 | 120 | 2.108 | 0 | 6.62 | 4.512 | 4.512 | available | 0.92 | 114 | SS 110/10 Nekouz | 6,3+6,3 | 0.052 | 2.212 | 0.052 | 120 | 2.16 | 0 | 6.62 | 4.46 | 4.46 | available
115 | SS 110/6 Yuzhnaya | 25+25 | 25 | 25 | 16.94 | 8.43 | 8.51 |  |  | 16.94 | 0 | 26.25 | 9.31 | 9.31 | available | 0.94 | 115 | SS 110/6 Yuzhnaya | 25+25 | 0.123 | 17.063 |  |  | 17.063 | 0 | 26.25 | 9.187 | 9.187 | available
116 | SS 110/10 Optika | 10+10 | 10 | 10 | 5.69 | 3.16 | 2.53 | 0.52 | 120 | 5.17 | 0 | 10.5 | 5.33 | 5.33 | available | 0.95 | 116 | SS 110/10 Optika | 10+10 | 0.66 | 6.35 | 0.52 | 120 | 5.83 | 0 | 10.5 | 4.67 | 4.67 | available
117 | SS 110/6 Poligrafmash | 16+16 | 16 | 16 | 10.43 | 5.78 | 4.65 |  |  | 10.43 | 0 | 16.8 | 6.37 | 6.37 | available | 0.95 | 117 | SS 110/6 Poligrafmash | 16+16 | 0.024 | 10.454 |  |  | 10.454 | 0 | 16.8 | 6.346 | 6.346 | available
118 | SS 110/6/6 Zapadnaya | 63+63 | 63 | 63 | 34.46 | 17.83 | 16.63 |  |  | 34.46 | 0 | 66.15 | 31.69 | 31.69 | available | 0.87 | 118 | SS 110/6/6 Zapadnaya | 63+63 | 2.557 | 37.017 |  |  | 37.017 | 0 | 66.15 | 29.133 | 29.133 | available
119 | SS 110/35/6 Volzhskaya | 40+40 | 40 | 40 | 15.13 |  |  |  |  | 15.13 | 0 | 42 | 26.87 | 26.87 | available | 0.84 | 119 | SS 110/35/6 Volzhskaya | 40+40 |  | 15.396 |  |  | 15.396 | 0 | 42 | 26.604 | 26.604 | available
| Nom. capacity MV, МVА | 40+40 |  |  | 0 | Т-1: 0; Т-2: 0; Min 8: 0 |  | Nom. capacity MV, МVА | 40+40 | [5 empty] | 0
| Nom. capacity LV, МVА | 40+40 |  |  | 15.13 | Т-1: 6.49; Т-2: 8.64; Min 7: 15.13; Min 8: 0; Min 9: 42; Min 10: 26.87 |  | Nom. capacity LV, МVА | 40+40 | 0.266 | 15.396 |  |  | 15.396 | 0 | 42 | 26.604
120 | SS 110/35/6 Levoberezhnaya | 16+16 | 16 | 16 | 14.04 |  |  |  |  | 14.04 | 0 | 16.8 | 2.76 | 2.76 | available | 0.96 | 120 | SS 110/35/6 Levoberezhnaya | 16+16 |  | 16.182 |  |  | 16.182 | 0 | 16.8 | 0.618 | 0.618 | available
| Nom. capacity MV, МVА | 16+16 |  |  | 8.62 | Т-1: 3.92; Т-2: 4.7; Min 7: 8.62; Min 8: 0; Min 9: 16.8; Min 10: 8.18 |  | Nom. capacity MV, МVА | 16+16 |  | 10.715 |  |  | 10.715 | 0 | 16.8 | 6.085
| Nom. capacity LV, МVА | 16+16 |  |  | 5.42 | Т-1: 2.28; Т-2: 3.14; Min 7: 5.42; Min 8: 0; Min 9: 16.8; Min 10: 11.38 |  | Nom. capacity LV, МVА | 16+16 | 0.047 | 5.467 |  |  | 5.467 | 0 | 16.8 | 11.333
121 | SS 110/35/10 Pishchalkino | 7,5+7,5 | 7.5 | 7.5 | 1.7 |  |  |  |  | 1.7 | 0 | 7.88 | 6.18 | 6.18 | available | 0.93 | 121 | SS 110/35/10 Pishchalkino | 7,5+7,5 |  | 1.7 |  |  | 1.7 | 0 | 7.88 | 6.18 | 6.18 | available
| Nom. capacity MV, МVА | 7,5+7,5 |  |  | 0.95 | Т-1: 0.95; Т-2: 0; Min 7: 0.95; Min 8: 0; Min 9: 7.88; Min 10: 6.93 |  | Nom. capacity MV, МVА | 7,5+7,5 |  | 0.95 |  |  | 0.95 | 0 | 7.88 | 6.93
| Nom. capacity LV, МVА | 7,5+7,5 |  |  | 0.75 | Т-1: 0.62; Т-2: 0.13; Min 7: 0.75; Min 8: 0; Min 9: 7.88; Min 10: 7.13 |  | Nom. capacity LV, МVА | 7,5+7,5 | 0 | 0.75 |  |  | 0.75 | 0 | 7.88 | 7.13
122 | SS 110/6 Dock yard | 10+10 | 10 | 10 | 5.5 | 2.8 | 2.7 |  |  | 5.5 | 0 | 10.5 | 5 | 5 | available | 0.93 | 122 | SS 110/6 Dock yard | 10+10 | 0.177 | 5.677 |  |  | 5.677 | 0 | 10.5 | 4.823 | 4.823 | available
123 | SS 110/6 Selekhovo | 6,3+6,3 | 6.3 | 6.3 | 3.62 | 2.97 | 0.65 |  |  | 3.62 | 0 | 6.62 | 3 | 3 | available | 0.96 | 123 | SS 110/6 Selekhovo | 6,3+6,3 | 0.973 | 4.593 |  |  | 4.593 | 0 | 6.62 | 2.027 | 2.027 | available
124 | SS 35/6 Kamenniki | 4,0+4,0 | 4 | 4 | 2.29 | 1.32 | 0.97 |  |  | 2.29 | 0 | 4.2 | 1.91 | 1.91 | available | 0.91 | 124 | SS 35/6 Kamenniki | 4,0+4,0 | 0.164 | 2.454 |  |  | 2.454 | 0 | 4.2 | 1.746 | 1.746 | available
125 | SS 35/10 Shashkovo | 1,6+1,6 | 1.6 | 1.6 | 0.6 | 0.44 | 0.16 |  |  | 0.6 | 0 | 1.68 | 1.08 | 1.08 | available | 0.94 | 125 | SS 35/10 Shashkovo | 1,6+1,6 | 0.458 | 1.058 |  |  | 1.058 | 0 | 1.68 | 0.622 | 0.622 | available
126 | SS 110/6 Veretye | 25+25 | 25 | 25 | 17.82 | 9.16 | 8.66 |  |  | 17.82 | 0 | 26.25 | 8.43 | 8.43 | available | 0.92 | 126 | SS 110/6 Veretye | 25+25 | 0.769 | 18.589 |  |  | 18.589 | 0 | 26.25 | 7.661 | 7.661 | available
127 | SS 35/10 Nikolo-Korma | 4,0+4,0 | 4 | 4 | 2.29 | 1.5 | 0.79 | 0.52 | 120 | 1.77 | 0 | 4.2 | 2.43 | 2.43 | available | 0.96 | 127 | SS 35/10 Nikolo-Korma | 4,0+4,0 | 2.772 | 5.062 | 0.52 | 120 | 4.542 | 0 | 4.2 | -0.342 | -0.342 | unavailable
128 | SS 35/10 Arefino | 2,5+2,5 | 2.5 | 2.5 | 1.26 | 0.7 | 0.56 | 0.035 | 120 | 1.225 | 0 | 2.63 | 1.405 | 1.405 | available | 0.94 | 128 | SS 35/10 Arefino | 2,5+2,5 | 0.092 | 1.352 | 0.035 | 120 | 1.317 | 0 | 2.63 | 1.313 | 1.313 | available
129 | SS 35/10 Knyazevo | 1,6+2,5 | 1.6 | 2.5 | 0.72 | 0.07 | 0.65 |  |  | 0.72 | 0 | 1.68 | 0.96 | 0.96 | available | 0.92 | 129 | SS 35/10 Knyazevo | 1,6+2,5 | 0.132 | 0.852 |  |  | 0.852 | 0 | 1.68 | 0.828 | 0.828 | available
130 | SS 35/10 Pokrov | 1,6+1,6 | 1.6 | 1.6 | 0.55 | 0.31 | 0.24 | 0.242 | 120 | 0.308 | 0 | 1.68 | 1.372 | 1.372 | available | 0.99 | 130 | SS 35/10 Pokrov | 1,6+1,6 | 0.017 | 0.567 | 0.242 | 120 | 0.325 | 0 | 1.68 | 1.355 | 1.355 | available
131 | SS 35/10 Anikovo | 2,5+2,5 | 2.5 | 2.5 | 0.85 | 0.61 | 0.24 | 0.017 | 120 | 0.833 | 0 | 2.63 | 1.797 | 1.797 | available | 0.85 | 131 | SS 35/10 Anikovo | 2,5+2,5 | 0.035 | 0.885 | 0.017 | 120 | 0.868 | 0 | 2.63 | 1.762 | 1.762 | available
132 | SS 35/10 Novoe selo | 2,5+2,5 | 2.5 | 2.5 | 0.86 | 0.54 | 0.32 |  |  | 0.86 | 0 | 2.63 | 1.77 | 1.77 | available | 0.91 | 132 | SS 35/10 Novoe selo | 2,5+2,5 | 0.656 | 1.516 |  |  | 1.516 | 0 | 2.63 | 1.114 | 1.114 | available
133 | SS 35/10 Bolshoe selo | 6,3+6,3 | 6.3 | 6.3 | 5.63 | 3.26 | 2.37 |  |  | 5.63 | 0 | 6.62 | 0.99 | 0.99 | available | 0.95 | 133 | SS 35/10 Bolshoe selo | 6,3+6,3 | 1.301 | 6.931 |  |  | 6.931 | 0 | 6.62 | -0.311 | -0.311 | unavailable
134 | SS 35/10 Breytovo | 6,3+6,3 | 6.3 | 6.3 | 4.34 | 2.01 | 2.33 |  |  | 4.34 | 0 | 6.62 | 2.28 | 2.28 | available | 0.95 | 134 | SS 35/10 Breytovo | 6,3+6,3 | 1.794 | 6.134 |  |  | 6.134 | 0 | 6.62 | 0.486 | 0.486 | available
135 | SS 35/10 Stanilovo | 1,6+1,6 | 1.6 | 1.6 | 0.68 | 0.16 | 0.52 | 0.208 | 120 | 0.472 | 0 | 1.68 | 1.208 | 1.208 | available | 0.94 | 135 | SS 35/10 Stanilovo | 1,6+1,6 | 0.128 | 0.808 | 0.208 | 120 | 0.6 | 0 | 1.68 | 1.08 | 1.08 | available
136 | SS 35/10 Znamovo | 2,5+2,5 | 2.5 | 2.5 | 1.01 | 0.31 | 0.7 | 0.173 | 120 | 0.837 | 0 | 2.63 | 1.793 | 1.793 | available | 0.92 | 136 | SS 35/10 Znamovo | 2,5+2,5 | 0.114 | 1.124 | 0.173 | 120 | 0.951 | 0 | 2.63 | 1.679 | 1.679 | available
137 | SS 35/10 Rozhdestvenno | 2,5+2,5 | 2.5 | 2.5 | 1.14 | 0.63 | 0.51 |  |  | 1.14 | 0 | 2.63 | 1.49 | 1.49 | available | 0.94 | 137 | SS 35/10 Rozhdestvenno | 2,5+2,5 | 0.118 | 1.258 |  |  | 1.258 | 0 | 2.63 | 1.372 | 1.372 | available
138 | SS 35/10 Zapolye | 2,5+2,5 | 2.5 | 2.5 | 0.55 | 0.25 | 0.3 |  |  | 0.55 | 0 | 2.63 | 2.08 | 2.08 | available | 0.99 | 138 | SS 35/10 Zapolye | 2,5+2,5 | 0.202 | 0.752 |  |  | 0.752 | 0 | 2.63 | 1.878 | 1.878 | available
139 | SS 35/10 Tikhmenevo | 1,6+1,6 | 1.6 | 1.6 | 1.25 | 0.55 | 0.7 | 0.329 | 120 | 0.921 | 0 | 1.68 | 0.759 | 0.759 | available | 0.93 | 139 | SS 35/10 Tikhmenevo | 1,6+1,6 | 0.192 | 1.442 | 0.329 | 120 | 1.113 | 0 | 1.68 | 0.567 | 0.567 | available
140 | SS 35/10 Latskoe | 1,6+2,5 | 1.6 | 2.5 | 0.24 | 0.17 | 0.07 | 0.052 | 120 | 0.188 | 0 | 1.68 | 1.492 | 1.492 | available | 0.64 | 140 | SS 35/10 Latskoe | 1,6+2,5 | 0.02 | 0.26 | 0.052 | 120 | 0.208 | 0 | 1.68 | 1.472 | 1.472 | available
141 | SS 35/10 Borok | 2,5+4,0 | 2.5 | 4 | 1.21 | 0.81 | 0.4 | 0.156 | 120 | 1.054 | 0 | 2.63 | 1.576 | 1.576 | available | 0.93 | 141 | SS 35/10 Borok | 2,5+4,0 | 0.485 | 1.695 | 0.156 | 120 | 1.539 | 0 | 2.63 | 1.091 | 1.091 | available
142 | SS 35/10 Myshkin | 6,3+6,3 | 6.3 | 6.3 | 3.57 | 2.28 | 1.29 |  |  | 3.57 | 0 | 6.62 | 3.05 | 3.05 | available | 0.94 | 142 | SS 35/10 Myshkin | 6,3+6,3 | 1.835 | 5.405 |  |  | 5.405 | 0 | 6.62 | 1.215 | 1.215 | available
143 | SS 110/10 Volga | 5,6+6,3 | 5.6 | 6.3 | 1.9 | 0.91 | 0.99 |  |  | 1.9 | 0 | 5.88 | 3.98 | 3.98 | available | 0.95 | 143 | SS 110/10 Volga | 5,6+6,3 | 0.19 | 2.09 |  |  | 2.09 | 0 | 5.88 | 3.79 | 3.79 | available
144 | SS 35/10 Krasnaya Gorka | 4,0+2,5 | 4 | 2.5 | 1.35 | 0.67 | 0.68 | 0.104 | 120 | 1.246 | 0 | 2.63 | 1.384 | 1.384 | available | 0.95 | 144 | SS 35/10 Krasnaya Gorka | 4,0+2,5 | 0.982 | 2.332 | 0.104 | 120 | 2.228 | 0 | 2.63 | 0.402 | 0.402 | available
145 | SS 110/35/6 Vostochnaya | 25+25 | 25 | 25 | 22.48 |  |  |  |  | 22.48 | 0 | 26.25 | 3.77 | 3.77 | available | 0.79 | 145 | SS 110/35/6 Vostochnaya | 25+25 |  | 25.448 |  |  | 25.448 | 0 | 26.25 | 0.802 | 0.802 | available
| Nom. capacity MV, МVА | 25+25 |  |  | 4.51 | Т-1: 4.51; Т-2: 0; Min 7: 4.51; Min 8: 0; Min 9: 26.25; Min 10: 21.74 |  | Nom. capacity MV, МVА | 25+25 |  | 7.08 |  |  | 7.08 | 0 | 26.25 | 19.17
| Nom. capacity LV, МVА | 25+25 |  |  | 17.97 | Т-1: 10.14; Т-2: 7.83; Min 7: 17.97; Min 8: 0; Min 9: 26.25; Min 10: 8.28 |  | Nom. capacity LV, МVА | 25+25 | 0.398 | 18.368 |  |  | 18.368 | 0 | 26.25 | 7.882
146 | SS 110/35/10 Zalesye | 10+10 | 10 | 10 | 7.7 |  |  | 1.126 | 120 | 6.574 | 0 | 10.5 | 3.926 | 3.926 | available | 0.93 | 146 | SS 110/35/10 Zalesye | 10+10 |  | 7.929 | 1.126 | 120 | 6.803 | 0 | 10.5 | 3.697 | 3.697 | available
| Nom. capacity MV, МVА | 10+10 |  |  | 1.16 | Т-1: 0.32; Т-2: 0.84; Min 7: 1.16; Min 8: 0; Min 9: 10.5; Min 10: 9.34 |  | Nom. capacity MV, МVА | 10+10 |  | 1.274 |  |  | 1.274 | 0 | 10.5 | 9.226
| Nom. capacity LV, МVА | 10+10 |  |  | 6.54 | 3.01 | 3.53 | 1.126 | 120 | 5.414 | 0 | 10.5 | 5.086 |  |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.115 | 6.655 | 1.126 | 120 | 5.529 | 0 | 10.5 | 4.971
147 | SS 110/10 Lugovaya | 6,3+6,3 | 6.3 | 6.3 | 2.39 | 1.64 | 0.75 |  |  | 2.39 | 0 | 6.62 | 4.23 | 4.23 | available | 0.88 | 147 | SS 110/10 Lugovaya | 6,3+6,3 | 0.397 | 2.787 |  |  | 2.787 | 0 | 6.62 | 3.833 | 3.833 | available
148 | SS 110/35/10 Lom | 10+10 | 10 | 10 | 8.8 |  |  | 1.057 | 120 | 7.743 | 0 | 10.5 | 2.757 | 2.757 | available | 0.92 | 148 | SS 110/35/10 Lom | 10+10 |  | 11.914 | 1.057 | 120 | 10.857 | 0 | 10.5 | -0.357 | -0.357 | unavailable
| Nom. capacity MV, МVА | 10+10 |  |  | 6.73 | Т-1: 4.25; Т-2: 2.48; Min 7: 6.73; Min 8: 0; Min 9: 10.5; Min 10: 3.77 |  | Nom. capacity MV, МVА | 10+10 |  | 9.137 |  |  | 9.137 | 0 | 10.5 | 1.363
| Nom. capacity LV, МVА | 10+10 |  |  | 2.07 | 1.65 | 0.42 | 1.057 | 120 | 1.013 | 0 | 10.5 | 9.487 |  |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.707 | 2.777 | 1.057 | 120 | 1.72 | 0 | 10.5 | 8.78
149 | SS 35/10 Varegovo | 1,6+2,5 | 1.6 | 2.5 | 0.66 | 0.43 | 0.23 |  |  | 0.66 | 0 | 1.68 | 1.02 | 1.02 | available | 0.91 | 149 | SS 35/10 Varegovo | 1,6+2,5 | 0.45 | 1.11 |  |  | 1.11 | 0 | 1.68 | 0.57 | 0.57 | available
150 | SS 110/35/10 Shestikhino | 10+10 | 10 | 10 | 6.79 |  |  | 0.208 | 120 | 6.582 | 0 | 10.5 | 3.918 | 3.918 | available | 0.97 | 150 | SS 110/35/10 Shestikhino | 10+10 |  | 10.2355 | 0.208 | 120 | 10.0275 | 0 | 10.5 | 0.4725 | 0.4725 | available
| Nom. capacity MV, МVА | 10+10 |  |  | 6.24 | Т-1: 1.98; Т-2: 4.26; Min 7: 6.24; Min 8: 0; Min 9: 10.5; Min 10: 4.26 |  | Nom. capacity MV, МVА | 10+10 |  | 9.4015 |  |  | 9.4015 | 0 | 10.5 | 1.0985
| Nom. capacity LV, МVА | 10+10 |  |  | 0.55 | 0.27 | 0.28 | 0.208 | 120 | 0.342 | 0 | 10.5 | 10.158 |  |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.284 | 0.834 | 0.208 | 120 | 0.626 | 0 | 10.5 | 9.874
151 | SS 110/35/10 Kryukovo | 6.3 | 6.3 |  | 2.53 | Min 8: 0; Min 11: 1.482; Min 12: available; Min 13: 0.94 | 151 | SS 110/35/10 Kryukovo | 6.3 |  | 3.4665 |  |  |  | 0 |  |  | 1.463 | available
| Nom. capacidty MV, МVА | 6.3 |  |  | 2.28 | Т-1: 2.28; Min 8: 0 |  | Nom. capacidty MV, МVА | 6.3 |  | 3.1975 |  |  |  | 0
| Nom. capacity LV, МVА | 6.3 |  |  | 0.25 | 0.25 |  | 1.732 | 1 day and night | 0.25 | 0 | 1.732 | 1.482 |  |  |  |  | Nom. capacity LV, МVА | 6.3 | 0.019 | 0.269 | 1.732 | 1 day and night | 0.269 | 0 | 1.732 | 1.463
152 | SS 35/10 Beloe | 2.5 | 2.5 |  | 0.56 | 0.56 |  | 1.455 | 1 day and night | 0.56 | 0 | 1.455 | 0.895 | 0.895 | available | 0.96 | 152 | SS 35/10 Beloe | 2.5 | 0.065 | 0.625 | 1.455 | 1 day and night | 0.625 | 0 | 1.455 | 0.83 | 0.83 | available
153 | SS 110/35/10 Glebovo | 10 | 10 |  | 5.5 | Min 8: 0; Min 11: -2.276; Min 12: unavailable; Min 13: 0.96 | 153 | SS 110/35/10 Glebovo | 10 |  | 9.493 |  |  |  | 0 |  |  | -4.691 | unavailable
| Nom. capacity MV, МVА | 10 |  |  | 2.41 | Т-1: 2.41; Min 8: 0 |  | Nom. capacity MV, МVА | 10 |  | 3.988 |  |  |  | 0
| Nom. capacity LV, МVА | 10 |  |  | 3.09 | 3.09 |  | 0.814 | 1 day and night | 3.09 | 0 | 0.814 | -2.276 |  |  |  |  | Nom. capacity LV, МVА | 10 | 2.415 | 5.505 | 0.814 | 1 day and night | 5.505 | 0 | 0.814 | -4.691
154 | SS 35/6 Pesochnoye | 1,8+1,8 | 1.8 | 1.8 | 1.48 | 1.03 | 0.45 |  |  | 1.48 | 0 | 1.89 | 0.41 | 0.41 | available | 0.85 | 154 | SS 35/6 Pesochnoye | 1,8+1,8 | 0 | 1.48 |  |  | 1.48 | 0 | 1.89 | 0.41 | 0.41
155 | SS 35/10 Demino | 2,5+2,5 | 2.5 | 2.5 | 0.52 | 0.15 | 0.37 | 0.035 |  | 0.485 | 0 | 2.63 | 2.145 | 2.145 | available | 0.98 | 155 | SS 35/10 Demino | 2,5+2,5 | 0.003 | 0.523 | 0.035 |  | 0.488 | 0 | 2.63 | 2.142 | 2.142
156 | SS 110/6 KS-18 | 63+63 | 63 | 63 | 17.89 | 17.05 | 0.84 |  |  | 17.89 | 0 | 66.15 | 48.26 | 48.26 | available | 0.999 | 156 | SS 110/6 KS-18 | 63+63 | 0 | 17.89 |  |  | 17.89 | 0 | 66.15 | 48.26 | 48.26
157 | SS 35/6 Makeikha | 1.6 | 1.6 |  | 0.25 | 0.25 |  | 0 | 1 day and night | 0.25 | 0 | 0 | -0.25 | -0.25 | unavailable | 1 | 157 | SS 35/6 Makeikha | 1.6 | 0 | 0.25 | 0 | 1 day and night | 0.25 | 0 | 0 | -0.25 | -0.25 | unavailable
158 | SS 35/10 Ermakovo | 1.6 | 1.6 |  | 0.87 | 0.87 |  | 1.143 | 1 day and night | 0.87 | 0 | 1.143 | 0.273 | 0.273 | available | 0.94 | 158 | SS 35/10 Ermakovo | 1.6 | 0.29 | 1.16 | 1.143 | 1 day and night | 1.16 | 0 | 1.143 | -0.017 | -0.017 | unavailable
159 | SS 35/10 Milyushino | 1.6 | 1.6 |  | 0.78 | 0.78 |  | 0.814 | 1 day and night | 0.78 | 0 | 0.814 | 0.034 | 0.034 | available | 0.93 | 159 | SS 35/10 Milyushino | 1.6 | 1.246 | 2.026 | 0.814 | 1 day and night | 2.026 | 0 | 0.814 | -1.212 | -1.212 | unavailable
160 | SS 35/10 Sutka | 2.5 | 2.5 |  | 0.62 | 0.62 |  | 0.606 | 1 day and night | 0.62 | 0 | 0.606 | -0.014 | -0.014 | unavailable | 0.87 | 160 | SS 35/10 Sutka | 2.5 | 0.039 | 0.659 | 0.606 | 1 day and night | 0.659 | 0 | 0.606 | -0.053 | -0.053 | unavailable
161 | SS 35/10 Sit | 1.6 | 1.6 |  | 0.58 | 0.58 |  | 0.572 | 1 day and night | 0.58 | 0 | 0.572 | -0.008 | -0.008 | unavailable | 0.83 | 161 | SS 35/10 Sit | 1.6 | 0.586 | 1.166 | 0.572 | 1 day and night | 1.166 | 0 | 0.572 | -0.594 | -0.594 | unavailable
162 | SS 35/10 Gorelovo | 1.6 | 1.6 |  | 0.82 | 0.82 |  | 0.901 | 1 day and night | 0.82 | 0 | 0.901 | 0.081 | 0.081 | available | 0.95 | 162 | SS 35/10 Gorelovo | 1.6 | 0.739 | 1.559 | 0.901 | 1 day and night | 1.559 | 0 | 0.901 | -0.658 | -0.658 | unavailable
163 | SS 35/6 Pishchalkino | 1.6 | 1.6 |  | 0.75 | 0.75 |  | 0 | 1 day and night | 0.75 | 0 | 0 | -0.75 | -0.75 | unavailable | 0.91 | 163 | SS 35/6 Pishchalkino | 1.6 | 0 | 0.75 | 0 | 1 day and night | 0.75 | 0 | 0 | -0.75 | -0.75 | unavailable
164 | SS 35/6 Varegovo | 1.6 | 1.6 |  | 0.02 | 0.02 |  | 0 | 1 day and night | 0.02 | 0 | 0 | -0.02 | -0.02 | unavailable | 0.89 | 164 | SS 35/6 Varegovo | 1.6 | 0.005 | 0.025 | 0 | 1 day and night | 0.025 | 0 | 0 | -0.025 | -0.025 | unavailable
165 | SS 35/10 Levoberezhnaya | 4 | 4 |  | 1.39 | 1.39 |  | 1.351 | 1 day and night | 1.39 | 0 | 1.351 | -0.039 | -0.039 | unavailable | 0.94 | 165 | SS 35/10 Levoberezhnaya | 4 | 1.289 | 2.679 | 1.351 | 1 day and night | 2.679 | 0 | 1.351 | -1.328 | -1.328 | unavailable
166 | SS 110/10 Depot | 16 | 16 |  | 4.34 | 4.34 |  | 4.34 | 1 day and night | 4.34 | 0 | 4.34 | 0 | 0 | available | 0.98 | 166 | SS 110/10 Depot | 16 | 0 | 4.34 | 4.34 | 1 day and night | 4.34 | 0 | 4.34 | 0 | 0
| Total: | 2914.7 | 1489.4 | 1425.3 | 873.93 | [12 empty] | Total: | 2914.7 |  | 1081.746
| deficit |  |  |  |  | Min 11: 16.409 |  | deficit | [9 empty] | 43.199
| proficit |  |  |  |  | Min 11: 671.799 |  | proficit | [9 empty] | 351.9025
Заместитель директора по техническим
вопросам - главный инженер
Note on H217: Т3
Note on H215: Т3
Note on H195: Т2
Note on I195: Т3
Note on H216: Т1
Note on H218: Т3

## Total current deficit Winter
The list of closed supply centers of IDGC of Centre according to winter load measurements in 2011 (current deficit of capacity).
No. | Name of supply center, voltage class | [5 empty] | Current deficit, MVA
Yarenergo
1 | SS 35/10 Mikhaylovsky | 6.3 |  |  |  |  | -1.24
2 | SS 35/10 Wave | 4,0+2,5 |  |  |  |  | -0.01
3 | SS 35/6 Zavolzhsky | 10+10 |  |  |  |  | -0.54
4 | SS 110/35/6 Pavlovsk | 20+25 |  |  |  |  | -4.52
5 | SS 35/6 Kelnot | 4,0 |  |  |  |  | -0.16
6 | SS 110/6 Film | 6,3+10 |  |  |  |  | -3.85
7 | SS 110/35/10 Niles | 6,3+6,3 |  |  |  |  | -0.98
8 | SS 110/35/10 Technical school | 6,3+6,3 |  |  |  |  | -1.04
9 | SS 35/10 Sarayevo | 1+1,6 |  |  |  |  | -0.3
10 | SS 35/10 Solomidino | 2.5 | 3.48 | 3.48 | 0 | 2.63 | -0.242
11 | SS 35/6 Coastal | 10+10 | 11.67 | 11.67 | 0 | 10.5 | -0.17
12 | SS 110/35/10 Glebovo | 10 | 25.25 | 25.25 | 0 | 21 | -2.276
13 | SS 35/6 Makeiha | 1.6 | 45.91 | 45.91 | 0 | 42 | -0.25
14 | SS 35/10 Sutka | 2.5 | 6.83 | 6.83 | 0 | 6.62 | -0.014
15 | SS 35/10 Sit | 1.6 |  |  |  |  | -0.008
16 | SS 35/6 Pishchalkino | 1.6 |  |  |  |  | -0.75
17 | SS 35/6 Varegovo | 1.6 |  |  |  |  | -0.02
18 | SS 35/10 Left-bank | 4 |  |  |  |  | -0.039
Total current deficit (winter) | [6 empty] | 16.409

## Total expected deficit Winter
The list of closed supply centers of IDGC of Centre with expected load taking into account new connections and other development of the electical networks.
No. | Name of supply center, voltage class | Expected deficit/proficit, MVA | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number provided that technical requirements at connections or other measures performed for reconstruction of the supply center, pcs/ MVA | Дополнительная мощность по выданным ТУ на ТП, МВА | Ожидаемая нагрузка ЦП, МВА | Полная перераспределяемая мощность в перспективе с учетом выполнения мероприятий ТУ или других мероприятий по реконструкции сети инвестпрограмм и др. |  | Полная мощность с учётом перераспределения, МВА | Ограничивающие факторы, МВА | Допустимая нагрузка расчётная в режиме n-1, МВА | Пропускная способность ЦП, МВА | Current deficit/proficit, MVA
[5 empty] | МВА | Мин.
1 | 2 |  | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
Yarenergo
1 | SS 35/10 Mihajlovsky | 6.3 |  | 3.48 |  |  | 3.48 | 0 | 2.63 | -0.85 | -1.243 | unavailable
2 | SS 35/10 Shirine | 4 | 0.2 | 3.26 |  |  | 3.26 | 0 | 2.63 | -0.63 | -0.192 | unavailable
3 | SS 110/35/10 Abbakumtsevo | 10+10 | 1.8815 | 12.1915 |  |  | 12.1915 | 0 | 10.5 | -1.6915 | -13.812 | unavailable
4 | SS 35/10 Vatolino | 4,0+4,0 | 4.6946 | 42.2246 |  |  | 42.2246 | 0 | 42 | -0.22459 | -4.016 | unavailable
5 | SS 35/10 Renaissance | 4,0+4,0 | 0.432 | 12.102 |  |  | 12.102 | 0 | 10.5 | -1.602 | -0.415 | unavailable
6 | SS 35/10 Wave | 4,0+2,5 | 8.5515 | 25.2515 |  |  | 25.2515 | 0 | 21 | -4.2515 | -0.076 | unavailable
7 | SS 35/10 Guzitsino | 4,0+4,0 | 5.3149 | 51.2249 |  |  | 51.2249 | 0 | 42 | -9.2249 | -4.982 | unavailable
8 | SS 110/6 Depots | 16+16 | Мин. 12: 5.511; Мин. 13: unavailable
9 | SS 35/10 Dorozhaevo | 1,6+1,6 | Мин. 12: -1.186; Мин. 13: unavailable
10 | SS 35/6 Zavolzhsky | 10+10 | Мин. 12: -1.332; Мин. 13: unavailable
11 | SS 35/10 Kurba | 2,5+2,5 | Мин. 12: -0.043; Мин. 13: unavailable
12 | SS 35/10 Modelovo-2 | 6,3+6,3 | Мин. 12: -5.462; Мин. 13: unavailable
13 | SS 110/35/6 Pavlovsk | 20+25 | Мин. 12: -5.119; Мин. 13: unavailable
14 | SS 35/10 Dispensary | 2,5+2,5 | Мин. 12: -0.809; Мин. 13: unavailable
15 | SS 35/6 Chebakovo | 2,5+2,5 | 2.027 | 3.237 | 0.39 | 120 | 2.847 | 0 | 2.63 | -0.217 | -0.795 | unavailable
16 | SS 110/35/10 Borisogleb | 16+10 | 0.01 | 6.84 |  |  | 6.84 | 0 | 6.62 | -0.22 | -3.864 | unavailable
17 | SS 110/6 Film | 6,3+10 | 23.7523 | 39.9523 |  |  | 39.9523 | 0 | 26.25 | -13.7023 | -6.704 | unavailable
18 | SS 110/35/10 Niles | 6,3+6,3 | 0.587 | 10.157 |  |  | 10.157 | 0 | 6.62 | -3.537 | -20.257 | unavailable
19 | SS 110/35/6 Pereslavl | 25+25 | 7.5755 | 9.3555 | 0.37 | 120 | 8.9855 | 0 | 6.62 | -2.3655 | -12.506 | unavailable
20 | SS 110/35/10 Rostov | 20+25 | 14.4054 | 27.9154 |  |  | 27.9154 | 0 | 26.25 | -1.6654 | -4.291 | unavailable
21 | SS 110/35/10 Technical school | 6,3+6,3 | 3.4781 | 21.7981 |  |  | 21.7981 | 0 | 21 | -0.7981 | -7.053 | unavailable
22 | SS 110/35/10 Uglich | 25+25 | 25.538 | 30.568 |  |  | 30.568 | 0 | 26.25 | -4.318 | -8.645 | unavailable
23 | SS 35/6 Fathers | 1,6+1,6 | 1.645 | 4.405 |  |  | 4.405 | 0 | 2.63 | -1.775 | -0.322 | unavailable
24 | SS 35/10 Glebovo | 2,5+2,5 | 0.273 | 2.723 |  |  | 2.723 | 0 | 2.63 | -0.093 | -4.889 | unavailable
25 | SS 35/10 Red | 4,0+4,0 | 2.193 | 3.283 | 0.3 | 120 | 2.983 | 0 | 2.63 | -0.353 | -0.293 | unavailable
26 | SS 35/10 Kulakovo | 2,5+2,5 | Мин. 12: -0.296; Мин. 13: unavailable
27 | SS 35/6 Kupan | 2,5+2,5 | Мин. 12: -1.462; Мин. 13: unavailable
28 | SS 35/10 Uplands | 4,0+4,0 | Мин. 12: -1.24; Мин. 13: unavailable
29 | SS 35/10 Sarajevo | 1+1,6 | Мин. 12: -1.163; Мин. 13: unavailable
30 | SS 35/10 Skomorohovo | 1,6+1,6 | Мин. 12: -2.231; Мин. 13: unavailable
31 | SS 35/10 Solomidino | 2.5 | Мин. 12: -2.895; Мин. 13: unavailable
32 | SS 35/10 Filimonovo | 2,5+2,5 | Мин. 12: -0.055; Мин. 13: unavailable
33 | SS 35/6 Coastal | 10+10 | Мин. 12: -0.938; Мин. 13: unavailable
34 | SS 35/10 Nikolo-forages | 4,0+4,0 | Мин. 12: -0.342; Мин. 13: unavailable
35 | SS 35/10 Big village | 6,3+6,3 | Мин. 12: -0.311; Мин. 13: unavailable
36 | SS 110/35/10 Breakage | 10+10 | Мин. 12: -0.357; Мин. 13: unavailable
37 | SS 110/35/10 Glebovo | 10 | Мин. 12: -4.691; Мин. 13: unavailable
38 | SS 35/6 Makeiha | 1.6 | Мин. 12: -0.25; Мин. 13: unavailable
39 | SS 35/10 Ermakovo | 1.6 | Мин. 12: -0.017; Мин. 13: unavailable
40 | SS 35/10 Miljushino | 1.6 | Мин. 12: -1.212; Мин. 13: unavailable
41 | SS 35/10 Sutka | 2.5 | Мин. 12: -0.053; Мин. 13: unavailable
42 | SS 35/10 Sit | 1.6 | Мин. 12: -0.594; Мин. 13: unavailable
43 | SS 35/10 Gorelovo | 1.6 | Мин. 12: -0.658; Мин. 13: unavailable
44 | SS 35/6 Pishchalkino | 1.6 | Мин. 12: -0.75; Мин. 13: unavailable
45 | SS 35/6 Varegovo | 1.6 | Мин. 12: -0.025; Мин. 13: unavailable
46 | SS 35/10 Left-bank | 4 | Мин. 12: -1.328; Мин. 13: unavailable
| Total: |  | Мин. 12: -123.663