## Yaroslavl
Calculation of transmission capacity of supply centres of IDGC of Center - Yarenergo following the winter peak load measurements in 2011
[13 empty] | table 1 | [16 empty] | table 2
No. | Name of supply center, voltage class | Current deficit | [12 empty] | Note | cosφ | No. | Name of supply center, voltage class |  | Expected deficit/proficit | [10 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Summary total capacity of supply centers following the results of measurements of load maximal Sмах | ячейки скрыть |  | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Supply Center deficit/proficit, MVA | [6 empty] | Installed power capacity of transformers Sinst. including their number provided that technical requirements at connections or other measures performed for reconstruction of the supply center, pcs/ MVA | Дополнительная мощность по выданным ТУ на ТП, МВт | Additional capacity issued for technical specifications for TS, МВА | Expected load of Supply Center, MVA | Total capacity redistributed according to operating rules, MVA for the time period provided that technical requirements at connections or other measures performed for reconstruction of the grid investment programs and etc. |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Expected deficit/proficit, MVA
|  |  | MVA |  | MVA |  |  | MVA | Min | [14 empty] | MVA | Min
1 | 2 | 3 |  |  | 4 | Т-1 | Т-2 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 1 | 2 | 2 | 3 |  | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | SS 35/10 Matveevo | 1.6 | 1.6 |  | 0.28 | 0.28 |  | 0.883 | 1 day and night | 0.28 | 0 | 0.883 | 0.603 | 0.603 | available | 0.99 | 1 | SS 35/10 Matveevo | SS35/10Матвеево | 1.6 | 0.466 | 0.47071 | 0.75071 | 0.883 | 1 day and night | 0.75071 | 0 | 0.883 | 0.13229 | 0.13229 | available
2 | SS 35/10 Mikhailovskoe | 6.3 | 6.3 |  | 1.24 | 1.24 |  | 0 | 1 day and night | 1.24 | 0 | 0 | -1.24 | -1.24 | unavailable | 0.97 | 2 | SS 35/10 Mikhailovskoe | SS35/10Михайловское | 6.3 | 0.003 | 0.0030928 | 1.2431 | 0 | 1 day and night | 1.2431 | 0 | 0 | -1.2431 | -1.2431 | unavailable
3 | SS 35/10 Shirinye | 4 | 4 |  | 1.85 |  | 1.85 | 2.095 | 1 day and night | 1.85 | 0 | 2.095 | 0.245 | 0.245 | available | 0.95 | 3 | SS 35/10 Shirinye | SS35/10Ширинье | 4 | 0.435 | 0.45789 | 2.3079 | 2.095 | 1 day and night | 2.3079 | 0 | 2.095 | -0.21289 | -0.21289 | unavailable
4 | SS 110/10 Pokrov | 2.5 | 2.5 |  | 0.3 | 0.3 |  | 1.273 | 1 day and night | 0.3 | 0 | 1.273 | 0.973 | 0.973 | available | 0.8 | 4 | SS 110/10 Pokrov | SS110/10Покров | 2.5 | 0.052 | 0.065 | 0.365 | 1.273 | 1 day and night | 0.365 | 0 | 1.273 | 0.908 | 0.908 | available
5 | SS 35/10 Obnora | 1.6 | 1.6 |  | 0.2 | 0.2 |  | 1.212 | 1 day and night | 0.2 | 0 | 1.212 | 1.012 | 1.012 | available | 0.91 | 5 | SS 35/10 Obnora | SS35/10Обнора | 1.6 | 0.0435 | 0.047802 | 0.2478 | 1.212 | 1 day and night | 0.2478 | 0 | 1.212 | 0.9642 | 0.9642 | available
6 | SS 110/35/10 Abbakumtsevo | 10+10 | 10 | 10 | 8.3 |  |  |  |  | 8.3 | 0 | 10.5 | 2.2 | 2.2 | available | 0.97 | 6 | SS 110/35/10 Abbakumtsevo | SS110/35/10Аббакумцево | 10+10 | 0 | 0 | 21.7986 |  |  | 21.7986 | 0 | 10.5 | -11.2986 | -11.2986 | unavailable
| Nom. capacity MV, МVА | 10+10 |  |  | 7.1 | Т-1: 1.82; Т-2: 5.28; Min 7: 7.1; Min 8: 0; Min 9: 10.5; Min 10: 3.4 |  | Nom. capacity MV, МVА | Ном.МощностьСН,МВА | 10+10 | 0 |  | 16.6501 |  |  | 16.6501 | 0 | 10.5 | -6.1501
| Nom. capacity LV, МVА | 10+10 |  |  | 1.2 | Т-1: 0.58; Т-2: 0.62; Min 7: 1.2; Min 8: 0; Min 9: 10.5; Min 10: 9.3 |  | Nom. capacity LV, МVА | Ном.мощностьНН,МВА | 10+10 | 3.83 | 3.9485 | 5.1485 |  |  | 5.1485 | 0 | 10.5 | 5.3515
7 | SS 35/10 Ananyino | 2,5+2,5 | 2.5 | 2.5 | 1.15 | 0.86 | 0.29 |  |  | 1.15 | 0 | 2.63 | 1.48 | 1.48 | available | 0.97 | 7 | SS 35/10 Ananyino | SS35/10Ананьино | 2,5+2,5 | 1.313 | 1.3536 | 2.5036 |  |  | 2.5036 | 0 | 2.63 | 0.12639 | 0.12639 | available
8 | SS 110/10/10 Bragino | 40+40 | 40 | 40 | 26.79 | 12.53 | 14.26 | 2.252 | 120 | 24.538 | 0 | 42 | 17.462 | 17.462 | available | 0.97 | 8 | SS 110/10/10 Bragino | SS110/10/10Брагино | 40+40 | 3.4184 | 3.5241 | 30.3141 | 2.252 | 120 | 28.0621 | 0 | 42 | 13.9379 | 13.9379 | available
9 | SS 35/10 Burmakino-1 | 4,0+4,0 | 4 | 4 | 1.73 | 0.68 | 1.05 | 0.52 | 120 | 1.21 | 0 | 4.2 | 2.99 | 2.99 | available | 0.97 | 9 | SS 35/10 Burmakino-1 | SS35/10Бурмакино-1 | 4,0+4,0 | 0.8495 | 0.87577 | 2.6058 | 0.52 | 120 | 2.0858 | 0 | 4.2 | 2.1142 | 2.1142 | available
10 | SS 35/10 Vatolino | 4,0+4,0 | 4 | 4 | 3.14 | 1.7 | 1.44 |  |  | 3.14 | 0 | 4.2 | 1.06 | 1.06 | available | 0.96 | 10 | SS 35/10 Vatolino | SS35/10Ватолино | 4,0+4,0 | 5.563 | 5.7948 | 8.9348 |  |  | 8.9348 | 0 | 4.2 | -4.7348 | -4.7348 | unavailable
11 | SS 35/6 Vederniki | 6,3+6,3 | 6.3 | 6.3 | 4.55 | 1.55 | 3 |  |  | 4.55 | 0 | 6.62 | 2.07 | 2.07 | available | 0.92 | 11 | SS 35/6 Vederniki | SS35/6Ведерники | 6,3+6,3 | 0.0392 | 0.042609 | 4.5926 |  |  | 4.5926 | 0 | 6.62 | 2.0274 | 2.0274 | available
12 | SS 35/10 Velikovskaya | 4,0+4,0 | 4 | 4 | 1.78 | 1.27 | 0.51 |  |  | 1.78 | 0 | 4.2 | 2.42 | 2.42 | available | 0.82 | 12 | SS 35/10 Velikovskaya | SS35/10Великовская | 4,0+4,0 | 0.112 | 0.13659 | 1.9166 |  |  | 1.9166 | 0 | 4.2 | 2.2834 | 2.2834 | available
13 | SS 35/10 Velikoe Selo | 1,6+1,6 | 1.6 | 1.6 | 0.62 | 0.52 | 0.1 |  |  | 0.62 | 0 | 1.68 | 1.06 | 1.06 | available | 0.93 | 13 | SS 35/10 Velikoe Selo | SS35/10ВеликоеСело | 1,6+1,6 | 0.062 | 0.066667 | 0.68667 |  |  | 0.68667 | 0 | 1.68 | 0.99333 | 0.99333 | available
14 | SS 35/10 Vozrozhdenie | 4,0+4,0 | 4 | 4 | 1.23 | 0.36 | 0.87 |  |  | 1.23 | 0 | 4.2 | 2.97 | 2.97 | available | 0.96 | 14 | SS 35/10 Vozrozhdenie | SS35/10Возрождение | 4,0+4,0 | 0.7604 | 0.79208 | 2.0221 |  |  | 2.0221 | 0 | 4.2 | 2.1779 | 2.1779 | available
15 | SS 35/10 Volna | 4,0+2,5 | 4 | 2.5 | 2.64 | 1.51 | 1.13 |  |  | 2.64 | 0 | 2.63 | -0.01 | -0.01 | unavailable | 0.88 | 15 | SS 35/10 Volna | SS35/10Волна | 4,0+2,5 | 0 | 0 | 2.64 |  |  | 2.64 | 0 | 2.63 | -0.01 | -0.01 | unavailable
16 | SS 35/10 Vyatskoe | 2,5+2,5 | 2.5 | 2.5 | 1.75 | 0.89 | 0.86 | 0.139 | 120 | 1.611 | 0 | 2.63 | 1.019 | 1.019 | available | 0.93 | 16 | SS 35/10 Vyatskoe | SS35/10Вятское | 2,5+2,5 | 0.387 | 0.41613 | 2.1661 | 0.139 | 120 | 2.0271 | 0 | 2.63 | 0.60287 | 0.60287 | available
17 | SS 35/10 Gorinskaya | 2,5+2,5 | 2.5 | 2.5 | 0.64 | 0.32 | 0.32 | 0.277 | 120 | 0.363 | 0 | 2.63 | 2.267 | 2.267 | available | 0.93 | 17 | SS 35/10 Gorinskaya | SS35/10Горинская | 2,5+2,5 | 0.161 | 0.17312 | 0.81312 | 0.277 | 120 | 0.53612 | 0 | 2.63 | 2.0939 | 2.0939 | available
18 | SS 35/10 Grigoryevskoe | 4,0+4,0 | 4 | 4 | 2.18 | 1.76 | 0.42 | 0.294 | 120 | 1.886 | 0 | 4.2 | 2.314 | 2.314 | available | 0.96 | 18 | SS 35/10 Grigoryevskoe | SS35/10Григорьевское | 4,0+4,0 | 0.7995 | 0.83281 | 3.0128 | 0.294 | 120 | 2.7188 | 0 | 4.2 | 1.4812 | 1.4812 | available
19 | SS 35/10 Guzitsino | 4,0+4,0 | 4 | 4 | 3.41 | 1.27 | 2.14 | 1.316 | 120 | 2.094 | 0 | 4.2 | 2.106 | 2.106 | available | 0.97 | 19 | SS 35/10 Guzitsino | SS35/10Гузицино | 4,0+4,0 | 5.0229 | 5.1782 | 8.5882 | 1.316 | 120 | 7.2722 | 0 | 4.2 | -3.0722 | -3.0722 | unavailable
20 | SS 35/10 State Fire-Fighting Service Yaroslavl | 6,3+6,3 | 6.3 | 6.3 | 2.04 | 1.74 | 0.3 |  |  | 2.04 | 0 | 6.62 | 4.58 | 4.58 | available | 0.99 | 20 | SS 35/10 State Fire-Fighting Service Yaroslavl | SS35/10ГSSЯрославль | 6,3+6,3 | 0.011 | 0.011111 | 2.0511 |  |  | 2.0511 | 0 | 6.62 | 4.5689 | 4.5689 | available
21 | SS 110/6 Depo | 16+16 | 16 | 16 | 8.56 | 5.24 | 3.32 |  |  | 8.56 | 0 | 16.8 | 8.24 | 8.24 | available | 0.97 | 21 | SS 110/6 Depo | SS110/6Депо | 16+16 | 1.9459 | 2.0061 | 10.5661 |  |  | 10.5661 | 0 | 16.8 | 6.2339 | 6.2339 | available
22 | SS 35/10 Dorozhaevo | 1,6+1,6 | 1.6 | 1.6 | 1.31 | 0.61 | 0.7 | 0.675 | 120 | 0.635 | 0 | 1.68 | 1.045 | 1.045 | available | 0.96 | 22 | SS 35/10 Dorozhaevo | SS35/10Дорожаево | 1,6+1,6 | 2.157 | 2.2469 | 3.5569 | 0.675 | 120 | 2.8819 | 0 | 1.68 | -1.2019 | -1.2019 | unavailable
23 | SS 110/10 Druzhba | 16+16 | 16 | 16 | 5.17 | 1.63 | 3.54 | 1.706 | 120 | 3.464 | 0 | 16.8 | 13.336 | 13.336 | available | 0.91 | 23 | SS 110/10 Druzhba | SS110/10Дружба | 16+16 | 0.97023 | 1.0662 | 6.2362 | 1.706 | 120 | 4.5302 | 0 | 16.8 | 12.2698 | 12.2698 | available
24 | SS 35/10 Dubki | 6,3+6,3 | 6.3 | 6.3 | 3.8 | 2.58 | 1.22 | 1.083 | 120 | 2.717 | 0 | 6.62 | 3.903 | 3.903 | available | 0.91 | 24 | SS 35/10 Dubki | SS35/10Дубки | 6,3+6,3 | 1.4505 | 1.594 | 5.394 | 1.083 | 120 | 4.311 | 0 | 6.62 | 2.309 | 2.309 | available
25 | SS 35/10 Dybino | 2,5+2,5 | 2.5 | 2.5 | 0.96 | 0.5 | 0.46 |  |  | 0.96 | 0 | 2.63 | 1.67 | 1.67 | available | 0.91 | 25 | SS 35/10 Dybino | SS35/10Дыбино | 2,5+2,5 | 0.499 | 0.54835 | 1.5084 |  |  | 1.5084 | 0 | 2.63 | 1.1216 | 1.1216 | available
26 | SS 35/6 Zavolzhskaya | 10+10 | 10 | 10 | 11.04 | 2.92 | 8.12 |  |  | 11.04 | 0 | 10.5 | -0.54 | -0.54 | unavailable | 0.97 | 26 | SS 35/6 Zavolzhskaya | SS35/6Заволжская | 10+10 | 0.20973 | 0.21622 | 11.2562 |  |  | 11.2562 | 0 | 10.5 | -0.75622 | -0.75622 | unavailable
27 | SS 110/6/6 Institutskaya | 40+40 | 40 | 40 | 34.35 | 18.11 | 16.24 |  |  | 34.35 | 0 | 42 | 7.65 | 7.65 | available | 0.95 | 27 | SS 110/6/6 Institutskaya | SS110/6/6Институтская | 40+40 | 1.2718 | 1.3388 | 35.6888 |  |  | 35.6888 | 0 | 42 | 6.3112 | 6.3112 | available
28 | SS 35/10 Koza | 1,6+1,6 | 1.6 | 1.6 | 0.33 | 0.1 | 0.23 | 0.07 | 120 | 0.26 | 0 | 1.68 | 1.42 | 1.42 | available | 0.98 | 28 | SS 35/10 Koza | SS35/10Коза | 1,6+1,6 | 0.01 | 0.010204 | 0.3402 | 0.07 | 120 | 0.2702 | 0 | 1.68 | 1.4098 | 1.4098 | available
29 | SS 110/35/6 Konstantinovo | 15+16 | 15 | 16 | 8.83 |  |  | 0.021 | 120 | 8.809 | 0 | 15.75 | 6.941 | 6.941 | available | 0.91 | 29 | SS 110/35/6 Konstantinovo | SS110/35/6Константиново | 15+16 | 0 | 0 | 12.5558 | 0.021 | 120 | 12.5348 | 0 | 15.75 | 3.2152 | 3.2152 | available
| Nom. capacity MV, МVА | 15+16 |  |  | 6.13 | Т-1: 4.14; Т-2: 1.99; Min 7: 6.13; Min 8: 0; Min 9: 15.75; Min 10: 9.62 |  | Nom. capacity MV, МVА | Ном.МощностьСН,МВА | 15+16 | 0 |  | 8.5174 |  |  | 8.5174 | 0 | 15.75 | 7.2326
| Nom. capacity LV, МVА | 15+16 |  |  | 2.7 | 1.94 | 0.76 | 0.021 | 120 | 2.679 | 0 | 15.75 | 13.071 |  |  |  |  | Nom. capacity LV, МVА | Ном.мощностьНН,МВА | 15+16 | 1.218 | 1.3385 | 4.0385 | 0.021 | 120 | 4.0175 | 0 | 15.75 | 11.7325
30 | SS 35/10 Kurba | 2,5+2,5 | 2.5 | 2.5 | 2.35 | 0.47 | 1.88 | 0.277 | 120 | 2.073 | 0 | 2.63 | 0.557 | 0.557 | available | 0.96 | 30 | SS 35/10 Kurba | SS35/10Курба | 2,5+2,5 | 0.632 | 0.65833 | 3.0083 | 0.277 | 120 | 2.7313 | 0 | 2.63 | -0.10133 | -0.10133 | unavailable
31 | SS 35/10 Lesnye Polyany | 10+10 | 10 | 10 | 6.52 | 3.43 | 3.09 | 1.212 | 120 | 5.308 | 0 | 10.5 | 5.192 | 5.192 | available | 0.91 | 31 | SS 35/10 Lesnye Polyany | SS35/10ЛесныеПоляны | 10+10 | 3.23 | 3.5495 | 10.0695 | 1.212 | 120 | 8.8575 | 0 | 10.5 | 1.6425 | 1.6425 | available
32 | SS 35/10 Modelovo-2 | 6,3+6,3 | 6.3 | 6.3 | 5.43 | 1.52 | 3.91 | 1.905 | 120 | 3.525 | 0 | 6.62 | 3.095 | 3.095 | available | 0.98 | 32 | SS 35/10 Modelovo-2 | SS35/10Моделово-2 | 6,3+6,3 | 6.6179 | 6.753 | 12.183 | 1.905 | 120 | 10.278 | 0 | 6.62 | -3.658 | -3.658 | unavailable
33 | SS 35/10 Nekrasovo | 16+16 | 16 | 16 | 9.99 | 3.8 | 6.19 |  |  | 9.99 | 0 | 16.8 | 6.81 | 6.81 | available | 0.96 | 33 | SS 35/10 Nekrasovo | SS35/10Некрасово | 16+16 | 2.5214 | 2.6264 | 12.6164 |  |  | 12.6164 | 0 | 16.8 | 4.1836 | 4.1836 | available
34 | SS 35/10 Nikolskoe | 2,5+2,5 | 2.5 | 2.5 | 0.77 | 0.37 | 0.4 | 0.416 | 120 | 0.354 | 0 | 2.63 | 2.276 | 2.276 | available | 0.94 | 34 | SS 35/10 Nikolskoe | SS35/10Никольское | 2,5+2,5 | 0.125 | 0.13298 | 0.90298 | 0.416 | 120 | 0.48698 | 0 | 2.63 | 2.143 | 2.143 | available
35 | SS 110/35/6 Oil refinary plant | 25+25 | 25 | 25 | 16.7 |  |  |  |  | 16.7 | 0 | 26.25 | 9.55 | 9.55 | available | 0.95 | 35 | SS 110/35/6 Oil refinary plant | SS110/35/6НПЗ | 25+25 | 0 | 0 | 24.4379 |  |  | 24.4379 | 0 | 26.25 | 1.8121 | 1.8121 | available
| Nom. capacity MV, МVА | 25+25 |  |  | 8.79 | Т-1: 5.2; Т-2: 3.59; Min 7: 8.79; Min 8: 0; Min 9: 26.25; Min 10: 17.46 |  | Nom. capacity MV, МVА | Ном.МощностьСН,МВА | 25+25 | 0 |  | 8.8437 |  |  | 8.8437 | 0 | 26.25 | 17.4063
| Nom. capacity LV, МVА | 25+25 |  |  | 7.91 | Т-1: 3.72; Т-2: 4.19; Min 7: 7.91; Min 8: 0; Min 9: 26.25; Min 10: 18.34 |  | Nom. capacity LV, МVА | Ном.мощностьНН,МВА | 25+25 | 7.3 | 7.6842 | 15.5942 |  |  | 15.5942 | 0 | 26.25 | 10.6558
36 | SS 110/6/6 Orion | 40+40 | 40 | 40 | 17.27 | 7.44 | 9.83 |  |  | 17.27 | 0 | 42 | 24.73 | 24.73 | available | 0.83 | 36 | SS 110/6/6 Orion | SS110/6/6Орион | 40+40 | 0.1581 | 0.19048 | 17.4605 |  |  | 17.4605 | 0 | 42 | 24.5395 | 24.5395 | available
37 | SS 110/35/6 Pavlovskaya | 20+25 | 20 | 25 | 25.52 |  |  |  |  | 25.52 | 0 | 21 | -4.52 | -4.52 | unavailable | 0.92 | 37 | SS 110/35/6 Pavlovskaya | SS110/35/6Павловская | 20+25 | 0 |  | 25.9549 |  |  | 25.9549 | 0 | 21 | -4.9549 | -4.9549 | unavailable
| Nom. capacity MV, МVА | 20+25 |  |  | 8.98 | Т-1: 0; Т-2: 8.98; Min 7: 8.98; Min 8: 0; Min 9: 21; Min 10: 12.02 |  | Nom. capacity MV, МVА | Ном.МощностьСН,МВА | 20+25 | 0 |  | 9.3964 |  |  | 9.3964 | 0 | 21 | 11.6036
| Nom. capaity LV, МVА | 20+25 |  |  | 16.54 | Т-1: 8.57; Т-2: 7.97; Min 7: 16.54; Min 8: 0; Min 9: 21; Min 10: 4.46 |  | Nom. capaity LV, МVА | Ном.мощностьНН,МВА | 20+25 | 0.017 | 0.018478 | 16.5585 |  |  | 16.5585 | 0 | 21 | 4.4415
38 | SS 110/10 Pereval | 16+16 | 16 | 16 | 8.04 | 3.87 | 4.17 |  |  | 8.04 | 0 | 16.8 | 8.76 | 8.76 | available | 0.99 | 38 | SS 110/10 Pereval | SS110/10Перевал | 16+16 | 6.8497 | 6.9189 | 14.9589 |  |  | 14.9589 | 0 | 16.8 | 1.8411 | 1.8411 | available
39 | SS 110/6/6 Perekop | 25+25 | 25 | 25 | 9.59 | 4.68 | 4.91 |  |  | 9.59 | 0 | 26.25 | 16.66 | 16.66 | available | 0.95 | 39 | SS 110/6/6 Perekop | SS110/6/6Перекоп | 25+25 | 0.62314 | 0.65593 | 10.2459 |  |  | 10.2459 | 0 | 26.25 | 16.0041 | 16.0041 | available
40 | SS 110/6/6 Poligraf | 40+40 | 40 | 40 | 30.75 | 18.47 | 12.28 |  |  | 30.75 | 0 | 42 | 11.25 | 11.25 | available | 0.98 | 40 | SS 110/6/6 Poligraf | SS110/6/6Полиграф | 40+40 | 0.61286 | 0.62537 | 31.3754 |  |  | 31.3754 | 0 | 42 | 10.6246 | 10.6246 | available
41 | SS 110/35/10 Prechistoe | 10+10 | 10 | 10 | 4.44 |  |  | 0.52 | 120 | 3.92 | 0 | 10.5 | 6.58 | 6.58 | available | 0.93 | 41 | SS 110/35/10 Prechistoe | SS110/35/10Пречистое | 10+10 | 0 |  | 5.1415 | 0.52 | 120 | 4.6215 | 0 | 10.5 | 5.8785 | 5.8785 | available
| Nom. capacity MV, МVА | 10+10 |  |  | 1.64 | Т-1: 0.07; Т-2: 1.57; Min 7: 1.64; Min 8: 0; Min 9: 10.5; Min 10: 8.86 |  | Nom. capacity MV, МVА | Ном.МощностьСН,МВА | 10+10 | 0 |  | 1.7668 |  |  | 1.7668 | 0 | 10.5 | 8.7332
| Nom. capacity LV, МVА | 10+10 |  |  | 2.8 | 1.34 | 1.46 | 0.52 | 120 | 2.28 | 0 | 10.5 | 8.22 |  |  |  |  | Nom. capacity LV, МVА | Ном.мощностьНН,МВА | 10+10 | 0.53442 | 0.57465 | 3.3746 | 0.52 | 120 | 2.8546 | 0 | 10.5 | 7.6454
42 | SS 35/10 Preventorium | 2,5+2,5 | 2.5 | 2.5 | 0.93 | 0.36 | 0.57 | 0.346 | 120 | 0.584 | 0 | 2.63 | 2.046 | 2.046 | available | 0.96 | 42 | SS 35/10 Preventorium | SS35/10Профилакторий | 2,5+2,5 | 2.7003 | 2.8128 | 3.7428 | 0.346 | 120 | 3.3968 | 0 | 2.63 | -0.76681 | -0.76681 | unavailable
43 | SS 35/10 Rozhdestveno | 2,5+2,5 | 2.5 | 2.5 | 0.23 | 0.03 | 0.2 | 0.052 | 120 | 0.178 | 0 | 2.63 | 2.452 | 2.452 | available | 0.77 | 43 | SS 35/10 Rozhdestveno | SS35/10Рождествено | 2,5+2,5 | 0.043 | 0.055844 | 0.28584 | 0.052 | 120 | 0.23384 | 0 | 2.63 | 2.3962 | 2.3962 | available
44 | SS 110/6/6 Severnaya | 63+63 | 63 | 63 | 36.14 | 16.37 | 19.77 |  |  | 36.14 | 0 | 66.15 | 30.01 | 30.01 | available | 0.97 | 44 | SS 110/6/6 Severnaya | SS110/6/6Северная | 63+63 | 0.44638 | 0.46019 | 36.6002 |  |  | 36.6002 | 0 | 66.15 | 29.5498 | 29.5498 | available
45 | SS 35/10 Sereda | 2,5+2,5 | 2.5 | 2.5 | 1.31 | 0.5 | 0.81 | 0.831 | 120 | 0.479 | 0 | 2.63 | 2.151 | 2.151 | available | 0.89 | 45 | SS 35/10 Sereda | SS35/10Середа | 2,5+2,5 | 0.341 | 0.38315 | 1.6931 | 0.831 | 120 | 0.86215 | 0 | 2.63 | 1.7679 | 1.7679 | available
46 | SS 110/6 Tormoznaya | 16+16 | 16 | 16 | 12.84 | 9.59 | 3.25 |  |  | 12.84 | 0 | 16.8 | 3.96 | 3.96 | available | 0.96 | 46 | SS 110/6 Tormoznaya | SS110/6Тормозная | 16+16 | 0.08 | 0.083333 | 12.9233 |  |  | 12.9233 | 0 | 16.8 | 3.8767 | 3.8767 | available
47 | SS 110/6 Petrol station pump | 16+16 | 16 | 16 | 4.89 | 2.47 | 2.42 |  |  | 4.89 | 0 | 16.8 | 11.91 | 11.91 | available | 0.98 | 47 | SS 110/6 Petrol station pump | SS110/6ТРК | 16+16 | 0 | 0 | 4.89 |  |  | 4.89 | 0 | 16.8 | 11.91 | 11.91 | available
48 | SS 35/10 Troitsa | 2,5+2,5 | 2.5 | 2.5 | 0.41 | 0.32 | 0.09 | 0.277 | 120 | 0.133 | 0 | 2.63 | 2.497 | 2.497 | available | 0.89 | 48 | SS 35/10 Troitsa | SS35/10Троица | 2,5+2,5 | 0.043 | 0.048315 | 0.45831 | 0.277 | 120 | 0.18131 | 0 | 2.63 | 2.4487 | 2.4487 | available
49 | SS 35/10 Tunoshna | 2,5+2,5 | 2.5 | 2.5 | 0.9 | 0.37 | 0.53 | 0.173 | 120 | 0.727 | 0 | 2.63 | 1.903 | 1.903 | available | 0.97 | 49 | SS 35/10 Tunoshna | SS35/10Туношна | 2,5+2,5 | 0.631 | 0.65052 | 1.5505 | 0.173 | 120 | 1.3775 | 0 | 2.63 | 1.2525 | 1.2525 | available
50 | SS 35/10 Tutaev-35 | 10+10 | 10 | 10 | 6.35 | 3.11 | 3.24 |  |  | 6.35 | 0 | 10.5 | 4.15 | 4.15 | available | 0.96 | 50 | SS 35/10 Tutaev-35 | SS35/10Тутаев-35 | 10+10 | 0.489 | 0.50938 | 6.8594 |  |  | 6.8594 | 0 | 10.5 | 3.6406 | 3.6406 | available
51 | SS 110/10 Tufanovo | 2,5+2,5 | 2.5 | 2.5 | 0.75 | 0.62 | 0.13 |  |  | 0.75 | 0 | 2.63 | 1.88 | 1.88 | available | 0.96 | 51 | SS 110/10 Tufanovo | SS110/10Туфаново | 2,5+2,5 | 0.34872 | 0.36325 | 1.1133 |  |  | 1.1133 | 0 | 2.63 | 1.5167 | 1.5167 | available
52 | SS 35/10 Urozhay | 4,0+4,0 | 4 | 4 | 1.61 | 0.73 | 0.88 | 0.346 | 120 | 1.264 | 0 | 4.2 | 2.936 | 2.936 | available | 0.98 | 52 | SS 35/10 Urozhay | SS35/10Урожай | 4,0+4,0 | 1.386 | 1.4143 | 3.0243 | 0.346 | 120 | 2.6783 | 0 | 4.2 | 1.5217 | 1.5217 | available
53 | SS 110/35/10 Khaldeevo | 3,2+6,3 | 3.2 | 6.3 | 2.69 | Min 8: 0; Min 11: 2.813; Min 12: available; Min 13: 0.92 | 53 | SS 110/35/10 Khaldeevo | SS110/35/10Халдеево | 3,2+6,3 | 0.02 | 0.021739 | 0.72 |  |  |  | 0 |  |  | 2.813 | available
| Nom. capacity MV, МVА | 0+6,3 |  |  | 1.97 | Т-2: 1.97; Min 8: 0 |  | Nom. capacity MV, МVА | Ном.МощностьСН,МВА | 0+6,3 | 0 | [5 empty] | 0
| Nom. capacity LV, МVА | 3.2+6.3 |  |  | 0.72 | 0.57 | 0.15 | 0.173 | 120 | 0.547 | 0 | 3.36 | 2.813 |  |  |  |  | Nom. capacity LV, МVА | Ном.мощностьНН,МВА | 3.2+6.3 | 0 | 0 | 0.72 | 0.173 | 120 | 0.547 | 0 | 3.36 | 2.813
54 | SS 110/10 Chayka | 25+25 | 25 | 25 | 17.51 | 10.5 | 7.01 |  |  | 17.51 | 0 | 26.25 | 8.74 | 8.74 | available | 0.98 | 54 | SS 110/10 Chayka | SS110/10/10Чайка | 25+25 | 2.4 | 2.449 | 19.959 |  |  | 19.959 | 0 | 26.25 | 6.291 | 6.291 | available
55 | SS 35/6 Chebakovo | 2,5+2,5 | 2.5 | 2.5 | 1.55 | 0.97 | 0.58 | 0.139 | 120 | 1.411 | 0 | 2.63 | 1.219 | 1.219 | available | 0.93 | 55 | SS 35/6 Chebakovo | SS35/6Чебаково | 2,5+2,5 | 1.833 | 1.971 | 3.521 | 0.139 | 120 | 3.382 | 0 | 2.63 | -0.75197 | -0.75197 | unavailable
56 | SS 35/10 Shchedrino | 4,0+4,0 | 4 | 4 | 1.31 | 0.23 | 1.08 |  |  | 1.31 | 0 | 4.2 | 2.89 | 2.89 | available | 0.94 | 56 | SS 35/10 Shchedrino | SS35/10Щедрино | 4,0+4,0 | 1.229 | 1.3074 | 2.6174 |  |  | 2.6174 | 0 | 4.2 | 1.5826 | 1.5826 | available
57 | SS 110/6 /6 Yuzhnaya | 40+40 | 40 | 40 | 29.6 | 12.7 | 16.9 |  |  | 29.6 | 0 | 42 | 12.4 | 12.4 | available | 0.96 | 57 | SS 110/6 /6 Yuzhnaya | SS110/6/6Южная | 40+40 | 2.8087 | 2.9257 | 32.5257 |  |  | 32.5257 | 0 | 42 | 9.4743 | 9.4743 | available
58 | SS 110/10/6 Yartsevo | 25+25 | 25 | 25 | 6.39 | 4.55 | 1.84 |  |  | 6.39 | 0 | 26.25 | 19.86 | 19.86 | available | 0.998 | 58 | SS 110/10/6 Yartsevo | SS110/10/6Ярцево | 25+25 | 0.8495 | 0.8512 | 7.2412 |  |  | 7.2412 | 0 | 26.25 | 19.0088 | 19.0088 | available
59 | ПС 110/6/6 Kotorosl | 25+25 | 25 | 25 | 6.89 | 2.73 | 4.16 |  |  | 6.89 | 0 | 26.25 | 19.36 | 19.36 | available | 0.98 | 59 | ПС 110/6/6 Kotorosl | SS110/6/6Которосль | 25+25 | 0.22633 | 0.23095 | 7.1209 |  |  | 7.1209 | 0 | 26.25 | 19.1291 | 19.1291 | available
60 | SS 35/6 Kelnot | 4,0 | 4 |  | 0.16 | 0.16 |  | 0 | 1 day and night | 0.16 | 0 | 0 | -0.16 | -0.16 | unavailable | 0.89 | 60 | SS 35/6 Kelnot | SS35/6Келноть | 4,0 | 0 | 0 | 0.16 | 0 | 1 day and night | 0.16 | 0 | 0 | -0.16 | -0.16 | unavailable
61 | SS 35/10 Ceramic | 10+10 | 10 | 10 | 6.19 | 2.77 | 3.42 |  |  | 6.19 | 0 | 10.5 | 4.31 | 4.31 | available | 0.97 | 61 | SS 35/10 Ceramic | SS35/10Керамик | 10+10 | 0 | 0 | 6.19 |  |  | 6.19 | 0 | 10.5 | 4.31 | 4.31 | available
62 | SS 110/10 Altynovo | 6,3+6,3 | 6.3 | 6.3 | 2.96 | 1.15 | 1.81 |  |  | 2.96 | 0 | 6.62 | 3.66 | 3.66 | available | 0.95 | 62 | SS 110/10 Altynovo | SS110/10Алтыново | 6,3+6,3 | 2.1808 | 2.2956 | 5.2556 |  |  | 5.2556 | 0 | 6.62 | 1.3644 | 1.3644 | available
63 | SS 110/35/10 Borisogleb | 16+10 | 16 | 10 | 7.83 |  |  |  |  | 7.83 | 0 | 10.5 | 2.67 | 2.67 | available | 0.94 | 63 | SS 110/35/10 Borisogleb | SS110/35/10Борисоглеб | 16+10 | 0 | 0 | 14.3466 |  |  | 14.3466 | 0 | 10.5 | -3.8466 | -3.8466 | unavailable
| Nom. capacity MV, МVА | 16+10 |  |  | 3.13 | Т-1: 1.6; Т-2: 1.53; Min 7: 3.13; Min 8: 0; Min 9: 10.5; Min 10: 7.37 |  | Nom. capacity MV, МVА | Ном.МощностьСН,МВА | 16+10 | 0 |  | 6.237 |  |  | 6.237 | 0 | 10.5 | 4.263
| Nom. capacity LV, МVА | 16+10 |  |  | 4.7 | Т-1: 2.45; Т-2: 2.25; Min 7: 4.7; Min 8: 0; Min 9: 10.5; Min 10: 5.8 |  | Nom. capacity LV, МVА | Ном.мощностьНН,МВА | 16+10 | 3.205 | 3.4096 | 8.1096 |  |  | 8.1096 | 0 | 10.5 | 2.3904
64 | SS 110/35/10 Vasilkovo | 10+10 | 10 | 10 | 3.09 |  |  | 0.52 | 120 | 2.57 | 0 | 10.5 | 7.93 | 7.93 | available | 0.95 | 64 | SS 110/35/10 Vasilkovo | SS110/35/10Васильково | 10+10 | 0 |  | 4.6108 | 0.52 | 120 | 4.0908 | 0 | 10.5 | 6.4092 | 6.4092 | available
| Nom. capacity MV, МVА | 10+10 |  |  | 2.14 | Т-1: 0; Т-2: 2.14; Min 7: 2.14; Min 8: 0; Min 9: 10.5; Min 10: 8.36 |  | Nom. capacity MV, МVА | Ном.МощностьСН,МВА | 10+10 | 0 |  | 2.3945 |  |  | 2.3945 | 0 | 10.5 | 8.1055
| Nom. capacity LV, МVА | 10+10 |  |  | 0.95 | 0.28 | 0.67 | 0.52 | 120 | 0.43 | 0 | 10.5 | 10.07 |  |  |  |  | Nom. capacity LV, МVА | Ном.мощностьНН,МВА | 10+10 | 1.203 | 1.2663 | 2.2163 | 0.52 | 120 | 1.6963 | 0 | 10.5 | 8.8037
65 | SS 110/10 Vakhrushevo | 6,3+6,3 | 6.3 | 6.3 | 0.32 | 0.07 | 0.25 | 0.052 | 120 | 0.268 | 0 | 6.62 | 6.352 | 6.352 | available | 0.96 | 65 | SS 110/10 Vakhrushevo | SS110/10Вахрушево | 6,3+6,3 | 0 | 0 | 0.32 | 0.052 | 120 | 0.268 | 0 | 6.62 | 6.352 | 6.352 | available
66 | SS 110/6 Gavrilov Yam | 16+16 | 16 | 16 | 13.31 | 5.78 | 7.53 |  |  | 13.31 | 0 | 16.8 | 3.49 | 3.49 | available | 0.81 | 66 | SS 110/6 Gavrilov Yam | SS110/6ГавриловЯм | 16+16 | 0 | 0 | 13.31 |  |  | 13.31 | 0 | 16.8 | 3.49 | 3.49 | available
67 | SS 110/6 Kinoplyonka | 6,3+10 | 6.3 | 10 | 10.47 | 4.84 | 5.63 |  |  | 10.47 | 0 | 6.62 | -3.85 | -3.85 | unavailable | 0.94 | 67 | SS 110/6 Kinoplyonka | SS110/6Kinoplenka | 6,3+10 | 2.854 | 3.0362 | 13.5062 |  |  | 13.5062 | 0 | 6.62 | -6.8862 | -6.8862 | unavailable
68 | SS 110/35/10 Klimatino | 6,3+6,3 | 6.3 | 6.3 | 1.23 |  |  |  |  | 1.23 | 0 | 6.62 | 5.39 | 5.39 | available | 0.98 | 68 | SS 110/35/10 Klimatino | SS110/35/10Климатино | 6,3+6,3 | 0 |  | 1.3504 |  |  | 1.3504 | 0 | 6.62 | 5.2696 | 5.2696 | available
| Nom. capacity MV, МVА | 0+6,3 |  |  | 0.24 | Т-2: 0.24; Min 7: 0.24; Min 8: 0; Min 9: 6.62; Min 10: 6.38 |  | Nom. capacity MV, МVА | Ном.МощностьСН,МВА | 0+6,3 | 0 |  | 0.32777 |  |  | 0.32777 | 0 | 6.62 | 6.2922
| Nom. capacity LV, МVА | 6,3+6,3 |  |  | 0.99 | Т-1: 0; Т-2: 0.99; Min 7: 0.99; Min 8: 0; Min 9: 6.62; Min 10: 5.63 |  | Nom. capacity LV, МVА | Ном.мощностьНН,МВА | 6,3+6,3 | 0.032 | 0.032653 | 1.0227 |  |  | 1.0227 | 0 | 6.62 | 5.5973
69 | SS 110/35/10 Nila | 6,3+6,3 | 6.3 | 6.3 | 8.12 |  |  | 0.52 | 120 | 7.6 | 0 | 6.62 | -0.98 | -0.98 | unavailable | 0.95 | 69 | SS 110/35/10 Nila | SS110/35/10Нила | 6,3+6,3 | 0 |  | 26.5802 | 0.52 | 120 | 26.0602 | 0 | 6.62 | -19.4402 | -19.4402 | unavailable
| Nom. capacity MV, МVА | 6,3+6,3 |  |  | 6.01 | Т-1: 3.06; Т-2: 2.95; Min 7: 6.01; Min 8: 0; Min 9: 6.62; Min 10: 0.61 |  | Nom. capacity MV, МVА | Ном.МощностьСН,МВА | 6,3+6,3 | 0 |  | 11.6002 |  |  | 11.6002 | 0 | 6.62 | -4.9802
| Nom. capacity LV, МVА | 6,3+6,3 |  |  | 2.11 | 1.08 | 1.03 | 0.52 | 120 | 1.59 | 0 | 6.62 | 5.03 |  |  |  |  | Nom. capacity LV, МVА | Ном.мощностьНН,МВА | 6,3+6,3 | 12.2265 | 12.87 | 14.98 | 0.52 | 120 | 14.46 | 0 | 6.62 | -7.84
70 | SS 110/35/6 Pereslavl | 25+25 | 25 | 25 | 23.82 |  |  |  |  | 23.82 | 0 | 26.25 | 2.43 | 2.43 | available | 0.94 | 70 | SS 110/35/6 Pereslavl | SS110/35/6Переславль | 25+25 | 0 |  | 37.2525 |  |  | 37.2525 | 0 | 26.25 | -11.0025 | -11.0025 | unavailable
| Nom. capacity MV, МVА | 25+25 |  |  | 10.23 | Т-1: 3.58; Т-2: 6.65; Min 7: 10.23; Min 8: 0; Min 9: 26.25; Min 10: 16.02 |  | Nom. capacity MV, МVА | Ном.МощностьСН,МВА | 25+25 | 0 |  | 22.9114 |  |  | 22.9114 | 0 | 26.25 | 3.3386
| Nom. capacity LV, МVА | 25+25 |  |  | 13.59 | Т-1: 5.97; Т-2: 7.62; Min 7: 13.59; Min 8: 0; Min 9: 26.25; Min 10: 12.66 |  | Nom. capacity LV, МVА | Ном.мощностьНН,МВА | 25+25 | 0.706 | 0.75106 | 14.3411 |  |  | 14.3411 | 0 | 26.25 | 11.9089
71 | SS 110/10 Ploski | 2,5+2,5 | 2.5 | 2.5 | 1.68 | 1.01 | 0.67 |  |  | 1.68 | 0 | 2.63 | 0.95 | 0.95 | available | 0.97 | 71 | SS 110/10 Ploski | SS110/10Плоски | 2,5+2,5 | 0.4595 | 0.47371 | 2.1537 |  |  | 2.1537 | 0 | 2.63 | 0.47629 | 0.47629 | available
72 | SS 110/35/10 Rostov | 20+25 | 20 | 25 | 20.85 |  |  |  |  | 20.85 | 0 | 21 | 0.15 | 0.15 | available | 0.95 | 72 | SS 110/35/10 Rostov | SS110/35/10Ростов | 20+25 | 0 |  | 24.7454 |  |  | 24.7454 | 0 | 21 | -3.7454 | -3.7454 | unavailable
| Nom. capacity MV, МVА | 20+25 |  |  | 1.67 | Т-1: 0; Т-2: 1.67; Min 7: 1.67; Min 8: 0; Min 9: 21; Min 10: 19.33 |  | Nom. capacity MV, МVА | Ном.МощностьСН,МВА | 20+25 | 0 |  | 2.1475 |  |  | 2.1475 | 0 | 21 | 18.8525
| Nom. Capacity LV, МVА | 20+25 |  |  | 19.18 | Т-1: 9.95; Т-2: 9.23; Min 7: 19.18; Min 8: 0; Min 9: 21; Min 10: 1.82 |  | Nom. Capacity LV, МVА | Ном.мощностьНН,МВА | 20+25 | 3.247 | 3.4179 | 22.5979 |  |  | 22.5979 | 0 | 21 | -1.5979
73 | SS 110/35/10 Technical school | 6,3+6,3 | 6.3 | 6.3 | 7.66 |  |  |  |  | 7.66 | 0 | 6.62 | -1.04 | -1.04 | unavailable | 0.94 | 73 | SS 110/35/10 Technical school | SS110/35/10Техникум | 6,3+6,3 | 0 |  | 14.0476 |  |  | 14.0476 | 0 | 6.62 | -7.4276 | -7.4276 | unavailable
| Nom. capacity MV, МVА | 6,3+6,3 |  |  | 4.45 | Т-1: 4.45; Т-2: 0; Min 7: 4.45; Min 8: 0; Min 9: 6.62; Min 10: 2.17 |  | Nom. capacity MV, МVА | Ном.МощностьСН,МВА | 6,3+6,3 | 0 |  | 8.2365 |  |  | 8.2365 | 0 | 6.62 | -1.6165
| Nom. capacity LV, МVА | 6,3+6,3 |  |  | 3.21 | Т-1: 1.68; Т-2: 1.53; Min 7: 3.21; Min 8: 0; Min 9: 6.62; Min 10: 3.41 |  | Nom. capacity LV, МVА | Ном.мощностьНН,МВА | 6,3+6,3 | 2.445 | 2.6011 | 5.8111 |  |  | 5.8111 | 0 | 6.62 | 0.80894
74 | SS 110/35/10 Uglich | 25+25 | 25 | 25 | 22.29 |  |  |  |  | 22.29 | 0 | 26.25 | 3.96 | 3.96 | available | 0.93 | 74 | SS 110/35/10 Uglich | SS110/35/10Углич | 25+25 | 0 |  | 36.2771 |  |  | 36.2771 | 0 | 26.25 | -10.0271 | -10.0271 | unavailable
| Nom. capacidty MV, МVА | 25+25 |  |  | 18.04 | Т-1: 6.47; Т-2: 11.57; Min 7: 18.04; Min 8: 0; Min 9: 26.25; Min 10: 8.21 |  | Nom. capacidty MV, МVА | Ном.МощностьСН,МВА | 25+25 | 0 |  | 27.4566 |  |  | 27.4566 | 0 | 26.25 | -1.2066
| Nom. capacity LV, МVА | 25+25 |  |  | 4.25 | Т-1: 2.34; Т-2: 1.91; Min 7: 4.25; Min 8: 0; Min 9: 26.25; Min 10: 22 |  | Nom. capacity LV, МVА | Ном.мощностьНН,МВА | 25+25 | 4.2505 | 4.5704 | 8.8204 |  |  | 8.8204 | 0 | 26.25 | 17.4296
75 | SS 110/10 Ustye | 10+10 | 10 | 10 | 3.87 | 2.23 | 1.64 | 0.727 | 120 | 3.143 | 0 | 10.5 | 7.357 | 7.357 | available | 0.9 | 75 | SS 110/10 Ustye | SS110/10Устье | 10+10 | 0.9369 | 1.041 | 4.911 | 0.727 | 120 | 4.184 | 0 | 10.5 | 6.316 | 6.316 | available
76 | SS 110/10 Shurskol | 10+10 | 10 | 10 | 2.16 | 1.17 | 0.99 | 0.953 | 120 | 1.207 | 0 | 10.5 | 9.293 | 9.293 | available | 0.93 | 76 | SS 110/10 Shurskol | SS110/10Шурскол | 10+10 | 0.089 | 0.095699 | 2.2557 | 0.953 | 120 | 1.3027 | 0 | 10.5 | 9.1973 | 9.1973 | available
77 | SS 110/10 Yur.Sloboda | 10+10 | 10 | 10 | 6.84 | 3.72 | 3.12 | 0.935 | 120 | 5.905 | 0 | 10.5 | 4.595 | 4.595 | available | 0.89 | 77 | SS 110/10 Yur.Sloboda | SS110/10Юр.Слобода | 10+10 | 1.7562 | 1.9733 | 8.8133 | 0.935 | 120 | 7.8783 | 0 | 10.5 | 2.6217 | 2.6217 | available
78 | SS 35/10 Aleshkino | 2,5+2,5 | 2.5 | 2.5 | 0.69 | 0.09 | 0.6 |  |  | 0.69 | 0 | 2.63 | 1.94 | 1.94 | available | 0.99 | 78 | SS 35/10 Aleshkino | SS35/10Алешкино | 2,5+2,5 | 0.023 | 0.023232 | 0.71323 |  |  | 0.71323 | 0 | 2.63 | 1.9168 | 1.9168 | available
79 | SS 35/6 Batki | 1,6+1,6 | 1.6 | 1.6 | 1.03 | 1.03 | 0 |  |  | 1.03 | 0 | 1.68 | 0.65 | 0.65 | available | 0.98 | 79 | SS 35/6 Batki | SS35/6Батьки | 1,6+1,6 | 0.797 | 0.81327 | 1.8433 |  |  | 1.8433 | 0 | 1.68 | -0.16327 | -0.16327 | unavailable
80 | SS 35/10 Beregovaya | 1,6 | 1.6 |  | 0.19 | 0.19 |  | 3.031 | 1 day and night | 0.19 | 0 | 3.031 | 2.841 | 2.841 | available | 0.95 | 80 | SS 35/10 Beregovaya | SS35/10Береговая | 1,6 | 0.057 | 0.06 | 0.25 | 3.031 | 1 day and night | 0.25 | 0 | 3.031 | 2.781 | 2.781 | available
81 | SS 35/10 Berendeevo | 2,5+2,5 | 2.5 | 2.5 | 1.35 | 1.12 | 0.23 | 0.242 |  | 1.108 | 0 | 2.63 | 1.522 | 1.522 | available | 0.96 | 81 | SS 35/10 Berendeevo | SS35/10Берендеево | 2,5+2,5 | 0.122 | 0.12708 | 1.4771 | 0.242 |  | 1.2351 | 0 | 2.63 | 1.3949 | 1.3949 | available
82 | SS 35/10 Vorzha | 1,8+1,6 | 1.8 | 1.6 | 0.48 | 0.24 | 0.24 | 0.329 | 120 | 0.151 | 0 | 1.68 | 1.529 | 1.529 | available | 0.997 | 82 | SS 35/10 Vorzha | SS35/10Воржа | 1,8+1,6 | 0.03 | 0.03009 | 0.51009 | 0.329 | 120 | 0.18109 | 0 | 1.68 | 1.4989 | 1.4989 | available
83 | SS 35/10 Voshchazhnikovo | 1,6+2,5 | 1.6 | 2.5 | 0.8 | 0.48 | 0.32 | 0.52 | 120 | 0.28 | 0 | 1.68 | 1.4 | 1.4 | available | 0.84 | 83 | SS 35/10 Voshchazhnikovo | SS35/10Вощажниково | 1,6+2,5 | 0.928 | 1.1048 | 1.9048 | 0.52 | 120 | 1.3848 | 0 | 1.68 | 0.29524 | 0.29524 | available
84 | SS 35/10 Glebovo | 2,5+2,5 | 2.5 | 2.5 | 2.44 | 0.3 | 2.14 |  |  | 2.44 | 0 | 2.63 | 0.19 | 0.19 | available | 0.96 | 84 | SS 35/10 Glebovo | SS35/10Глебово | 2,5+2,5 | 3.2331 | 3.3678 | 5.8078 |  |  | 5.8078 | 0 | 2.63 | -3.1778 | -3.1778 | unavailable
85 | SS 35/10 Gorki | 2,5+2,5 | 2.5 | 2.5 | 1.05 | 0.57 | 0.48 |  |  | 1.05 | 0 | 2.63 | 1.58 | 1.58 | available | 0.91 | 85 | SS 35/10 Gorki | SS35/10Горки | 2,5+2,5 | 0.268 | 0.29451 | 1.3445 |  |  | 1.3445 | 0 | 2.63 | 1.2855 | 1.2855 | available
86 | SS 35/10 Dmitrianovo | 1,6+1,6 | 1.6 | 1.6 | 1.19 | 0.73 | 0.46 |  |  | 1.19 | 0 | 1.68 | 0.49 | 0.49 | available | 0.98 | 86 | SS 35/10 Dmitrianovo | SS35/10Дмитрианово | 1,6+1,6 | 0.072 | 0.073469 | 1.2635 |  |  | 1.2635 | 0 | 1.68 | 0.41653 | 0.41653 | available
87 | SS 35/10 Zaozerye | 2,5+1,6 | 2.5 | 1.6 | 1.16 | 0.47 | 0.69 |  |  | 1.16 | 0 | 1.68 | 0.52 | 0.52 | available | 0.95 | 87 | SS 35/10 Zaozerye | SS35/10Заозерье | 2,5+1,6 | 0.196 | 0.20632 | 1.3663 |  |  | 1.3663 | 0 | 1.68 | 0.31368 | 0.31368 | available
88 | SS 35/10 Ilyinskoe | 2,5+2,5 | 2.5 | 2.5 | 1.38 | 0.95 | 0.43 |  |  | 1.38 | 0 | 2.63 | 1.25 | 1.25 | available | 0.94 | 88 | SS 35/10 Ilyinskoe | SS35/10Ильинское | 2,5+2,5 | 0.1795 | 0.19096 | 1.571 |  |  | 1.571 | 0 | 2.63 | 1.059 | 1.059 | available
89 | SS 35/10 Kibernetik | 6,3+6,3 | 6.3 | 6.3 | 2.03 | 0.68 | 1.35 |  |  | 2.03 | 0 | 6.62 | 4.59 | 4.59 | available | 0.96 | 89 | SS 35/10 Kibernetik | SS35/10Кибернетик | 6,3+6,3 | 1.245 | 1.2969 | 3.3269 |  |  | 3.3269 | 0 | 6.62 | 3.2931 | 3.2931 | available
90 | SS 35/10 Klementyevo | 1,6 | 1.6 |  | 0.34 | 0.34 |  | 0.588 | 1 day and night | 0.34 | 0 | 0.588 | 0.248 | 0.248 | available | 0.94 | 90 | SS 35/10 Klementyevo | SS35/10Клементьево | 1,6 | 0 | 0 | 0.34 | 0.588 | 1 day and night | 0.34 | 0 | 0.588 | 0.248 | 0.248 | available
91 | SS 35/10 Krasnoe | 4,0+4,0 | 4 | 4 | 2.28 | 0.66 | 1.62 | 0.866 | 120 | 1.414 | 0 | 4.2 | 2.786 | 2.786 | available | 0.97 | 91 | SS 35/10 Krasnoe | SS35/10Красное | 4,0+4,0 | 3.411 | 3.5165 | 5.7965 | 0.866 | 120 | 4.9305 | 0 | 4.2 | -0.73049 | -0.73049 | unavailable
92 | SS 35/10 Kulakovo | 2,5+2,5 | 2.5 | 2.5 | 1.63 | 1.23 | 0.4 |  |  | 1.63 | 0 | 2.63 | 1 | 1 | available | 0.78 | 92 | SS 35/10 Kulakovo | SS35/10Кулаково | 2,5+2,5 | 1.0348 | 1.3267 | 2.9567 |  |  | 2.9567 | 0 | 2.63 | -0.32667 | -0.32667 | unavailable
93 | SS 35/6 Kupan | 2,5+2,5 | 2.5 | 2.5 | 2.29 | 1.45 | 0.84 |  |  | 2.29 | 0 | 2.63 | 0.34 | 0.34 | available | 0.99 | 93 | SS 35/6 Kupan | SS35/6Купань | 2,5+2,5 | 1.2456 | 1.2582 | 3.5482 |  |  | 3.5482 | 0 | 2.63 | -0.91818 | -0.91818 | unavailable
94 | SS 35/10 Markovo | 2,5+2,5 | 2.5 | 2.5 | 0.98 | 0.57 | 0.41 | 0.537 | 120 | 0.443 | 0 | 2.63 | 2.187 | 2.187 | available | 0.96 | 94 | SS 35/10 Markovo | SS35/10Марково | 2,5+2,5 | 0.245 | 0.25521 | 1.2352 | 0.537 | 120 | 0.69821 | 0 | 2.63 | 1.9318 | 1.9318 | available
95 | SS 35/10 Nagorye | 4,0+4,0 | 4 | 4 | 2.94 | 1.33 | 1.61 |  |  | 2.94 | 0 | 4.2 | 1.26 | 1.26 | available | 0.92 | 95 | SS 35/10 Nagorye | SS35/10Нагорье | 4,0+4,0 | 2.649 | 2.8793 | 5.8193 |  |  | 5.8193 | 0 | 4.2 | -1.6193 | -1.6193 | unavailable
96 | SS 35/10 Porechye | 4,0+4,0 | 4 | 4 | 1.79 | 1.14 | 0.65 | 0.07 | 120 | 1.72 | 0 | 4.2 | 2.48 | 2.48 | available | 0.94 | 96 | SS 35/10 Porechye | SS35/10Поречье | 4,0+4,0 | 0.309 | 0.32872 | 2.1187 | 0.07 | 120 | 2.0487 | 0 | 4.2 | 2.1513 | 2.1513 | available
97 | SS 35/10 Pruzhinino | 2,5+2,5 | 2.5 | 2.5 | 0.98 | 0.74 | 0.24 |  |  | 0.98 | 0 | 2.63 | 1.65 | 1.65 | available | 0.98 | 97 | SS 35/10 Pruzhinino | SS35/10Пружинино | 2,5+2,5 | 0.36 | 0.36735 | 1.3473 |  |  | 1.3473 | 0 | 2.63 | 1.2827 | 1.2827 | available
98 | SS 35/10 Ramenye | 2,5+2,5 | 2.5 | 2.5 | 0.35 | 0.29 | 0.06 | 0.02 | 120 | 0.33 | 0 | 2.63 | 2.3 | 2.3 | available | 0.81 | 98 | SS 35/10 Ramenye | SS35/10Раменье | 2,5+2,5 | 0.131 | 0.16173 | 0.51173 | 0.02 | 120 | 0.49173 | 0 | 2.63 | 2.1383 | 2.1383 | available
99 | SS 35/10 Ryazantsevo | 2,5+2,5 | 2.5 | 2.5 | 1.36 | 0.91 | 0.45 |  |  | 1.36 | 0 | 2.63 | 1.27 | 1.27 | available | 0.95 | 99 | SS 35/10 Ryazantsevo | SS35/10Рязанцево | 2,5+2,5 | 0.169 | 0.17789 | 1.5379 |  |  | 1.5379 | 0 | 2.63 | 1.0921 | 1.0921 | available
100 | SS 35/10 Saraevo | 1+1,6 | 1 | 1.6 | 1.35 | 0.37 | 0.98 |  |  | 1.35 | 0 | 1.05 | -0.3 | -0.3 | unavailable | 0.98 | 100 | SS 35/10 Saraevo | SS35/10Сараево | 1+1,6 | 0.859 | 0.87653 | 2.2265 |  |  | 2.2265 | 0 | 1.05 | -1.1765 | -1.1765 | unavailable
101 | SS 35/10 Selifontovo | 2,5+2,5 | 2.5 | 2.5 | 1.08 | 0.3 | 0.78 | 0.693 | 120 | 0.387 | 0 | 2.63 | 2.243 | 2.243 | available | 0.96 | 101 | SS 35/10 Selifontovo | SS35/10Селифонтово | 2,5+2,5 | 1.736 | 1.8083 | 2.8883 | 0.693 | 120 | 2.1953 | 0 | 2.63 | 0.43467 | 0.43467 | available
102 | SS 35/10 Semibratovo | 4,0+4,0 | 4 | 4 | 1.12 | 0.32 | 0.8 | 0.07 | 120 | 1.05 | 0 | 4.2 | 3.15 | 3.15 | available | 0.96 | 102 | SS 35/10 Semibratovo | SS35/10Семибратово | 4,0+4,0 | 0.318 | 0.33125 | 1.4513 | 0.07 | 120 | 1.3813 | 0 | 4.2 | 2.8187 | 2.8187 | available
103 | SS 35/10 Skomorokhovo | 1,6+1,6 | 1.6 | 1.6 | 1.11 | 0.03 | 1.08 |  |  | 1.11 | 0 | 1.68 | 0.57 | 0.57 | available | 0.96 | 103 | SS 35/10 Skomorokhovo | SS35/10Скоморохово | 1,6+1,6 | 3.5346 | 3.6819 | 4.7919 |  |  | 4.7919 | 0 | 1.68 | -3.1119 | -3.1119 | unavailable
104 | SS 35/10 Solomidino | 2.5 | 2.5 |  | 1.16 | 1.16 |  | 0.918 | 1 day and night | 1.16 | 0 | 0.918 | -0.242 | -0.242 | unavailable | 0.93 | 104 | SS 35/10 Solomidino | SS35/10Соломидино | 2.5 | 2.09 | 2.2473 | 3.4073 | 0.918 | 1 day and night | 3.4073 | 0 | 0.918 | -2.4893 | -2.4893 | unavailable
105 | SS 35/10 Stavotino | 4,0+4,0 | 4 | 4 | 1.69 | 0.61 | 1.08 | 0.277 | 120 | 1.413 | 0 | 4.2 | 2.787 | 2.787 | available | 0.82 | 105 | SS 35/10 Stavotino | SS35/10Ставотино | 4,0+4,0 | 1.2645 | 1.5421 | 3.2321 | 0.277 | 120 | 2.9551 | 0 | 4.2 | 1.2449 | 1.2449 | available
106 | SS 35/10 Urusovo | 2,5+2,5 | 2.5 | 2.5 | 0.28 | 0.25 | 0.03 | 0.02 | 120 | 0.26 | 0 | 2.63 | 2.37 | 2.37 | available | 0.97 | 106 | SS 35/10 Urusovo | SS35/10Урусово | 2,5+2,5 | 0.055 | 0.056701 | 0.3367 | 0.02 | 120 | 0.3167 | 0 | 2.63 | 2.3133 | 2.3133 | available
107 | SS 35/10 Filimonovo | 2,5+2,5 | 2.5 | 2.5 | 1.63 | 0.34 | 1.29 |  |  | 1.63 | 0 | 2.63 | 1 | 1 | available | 0.93 | 107 | SS 35/10 Filimonovo | SS35/10Филимоново | 2,5+2,5 | 1.792 | 1.9269 | 3.5569 |  |  | 3.5569 | 0 | 2.63 | -0.92688 | -0.92688 | unavailable
108 | SS 35/10 Choporovo | 2,5+2,5 | 2.5 | 2.5 | 0.28 | 0.09 | 0.19 |  |  | 0.28 | 0 | 2.63 | 2.35 | 2.35 | available | 0.89 | 108 | SS 35/10 Choporovo | SS35/10Чопорово | 2,5+2,5 | 0.164 | 0.18427 | 0.46427 |  |  | 0.46427 | 0 | 2.63 | 2.1657 | 2.1657 | available
109 | SS 35/10 Shchurovo | 2,5+2,5 | 2.5 | 2.5 | 0.99 | 0.48 | 0.51 | 0.277 | 120 | 0.713 | 0 | 2.63 | 1.917 | 1.917 | available | 0.73 | 109 | SS 35/10 Shchurovo | SS35/10Щурово | 2,5+2,5 | 0.074 | 0.10137 | 1.0914 | 0.277 | 120 | 0.81437 | 0 | 2.63 | 1.8156 | 1.8156 | available
110 | SS 35/10 Neksans | 10+10 | 10 | 10 | 1.9 | 0.87 | 1.03 |  |  | 1.9 | 0 | 10.5 | 8.6 | 8.6 | available | 0.8 | 110 | SS 35/10 Neksans | SS35/10Нексанс | 10+10 | 6.5 | 8.125 | 10.025 |  |  | 10.025 | 0 | 10.5 | 0.475 | 0.475 | available
111 | SS 35/6 Pribrezhnaya | 10+10 | 10 | 10 | 10.67 | 5.99 | 4.68 |  |  | 10.67 | 0 | 10.5 | -0.17 | -0.17 | unavailable | 0.92 | 111 | SS 35/6 Pribrezhnaya | SS35/6Прибрежная | 10+10 | 0.8228 | 0.89435 | 11.5643 |  |  | 11.5643 | 0 | 10.5 | -1.0643 | -1.0643 | unavailable
112 | SS 110/10 Tishino | 25+25 | 25 | 25 | 20.15 | 12.46 | 7.69 |  |  | 20.15 | 0 | 26.25 | 6.1 | 6.1 | available | 0.99 | 112 | SS 110/10 Tishino | SS110/10Тишино | 25+25 | 0.0938 | 0.094747 | 20.2447 |  |  | 20.2447 | 0 | 26.25 | 6.0053 | 6.0053
113 | SS 110/10 Product pipeline | 6,3+6,3 | 6.3 | 6.3 | 1.6 | 0.12 | 1.48 |  |  | 1.6 | 0 | 6.62 | 5.02 | 5.02 | available | 0.99 | 113 | SS 110/10 Product pipeline | SS110/10Продуктопровод | 6,3+6,3 | 0 | 0 | 1.6 |  |  | 1.6 | 0 | 6.62 | 5.02 | 5.02 | available
114 | SS 110/10 Nekouz | 6,3+6,3 | 6.3 | 6.3 | 2.16 | 0.73 | 1.43 | 0.052 | 120 | 2.108 | 0 | 6.62 | 4.512 | 4.512 | available | 0.92 | 114 | SS 110/10 Nekouz | SS110/10Некоуз | 6,3+6,3 | 0.022 | 0.023913 | 2.1839 | 0.052 | 120 | 2.1319 | 0 | 6.62 | 4.4881 | 4.4881 | available
115 | SS 110/6 Yuzhnaya | 25+25 | 25 | 25 | 16.94 | 8.43 | 8.51 |  |  | 16.94 | 0 | 26.25 | 9.31 | 9.31 | available | 0.94 | 115 | SS 110/6 Yuzhnaya | SS110/6Южная | 25+25 | 0.09926 | 0.1056 | 17.0456 |  |  | 17.0456 | 0 | 26.25 | 9.2044 | 9.2044 | available
116 | SS 110/10 Optika | 10+10 | 10 | 10 | 5.69 | 3.16 | 2.53 | 0.52 | 120 | 5.17 | 0 | 10.5 | 5.33 | 5.33 | available | 0.95 | 116 | SS 110/10 Optika | SS110/10Оптика | 10+10 | 0.448 | 0.47158 | 6.1616 | 0.52 | 120 | 5.6416 | 0 | 10.5 | 4.8584 | 4.8584 | available
117 | SS 110/6 Poligrafmash | 16+16 | 16 | 16 | 10.43 | 5.78 | 4.65 |  |  | 10.43 | 0 | 16.8 | 6.37 | 6.37 | available | 0.95 | 117 | SS 110/6 Poligrafmash | SS110/6Полиграфмаш | 16+16 | 0 | 0 | 10.43 |  |  | 10.43 | 0 | 16.8 | 6.37 | 6.37 | available
118 | SS 110/6/6 Zapadnaya | 63+63 | 63 | 63 | 34.46 | 17.83 | 16.63 |  |  | 34.46 | 0 | 66.15 | 31.69 | 31.69 | available | 0.87 | 118 | SS 110/6/6 Zapadnaya | SS110/6/6Западная | 63+63 | 0.3609 | 0.41483 | 34.8748 |  |  | 34.8748 | 0 | 66.15 | 31.2752 | 31.2752 | available
119 | SS 110/35/6 Volzhskaya | 40+40 | 40 | 40 | 15.13 |  |  |  |  | 15.13 | 0 | 42 | 26.87 | 26.87 | available | 0.84 | 119 | SS 110/35/6 Volzhskaya | SS110/35/6Волжская | 40+40 | 0 | 0 | 15.2919 |  |  | 15.2919 | 0 | 42 | 26.7081 | 26.7081 | available
| Nom. capacity MV, МVА | 40+40 |  |  | 0 | Т-1: 0; Т-2: 0; Min 8: 0 |  | Nom. capacity MV, МVА | Ном.МощностьСН,МВА | 40+40 | 0 | [5 empty] | 0
| Nom. capacity LV, МVА | 40+40 |  |  | 15.13 | Т-1: 6.49; Т-2: 8.64; Min 7: 15.13; Min 8: 0; Min 9: 42; Min 10: 26.87 |  | Nom. capacity LV, МVА | Ном.мощностьНН,МВА | 40+40 | 0.136 | 0.1619 | 15.2919 |  |  | 15.2919 | 0 | 42 | 26.7081
120 | SS 110/35/6 Levoberezhnaya | 16+16 | 16 | 16 | 14.04 |  |  |  |  | 14.04 | 0 | 16.8 | 2.76 | 2.76 | available | 0.96 | 120 | SS 110/35/6 Levoberezhnaya | SS110/35/6Левобережная | 16+16 | 0 |  | 15.9545 |  |  | 15.9545 | 0 | 16.8 | 0.84553 | 0.84553 | available
| Nom. capacity MV, МVА | 16+16 |  |  | 8.62 | Т-1: 3.92; Т-2: 4.7; Min 7: 8.62; Min 8: 0; Min 9: 16.8; Min 10: 8.18 |  | Nom. capacity MV, МVА | Ном.МощностьСН,МВА | 16+16 | 0 |  | 10.4918 |  |  | 10.4918 | 0 | 16.8 | 6.3082
| Nom. capacity LV, МVА | 16+16 |  |  | 5.42 | Т-1: 2.28; Т-2: 3.14; Min 7: 5.42; Min 8: 0; Min 9: 16.8; Min 10: 11.38 |  | Nom. capacity LV, МVА | Ном.мощностьНН,МВА | 16+16 | 0.041 | 0.042708 | 5.4627 |  |  | 5.4627 | 0 | 16.8 | 11.3373
121 | SS 110/35/10 Pishchalkino | 7,5+7,5 | 7.5 | 7.5 | 1.7 |  |  |  |  | 1.7 | 0 | 7.88 | 6.18 | 6.18 | available | 0.93 | 121 | SS 110/35/10 Pishchalkino | SS110/35/10Пищалкино | 7,5+7,5 | 0 |  | 1.7 |  |  | 1.7 | 0 | 7.88 | 6.18 | 6.18 | available
| Nom. capacity MV, МVА | 7,5+7,5 |  |  | 0.95 | Т-1: 0.95; Т-2: 0; Min 7: 0.95; Min 8: 0; Min 9: 7.88; Min 10: 6.93 |  | Nom. capacity MV, МVА | Ном.МощностьСН,МВА | 7,5+7,5 | 0 |  | 0.95 |  |  | 0.95 | 0 | 7.88 | 6.93
| Nom. capacity LV, МVА | 7,5+7,5 |  |  | 0.75 | Т-1: 0.62; Т-2: 0.13; Min 7: 0.75; Min 8: 0; Min 9: 7.88; Min 10: 7.13 |  | Nom. capacity LV, МVА | Ном.мощностьНН,МВА | 7,5+7,5 | 0 | 0 | 0.75 |  |  | 0.75 | 0 | 7.88 | 7.13
122 | SS 110/6 Dock yard | 10+10 | 10 | 10 | 5.5 | 2.8 | 2.7 |  |  | 5.5 | 0 | 10.5 | 5 | 5 | available | 0.93 | 122 | SS 110/6 Dock yard | SS110/6Судоверфь | 10+10 | 0.174 | 0.1871 | 5.6871 |  |  | 5.6871 | 0 | 10.5 | 4.8129 | 4.8129 | available
123 | SS 110/6 Selekhovo | 6,3+6,3 | 6.3 | 6.3 | 3.62 | 2.97 | 0.65 |  |  | 3.62 | 0 | 6.62 | 3 | 3 | available | 0.96 | 123 | SS 110/6 Selekhovo | SS110/6Селехово | 6,3+6,3 | 0.754 | 0.78542 | 4.4054 |  |  | 4.4054 | 0 | 6.62 | 2.2146 | 2.2146 | available
124 | SS 35/6 Kamenniki | 4,0+4,0 | 4 | 4 | 2.29 | 1.32 | 0.97 |  |  | 2.29 | 0 | 4.2 | 1.91 | 1.91 | available | 0.91 | 124 | SS 35/6 Kamenniki | SS35/6Каменники | 4,0+4,0 | 0.149 | 0.16374 | 2.4537 |  |  | 2.4537 | 0 | 4.2 | 1.7463 | 1.7463 | available
125 | SS 35/10 Shashkovo | 1,6+1,6 | 1.6 | 1.6 | 0.6 | 0.44 | 0.16 |  |  | 0.6 | 0 | 1.68 | 1.08 | 1.08 | available | 0.94 | 125 | SS 35/10 Shashkovo | SS35/10Шашково | 1,6+1,6 | 0.291 | 0.30957 | 0.90957 |  |  | 0.90957 | 0 | 1.68 | 0.77043 | 0.77043 | available
126 | SS 110/6 Veretye | 25+25 | 25 | 25 | 17.82 | 9.16 | 8.66 |  |  | 17.82 | 0 | 26.25 | 8.43 | 8.43 | available | 0.92 | 126 | SS 110/6 Veretye | SS110/6Веретье | 25+25 | 0.4615 | 0.50163 | 18.3216 |  |  | 18.3216 | 0 | 26.25 | 7.9284 | 7.9284 | available
127 | SS 35/10 Nikolo-Korma | 4,0+4,0 | 4 | 4 | 2.29 | 1.5 | 0.79 | 0.52 | 120 | 1.77 | 0 | 4.2 | 2.43 | 2.43 | available | 0.96 | 127 | SS 35/10 Nikolo-Korma | SS35/10Николо-Корма | 4,0+4,0 | 2.1998 | 2.2915 | 4.5815 | 0.52 | 120 | 4.0615 | 0 | 4.2 | 0.13854 | 0.13854 | available
128 | SS 35/10 Arefino | 2,5+2,5 | 2.5 | 2.5 | 1.26 | 0.7 | 0.56 | 0.035 | 120 | 1.225 | 0 | 2.63 | 1.405 | 1.405 | available | 0.94 | 128 | SS 35/10 Arefino | SS35/10Арефино | 2,5+2,5 | 0.096 | 0.10213 | 1.3621 | 0.035 | 120 | 1.3271 | 0 | 2.63 | 1.3029 | 1.3029 | available
129 | SS 35/10 Knyazevo | 1,6+2,5 | 1.6 | 2.5 | 0.72 | 0.07 | 0.65 |  |  | 0.72 | 0 | 1.68 | 0.96 | 0.96 | available | 0.92 | 129 | SS 35/10 Knyazevo | SS35/10Князево | 1,6+2,5 | 0.141 | 0.15326 | 0.87326 |  |  | 0.87326 | 0 | 1.68 | 0.80674 | 0.80674 | available
130 | SS 35/10 Pokrov | 1,6+1,6 | 1.6 | 1.6 | 0.55 | 0.31 | 0.24 | 0.242 | 120 | 0.308 | 0 | 1.68 | 1.372 | 1.372 | available | 0.99 | 130 | SS 35/10 Pokrov | SS35/10Покров | 1,6+1,6 | 0.014 | 0.014141 | 0.56414 | 0.242 | 120 | 0.32214 | 0 | 1.68 | 1.3579 | 1.3579 | available
131 | SS 35/10 Anikovo | 2,5+2,5 | 2.5 | 2.5 | 0.85 | 0.61 | 0.24 | 0.017 | 120 | 0.833 | 0 | 2.63 | 1.797 | 1.797 | available | 0.85 | 131 | SS 35/10 Anikovo | SS35/10Аниково | 2,5+2,5 | 0.021 | 0.024706 | 0.87471 | 0.017 | 120 | 0.85771 | 0 | 2.63 | 1.7723 | 1.7723 | available
132 | SS 35/10 Novoe selo | 2,5+2,5 | 2.5 | 2.5 | 0.86 | 0.54 | 0.32 |  |  | 0.86 | 0 | 2.63 | 1.77 | 1.77 | available | 0.91 | 132 | SS 35/10 Novoe selo | SS35/10Новоесело | 2,5+2,5 | 0.508 | 0.55824 | 1.4182 |  |  | 1.4182 | 0 | 2.63 | 1.2118 | 1.2118 | available
133 | SS 35/10 Bolshoe selo | 6,3+6,3 | 6.3 | 6.3 | 5.63 | 3.26 | 2.37 |  |  | 5.63 | 0 | 6.62 | 0.99 | 0.99 | available | 0.95 | 133 | SS 35/10 Bolshoe selo | SS35/10Большоесело | 6,3+6,3 | 0.8835 | 0.93 | 6.56 |  |  | 6.56 | 0 | 6.62 | 0.06 | 0.06 | available
134 | SS 35/10 Breytovo | 6,3+6,3 | 6.3 | 6.3 | 4.34 | 2.01 | 2.33 |  |  | 4.34 | 0 | 6.62 | 2.28 | 2.28 | available | 0.95 | 134 | SS 35/10 Breytovo | SS35/10Брейтово | 6,3+6,3 | 1.108 | 1.1663 | 5.5063 |  |  | 5.5063 | 0 | 6.62 | 1.1137 | 1.1137 | available
135 | SS 35/10 Stanilovo | 1,6+1,6 | 1.6 | 1.6 | 0.68 | 0.16 | 0.52 | 0.208 | 120 | 0.472 | 0 | 1.68 | 1.208 | 1.208 | available | 0.94 | 135 | SS 35/10 Stanilovo | SS35/10Станилово | 1,6+1,6 | 0.113 | 0.12021 | 0.80021 | 0.208 | 120 | 0.59221 | 0 | 1.68 | 1.0878 | 1.0878 | available
136 | SS 35/10 Znamovo | 2,5+2,5 | 2.5 | 2.5 | 1.01 | 0.31 | 0.7 | 0.173 | 120 | 0.837 | 0 | 2.63 | 1.793 | 1.793 | available | 0.92 | 136 | SS 35/10 Znamovo | SS35/10Знамово | 2,5+2,5 | 0.042 | 0.045652 | 1.0557 | 0.173 | 120 | 0.88265 | 0 | 2.63 | 1.7473 | 1.7473 | available
137 | SS 35/10 Rozhdestvenno | 2,5+2,5 | 2.5 | 2.5 | 1.14 | 0.63 | 0.51 |  |  | 1.14 | 0 | 2.63 | 1.49 | 1.49 | available | 0.94 | 137 | SS 35/10 Rozhdestvenno | SS35/10Рождественно | 2,5+2,5 | 0.165 | 0.17553 | 1.3155 |  |  | 1.3155 | 0 | 2.63 | 1.3145 | 1.3145 | available
138 | SS 35/10 Zapolye | 2,5+2,5 | 2.5 | 2.5 | 0.55 | 0.25 | 0.3 |  |  | 0.55 | 0 | 2.63 | 2.08 | 2.08 | available | 0.99 | 138 | SS 35/10 Zapolye | SS35/10Заполье | 2,5+2,5 | 0.161 | 0.16263 | 0.71263 |  |  | 0.71263 | 0 | 2.63 | 1.9174 | 1.9174 | available
139 | SS 35/10 Tikhmenevo | 1,6+1,6 | 1.6 | 1.6 | 1.25 | 0.55 | 0.7 | 0.329 | 120 | 0.921 | 0 | 1.68 | 0.759 | 0.759 | available | 0.93 | 139 | SS 35/10 Tikhmenevo | SS35/10Тихменево | 1,6+1,6 | 0.17 | 0.1828 | 1.4328 | 0.329 | 120 | 1.1038 | 0 | 1.68 | 0.5762 | 0.5762 | available
140 | SS 35/10 Latskoe | 1,6+2,5 | 1.6 | 2.5 | 0.24 | 0.17 | 0.07 | 0.052 | 120 | 0.188 | 0 | 1.68 | 1.492 | 1.492 | available | 0.64 | 140 | SS 35/10 Latskoe | SS35/10Лацкое | 1,6+2,5 | 0.007 | 0.010937 | 0.25094 | 0.052 | 120 | 0.19894 | 0 | 1.68 | 1.4811 | 1.4811 | available
141 | SS 35/10 Borok | 2,5+4,0 | 2.5 | 4 | 1.21 | 0.81 | 0.4 | 0.156 | 120 | 1.054 | 0 | 2.63 | 1.576 | 1.576 | available | 0.93 | 141 | SS 35/10 Borok | SS35/10Борок | 2,5+4,0 | 0.274 | 0.29462 | 1.5046 | 0.156 | 120 | 1.3486 | 0 | 2.63 | 1.2814 | 1.2814 | available
142 | SS 35/10 Myshkin | 6,3+6,3 | 6.3 | 6.3 | 3.57 | 2.28 | 1.29 |  |  | 3.57 | 0 | 6.62 | 3.05 | 3.05 | available | 0.94 | 142 | SS 35/10 Myshkin | SS35/10Мышкин | 6,3+6,3 | 1.569 | 1.6691 | 5.2391 |  |  | 5.2391 | 0 | 6.62 | 1.3809 | 1.3809 | available
143 | SS 110/10 Volga | 5,6+6,3 | 5.6 | 6.3 | 1.9 | 0.91 | 0.99 |  |  | 1.9 | 0 | 5.88 | 3.98 | 3.98 | available | 0.95 | 143 | SS 110/10 Volga | SS110/10Волга | 5,6+6,3 | 0.19 | 0.2 | 2.1 |  |  | 2.1 | 0 | 5.88 | 3.78 | 3.78 | available
144 | SS 35/10 Krasnaya Gorka | 4,0+2,5 | 4 | 2.5 | 1.35 | 0.67 | 0.68 | 0.104 | 120 | 1.246 | 0 | 2.63 | 1.384 | 1.384 | available | 0.95 | 144 | SS 35/10 Krasnaya Gorka | SS35/10КраснаяГорка | 4,0+2,5 | 0.8227 | 0.866 | 2.216 | 0.104 | 120 | 2.112 | 0 | 2.63 | 0.518 | 0.518 | available
145 | SS 110/35/6 Vostochnaya | 25+25 | 25 | 25 | 22.48 |  |  |  |  | 22.48 | 0 | 26.25 | 3.77 | 3.77 | available | 0.79 | 145 | SS 110/35/6 Vostochnaya | SS110/35/6Восточная | 25+25 | 0 | 0 | 25.1587 |  |  | 25.1587 | 0 | 26.25 | 1.0913 | 1.0913 | available
| Nom. capacity MV, МVА | 25+25 |  |  | 4.51 | Т-1: 4.51; Т-2: 0; Min 7: 4.51; Min 8: 0; Min 9: 26.25; Min 10: 21.74 |  | Nom. capacity MV, МVА | Ном.МощностьСН,МВА | 25+25 | 0 |  | 6.6844 |  |  | 6.6844 | 0 | 26.25 | 19.5656
| Nom. capacity LV, МVА | 25+25 |  |  | 17.97 | Т-1: 10.14; Т-2: 7.83; Min 7: 17.97; Min 8: 0; Min 9: 26.25; Min 10: 8.28 |  | Nom. capacity LV, МVА | Ном.мощностьНН,МВА | 25+25 | 0.39842 | 0.50433 | 18.4743 |  |  | 18.4743 | 0 | 26.25 | 7.7757
146 | SS 110/35/10 Zalesye | 10+10 | 10 | 10 | 7.7 |  |  | 1.126 | 120 | 6.574 | 0 | 10.5 | 3.926 | 3.926 | available | 0.93 | 146 | SS 110/35/10 Zalesye | SS110/35/10Залесье | 10+10 | 0 |  | 8.2241 | 1.126 | 120 | 7.0981 | 0 | 10.5 | 3.4019 | 3.4019 | available
| Nom. capacity MV, МVА | 10+10 |  |  | 1.16 | Т-1: 0.32; Т-2: 0.84; Min 7: 1.16; Min 8: 0; Min 9: 10.5; Min 10: 9.34 |  | Nom. capacity MV, МVА | Ном.МощностьСН,МВА | 10+10 | 0 |  | 1.2057 |  |  | 1.2057 | 0 | 10.5 | 9.2943
| Nom. capacity LV, МVА | 10+10 |  |  | 6.54 | 3.01 | 3.53 | 1.126 | 120 | 5.414 | 0 | 10.5 | 5.086 |  |  |  |  | Nom. capacity LV, МVА | Ном.мощностьНН,МВА | 10+10 | 0.445 | 0.47849 | 7.0185 | 1.126 | 120 | 5.8925 | 0 | 10.5 | 4.6075
147 | SS 110/10 Lugovaya | 6,3+6,3 | 6.3 | 6.3 | 2.39 | 1.64 | 0.75 |  |  | 2.39 | 0 | 6.62 | 4.23 | 4.23 | available | 0.88 | 147 | SS 110/10 Lugovaya | SS110/10Луговая | 6,3+6,3 | 0.3385 | 0.38466 | 2.7747 |  |  | 2.7747 | 0 | 6.62 | 3.8453 | 3.8453 | available
148 | SS 110/35/10 Lom | 10+10 | 10 | 10 | 8.8 |  |  | 1.057 | 120 | 7.743 | 0 | 10.5 | 2.757 | 2.757 | available | 0.92 | 148 | SS 110/35/10 Lom | SS110/35/10Лом | 10+10 | 0 |  | 11.377 | 1.057 | 120 | 10.32 | 0 | 10.5 | 0.18002 | 0.18002 | available
| Nom. capacity MV, МVА | 10+10 |  |  | 6.73 | Т-1: 4.25; Т-2: 2.48; Min 7: 6.73; Min 8: 0; Min 9: 10.5; Min 10: 3.77 |  | Nom. capacity MV, МVА | Ном.МощностьСН,МВА | 10+10 | 0 |  | 8.6618 |  |  | 8.6618 | 0 | 10.5 | 1.8382
| Nom. capacity LV, МVА | 10+10 |  |  | 2.07 | 1.65 | 0.42 | 1.057 | 120 | 1.013 | 0 | 10.5 | 9.487 |  |  |  |  | Nom. capacity LV, МVА | Ном.мощностьНН,МВА | 10+10 | 0.5936 | 0.64522 | 2.7152 | 1.057 | 120 | 1.6582 | 0 | 10.5 | 8.8418
149 | SS 35/10 Varegovo | 1,6+2,5 | 1.6 | 2.5 | 0.66 | 0.43 | 0.23 |  |  | 0.66 | 0 | 1.68 | 1.02 | 1.02 | available | 0.91 | 149 | SS 35/10 Varegovo | SS35/10Варегово | 1,6+2,5 | 0.4036 | 0.44352 | 1.1035 |  |  | 1.1035 | 0 | 1.68 | 0.57648 | 0.57648 | available
150 | SS 110/35/10 Shestikhino | 10+10 | 10 | 10 | 6.79 |  |  | 0.208 | 120 | 6.582 | 0 | 10.5 | 3.918 | 3.918 | available | 0.97 | 150 | SS 110/35/10 Shestikhino | SS110/35/10Шестихино | 10+10 | 0 |  | 9.422 | 0.208 | 120 | 9.214 | 0 | 10.5 | 1.286 | 1.286 | available
| Nom. capacity MV, МVА | 10+10 |  |  | 6.24 | Т-1: 1.98; Т-2: 4.26; Min 7: 6.24; Min 8: 0; Min 9: 10.5; Min 10: 4.26 |  | Nom. capacity MV, МVА | Ном.МощностьСН,МВА | 10+10 | 0 |  | 8.7318 |  |  | 8.7318 | 0 | 10.5 | 1.7682
| Nom. capacity LV, МVА | 10+10 |  |  | 0.55 | 0.27 | 0.28 | 0.208 | 120 | 0.342 | 0 | 10.5 | 10.158 |  |  |  |  | Nom. capacity LV, МVА | Ном.мощностьНН,МВА | 10+10 | 0.136 | 0.14021 | 0.69021 | 0.208 | 120 | 0.48221 | 0 | 10.5 | 10.0178
151 | SS 110/35/10 Kryukovo | 6.3 | 6.3 |  | 2.53 | Min 8: 0; Min 11: 1.482; Min 12: available; Min 13: 0.94 | 151 | SS 110/35/10 Kryukovo | SS110/35/10Крюково | 6.3 | 0 |  | 3.3986 |  |  |  | 0 |  |  | 1.448 | available
| Nom. capacidty MV, МVА | 6.3 |  |  | 2.28 | Т-1: 2.28; Min 8: 0 |  | Nom. capacidty MV, МVА | Ном.МощностьСН,МВА | 6.3 | 0 |  | 3.1146 |  |  |  | 0
| Nom. capacity LV, МVА | 6.3 |  |  | 0.25 | 0.25 |  | 1.732 | 1 day and night | 0.25 | 0 | 1.732 | 1.482 |  |  |  |  | Nom. capacity LV, МVА | Ном.мощностьНН,МВА | 6.3 | 0.032 | 0.034043 | 0.28404 | 1.732 | 1 day and night | 0.28404 | 0 | 1.732 | 1.448
152 | SS 35/10 Beloe | 2.5 | 2.5 |  | 0.56 | 0.56 |  | 1.455 | 1 day and night | 0.56 | 0 | 1.455 | 0.895 | 0.895 | available | 0.96 | 152 | SS 35/10 Beloe | SS35/10Белое | 2.5 | 0.03 | 0.03125 | 0.59125 | 1.455 | 1 day and night | 0.59125 | 0 | 1.455 | 0.86375 | 0.86375 | available
153 | SS 110/35/10 Glebovo | 10 | 10 |  | 5.5 | Min 8: 0; Min 11: -2.276; Min 12: unavailable; Min 13: 0.96 | 153 | SS 110/35/10 Glebovo | SS110/35/10Глебово | 10 | 0 |  | 8.3306 |  |  |  | 0 |  |  | -3.7781 | unavailable
| Nom. capacity MV, МVА | 10 |  |  | 2.41 | Т-1: 2.41; Min 8: 0 |  | Nom. capacity MV, МVА | Ном.МощностьСН,МВА | 10 | 0 |  | 3.7385 |  |  |  | 0
| Nom. capacity LV, МVА | 10 |  |  | 3.09 | 3.09 |  | 0.814 | 1 day and night | 3.09 | 0 | 0.814 | -2.276 |  |  |  |  | Nom. capacity LV, МVА | Ном.мощностьНН,МВА | 10 | 1.442 | 1.5021 | 4.5921 | 0.814 | 1 day and night | 4.5921 | 0 | 0.814 | -3.7781
154 | SS 35/6 Pesochnoye | 1,8+1,8 | 1.8 | 1.8 | 1.48 | 1.03 | 0.45 |  |  | 1.48 | 0 | 1.89 | 0.41 | 0.41 | available | 0.85 | 154 | SS 35/6 Pesochnoye | SS35/6Песочное | 1,8+1,8 | 0.0416 | 0.048941 | 1.5289 |  |  | 1.5289 | 0 | 1.89 | 0.36106 | 0.36106 | available
155 | SS 35/10 Demino | 2,5+2,5 | 2.5 | 2.5 | 0.52 | 0.15 | 0.37 | 0.035 |  | 0.485 | 0 | 2.63 | 2.145 | 2.145 | available | 0.98 | 155 | SS 35/10 Demino | SS35/10Демино | 2,5+2,5 | 0.003 | 0.0030612 | 0.52306 | 0.035 |  | 0.48806 | 0 | 2.63 | 2.1419 | 2.1419 | available
156 | SS 110/6 KS-18 | 63+63 | 63 | 63 | 17.89 | 17.05 | 0.84 |  |  | 17.89 | 0 | 66.15 | 48.26 | 48.26 | available | 0.999 | 156 | SS 110/6 KS-18 | SS110/6КС-18 | 63+63 | 0 | 0 | 17.89 |  |  | 17.89 | 0 | 66.15 | 48.26 | 48.26 | available
157 | SS 35/6 Makeikha | 1.6 | 1.6 |  | 0.25 | 0.25 |  | 0 | 1 day and night | 0.25 | 0 | 0 | -0.25 | -0.25 | unavailable | 1 | 157 | SS 35/6 Makeikha | SS35/6Макеиха | 1.6 | 0 | 0 | 0.25 | 0 | 1 day and night | 0.25 | 0 | 0 | -0.25 | -0.25 | unavailable
158 | SS 35/10 Ermakovo | 1.6 | 1.6 |  | 0.87 | 0.87 |  | 1.143 | 1 day and night | 0.87 | 0 | 1.143 | 0.273 | 0.273 | available | 0.94 | 158 | SS 35/10 Ermakovo | SS35/10Ермаково | 1.6 | 0.192 | 0.20426 | 1.0743 | 1.143 | 1 day and night | 1.0743 | 0 | 1.143 | 0.068745 | 0.068745 | available
159 | SS 35/10 Milyushino | 1.6 | 1.6 |  | 0.78 | 0.78 |  | 0.814 | 1 day and night | 0.78 | 0 | 0.814 | 0.034 | 0.034 | available | 0.93 | 159 | SS 35/10 Milyushino | SS35/10Милюшино | 1.6 | 1.121 | 1.2054 | 1.9854 | 0.814 | 1 day and night | 1.9854 | 0 | 0.814 | -1.1714 | -1.1714 | unavailable
160 | SS 35/10 Sutka | 2.5 | 2.5 |  | 0.62 | 0.62 |  | 0.606 | 1 day and night | 0.62 | 0 | 0.606 | -0.014 | -0.014 | unavailable | 0.87 | 160 | SS 35/10 Sutka | SS35/10Сутка | 2.5 | 0.017 | 0.01954 | 0.63954 | 0.606 | 1 day and night | 0.63954 | 0 | 0.606 | -0.03354 | -0.03354 | unavailable
161 | SS 35/10 Sit | 1.6 | 1.6 |  | 0.58 | 0.58 |  | 0.572 | 1 day and night | 0.58 | 0 | 0.572 | -0.008 | -0.008 | unavailable | 0.83 | 161 | SS 35/10 Sit | SS35/10Сить | 1.6 | 0.438 | 0.52771 | 1.1077 | 0.572 | 1 day and night | 1.1077 | 0 | 0.572 | -0.53571 | -0.53571 | unavailable
162 | SS 35/10 Gorelovo | 1.6 | 1.6 |  | 0.82 | 0.82 |  | 0.901 | 1 day and night | 0.82 | 0 | 0.901 | 0.081 | 0.081 | available | 0.95 | 162 | SS 35/10 Gorelovo | SS35/10Горелово | 1.6 | 0.6 | 0.63158 | 1.4516 | 0.901 | 1 day and night | 1.4516 | 0 | 0.901 | -0.55058 | -0.55058 | unavailable
163 | SS 35/6 Pishchalkino | 1.6 | 1.6 |  | 0.75 | 0.75 |  | 0 | 1 day and night | 0.75 | 0 | 0 | -0.75 | -0.75 | unavailable | 0.91 | 163 | SS 35/6 Pishchalkino | SS35/6Пищалкино | 1.6 | 0 | 0 | 0.75 | 0 | 1 day and night | 0.75 | 0 | 0 | -0.75 | -0.75 | unavailable
164 | SS 35/6 Varegovo | 1.6 | 1.6 |  | 0.02 | 0.02 |  | 0 | 1 day and night | 0.02 | 0 | 0 | -0.02 | -0.02 | unavailable | 0.89 | 164 | SS 35/6 Varegovo | SS35/6Варегово | 1.6 | 0.005 | 0.005618 | 0.025618 | 0 | 1 day and night | 0.025618 | 0 | 0 | -0.025618 | -0.025618 | unavailable
165 | SS 35/10 Levoberezhnaya | 4 | 4 |  | 1.39 | 1.39 |  | 1.351 | 1 day and night | 1.39 | 0 | 1.351 | -0.039 | -0.039 | unavailable | 0.94 | 165 | SS 35/10 Levoberezhnaya | SS35/10Левобережная | 4 | 1.178 | 1.2532 | 2.6432 | 1.351 | 1 day and night | 2.6432 | 0 | 1.351 | -1.2922 | -1.2922 | unavailable
166 | SS 110/10 Depot | 16 | 16 |  | 4.34 | 4.34 |  | 4.34 | 1 day and night | 4.34 | 0 | 4.34 | 0 | 0 | available | 0.98 | 166 | SS 110/10 Depot | SS110/10Депо | 16 | 0 | 0 | 4.34 | 4.34 | 1 day and night | 4.34 | 0 | 4.34 | 0 | 0
| Total: | 2914.7 | 1489.4 | 1425.3 | 873.93 | [12 empty] | Total: | Итого: | 2914.7 |  |  | 1048.9076
| deficit |  |  |  |  | Min 11: 16.409 |  | deficit | дефицит | [10 empty] | 29.4614
| proficit |  |  |  |  | Min 11: 671.799 |  | proficit | профицит | [10 empty] | 370.6709
[18 empty] | SS 110/6 Kinoplenka* |  | When referring to the power per the issued Technical Specifications the output power of 8780 kW is not specified, as no average power value (there is no clarity on the power flows).
Deputy Director for Technical
Issues - Chief Engineer
Note on H217: Т3
Note on H215: Т3
Note on H195: Т2
Note on I195: Т3
Note on H216: Т1
Note on H218: Т3

## Total current deficit Winter
The list of closed supply centers of IDGC of Centre according to winter load measurements in 2011 (current deficit of capacity).
No. | Name of supply center, voltage class | [5 empty] | Current deficit, MVA
Yarenergo
1 | SS 35/10 Mikhaylovsky | 6.3 |  |  |  |  | -1.24
2 | SS 35/10 Wave | 4,0+2,5 |  |  |  |  | -0.01
3 | SS 35/6 Zavolzhsky | 10+10 |  |  |  |  | -0.54
4 | SS 110/35/6 Pavlovsk | 20+25 |  |  |  |  | -4.52
5 | SS 35/6 Kelnot | 4,0 |  |  |  |  | -0.16
6 | SS 110/6 Film | 6,3+10 |  |  |  |  | -3.85
7 | SS 110/35/10 Niles | 6,3+6,3 |  |  |  |  | -0.98
8 | SS 110/35/10 Technical school | 6,3+6,3 |  |  |  |  | -1.04
9 | SS 35/10 Sarayevo | 1+1,6 |  |  |  |  | -0.3
10 | SS 35/10 Solomidino | 2.5 | 3.48 | 3.48 | 0 | 2.63 | -0.242
11 | SS 35/6 Coastal | 10+10 | 11.67 | 11.67 | 0 | 10.5 | -0.17
12 | SS 110/35/10 Glebovo | 10 | 25.25 | 25.25 | 0 | 21 | -2.276
13 | SS 35/6 Makeiha | 1.6 | 45.91 | 45.91 | 0 | 42 | -0.25
14 | SS 35/10 Sutka | 2.5 | 6.83 | 6.83 | 0 | 6.62 | -0.014
15 | SS 35/10 Sit | 1.6 |  |  |  |  | -0.008
16 | SS 35/6 Pishchalkino | 1.6 |  |  |  |  | -0.75
17 | SS 35/6 Varegovo | 1.6 |  |  |  |  | -0.02
18 | SS 35/10 Left-bank | 4 |  |  |  |  | -0.039
Total current deficit (winter) | [6 empty] | 16.409
Supply Centers, which are not taken into account due to their insignificant load

## Total expected deficit Winter
The list of closed supply centers of IDGC of Centre with expected load taking into account new connections and other development of the electical networks.
No. | Name of supply center, voltage class | Expected deficit/proficit, MVA | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number provided that technical requirements at connections or other measures performed for reconstruction of the supply center, pcs/ MVA | Дополнительная мощность по выданным ТУ на ТП, МВА | Ожидаемая нагрузка ЦП, МВА | Полная перераспределяемая мощность в перспективе с учетом выполнения мероприятий ТУ или других мероприятий по реконструкции сети инвестпрограмм и др. |  | Полная мощность с учётом перераспределения, МВА | Ограничивающие факторы, МВА | Допустимая нагрузка расчётная в режиме n-1, МВА | Пропускная способность ЦП, МВА | Current deficit/proficit, MVA
[5 empty] | МВА | Мин.
1 | 2 |  | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
Yarenergo
1 | SS 35/10 Mihajlovsky | 6.3 |  | 3.48 |  |  | 3.48 | 0 | 2.63 | -0.85 | -1.243 | unavailable
2 | SS 35/10 Shirine | 4 | 0.2 | 3.26 |  |  | 3.26 | 0 | 2.63 | -0.63 | -0.21289 | unavailable
3 | SS 110/35/10 Abbakumtsevo | 10+10 | 1.8815 | 12.1915 |  |  | 12.1915 | 0 | 10.5 | -1.6915 | -11.3 | unavailable
4 | SS 35/10 Vatolino | 4,0+4,0 | 4.6946 | 42.2246 |  |  | 42.2246 | 0 | 42 | -0.22459 | -4.7348 | unavailable
5 | SS 35/10 Wave | 4,0+2,5 | 0.432 | 12.102 |  |  | 12.102 | 0 | 10.5 | -1.602 | -0.01 | unavailable
6 | SS 35/10 Guzitsino | 4,0+4,0 | 8.5515 | 25.2515 |  |  | 25.2515 | 0 | 21 | -4.2515 | -3.0722 | unavailable
7 | SS 35/10 Dorozhaevo | 1,6+1,6 | Мин. 12: -1.2019; Мин. 13: unavailable
8 | SS 35/6 Zavolzhsky | 10+10 | Мин. 12: -0.75622; Мин. 13: unavailable
9 | SS 35/10 Kurba | 2,5+2,5 | Мин. 12: -0.10133; Мин. 13: unavailable
10 | SS 35/10 Modelovo-2 | 6,3+6,3 | Мин. 12: -3.658; Мин. 13: unavailable
11 | SS 110/35/6 Pavlovsk | 20+25 | Мин. 12: -4.95; Мин. 13: unavailable
12 | SS 35/10 Dispensary | 2,5+2,5 | Мин. 12: -0.76681; Мин. 13: unavailable
13 | SS 35/6 Chebakovo | 2,5+2,5 | Мин. 12: -0.75197; Мин. 13: unavailable
14 | SS 110/35/10 Borisogleb | 16+10 | 2.027 | 3.237 | 0.39 | 120 | 2.847 | 0 | 2.63 | -0.217 | -3.85 | unavailable
15 | SS 110/6 Film | 6,3+10 | 0.01 | 6.84 |  |  | 6.84 | 0 | 6.62 | -0.22 | -6.89 | unavailable
16 | SS 110/35/10 Niles | 6,3+6,3 | 23.7523 | 39.9523 |  |  | 39.9523 | 0 | 26.25 | -13.7023 | -19.44 | unavailable
17 | SS 110/35/6 Pereslavl | 25+25 | 0.587 | 10.157 |  |  | 10.157 | 0 | 6.62 | -3.537 | -11 | unavailable
18 | SS 110/35/10 Rostov | 20+25 | 7.5755 | 9.3555 | 0.37 | 120 | 8.9855 | 0 | 6.62 | -2.3655 | -3.75 | unavailable
19 | SS 110/35/10 Technical school | 6,3+6,3 | 14.4054 | 27.9154 |  |  | 27.9154 | 0 | 26.25 | -1.6654 | -7.43 | unavailable
20 | SS 110/35/10 Uglich | 25+25 | 3.4781 | 21.7981 |  |  | 21.7981 | 0 | 21 | -0.7981 | -10.03 | unavailable
21 | SS 35/6 Fathers | 1,6+1,6 | 25.538 | 30.568 |  |  | 30.568 | 0 | 26.25 | -4.318 | -0.16327 | unavailable
22 | SS 35/10 Glebovo | 2,5+2,5 | 1.645 | 4.405 |  |  | 4.405 | 0 | 2.63 | -1.775 | -3.1778 | unavailable
23 | SS 35/10 Kulakovo | 2,5+2,5 | 0.273 | 2.723 |  |  | 2.723 | 0 | 2.63 | -0.093 | -0.32667 | unavailable
24 | SS 35/6 Kupan | 2,5+2,5 | 2.193 | 3.283 | 0.3 | 120 | 2.983 | 0 | 2.63 | -0.353 | -0.91818 | unavailable
25 | SS 35/10 Uplands | 4,0+4,0 | Мин. 12: -1.6193; Мин. 13: unavailable
26 | SS 35/10 Sarajevo | 1+1,6 | Мин. 12: -1.1765; Мин. 13: unavailable
27 | SS 35/10 Skomorohovo | 1,6+1,6 | Мин. 12: -3.1119; Мин. 13: unavailable
28 | SS 35/10 Solomidino | 2.5 | Мин. 12: -2.4893; Мин. 13: unavailable
29 | SS 35/6 Coastal | 10+10 | Мин. 12: -1.0643; Мин. 13: unavailable
30 | SS 110/35/10 Glebovo | 10 | Мин. 12: -3.78; Мин. 13: unavailable
31 | SS 35/6 Makeiha | 1.6 | Мин. 12: -0.25; Мин. 13: unavailable
32 | SS 35/10 Miljushino | 1.6 | Мин. 12: -1.1714; Мин. 13: unavailable
33 | SS 35/10 Sutka | 2.5 | Мин. 12: -0.03354; Мин. 13: unavailable
34 | SS 35/10 Sit | 1.6 | Мин. 12: -0.53571; Мин. 13: unavailable
35 | SS 35/10 Gorelovo | 1.6 | Мин. 12: -0.55058; Мин. 13: unavailable
36 | SS 35/6 Pishchalkino | 1.6 | Мин. 12: -0.75; Мин. 13: unavailable
37 | SS 35/6 Varegovo | 1.6 | Мин. 12: -0.025618; Мин. 13: unavailable
38 | SS 35/10 Left-bank | 4 | Мин. 12: -1.2922; Мин. 13: unavailable
39 | SS 35/10 Krasnoye | 4,0+4,0 | Мин. 12: -0.73049; Мин. 13: unavailable
40 | SS 35/10 Filimonovo | 2,5+2,5 | Мин. 12: -0.92688; Мин. 13: unavailable
| Total: |  | Мин. 12: -119.2428