## брянск
[9 empty] | table 1 | [12 empty] | table 2
No. | Object of main substation, voltage class | Current deficit | [8 empty] | Note | No. | Object of main substation, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | Summary total capacity of Central Substation following the results of measurements of load maximum Sмах , MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Main Substation, MVA |  |  |  |  | Installed power capacity of transformers Sуst., including their number in future subject to fulfillment of technical specifications at TS or other measures on reconstruction of MS pcs/ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load of Main substation, MVA | Full re-distributed capacity in future subject to fulfillment of measures of technical specifications or other measures on reconstruction of network of investment programs etc. |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Main Substation, MVA
|  |  |  | MVA | Min. | [11 empty] | MVA | Min.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | SS 110/10 kv Lopandino | 6.3 | 1.2 | 1.2 | 24 hours | 0 | 0 | 6.615 | 6.615 | 6.615 | opened | 1 | SS 110/10 kv Lopandino | 6.3 | 0 | 1.2 | 1.2 | 24 hours | 0 | 0 | 6.615 | 6.615 | 6.615 | opened
2 | SS 110/35/10 kv Nerussa | 16 | 3.8 | 3.4 | 24 hours | 0.4 | 0 | 16.8 | 16.4 | 15.1 | opened | 2 | SS 110/35/10 kv Nerussa | 16 | 0.054 | 3.854 | 2.6 | 24 hours | 1.254 | 0 | 16.8 | 15.546 | 15.1 | opened
| Nom. capacity MV, MVA | 16 | 1.7 | 1.5 | 24 hours | 0.2 | 0 | 16.8 | 15.1 |  |  |  | Nom. capacity MV, MVA | 16 |  | 1.7 | 1.5 | 24 hours | 0.2 | 0 | 16.8 | 15.1
| Nom. capacity LV, MVA | 16 | 2.1 | 1.9 | 24 hours | 0.2 | 0 | 16.8 | 16.6 |  |  |  | Nom. capacity LV, MVA | 16 | 0.054 | 2.154 | 1.1 | 24 hours | 1.054 | 0 | 16.8 | 15.746
3 | SS 110/6 kv Svenskaya | 6.3 | 1.602 | 1.5 | 24 hours | 0.102 | 0 | 6.615 | 6.513 | 6.513 | opened | 3 | SS 110/6 kv Svenskaya | 6.3 | 0.177 | 1.779 | 1.5 | 24 hours | 0.279 | 0 | 6.615 | 6.336 | 6.336 | opened
4 | SS 110/10 kv Khmelevskaya | 6.3 | 0.361 | 0.361 | 24 hours | 0 | 0 | 6.615 | 6.615 | 6.615 | opened | 4 | SS 110/10 kv Khmelevskaya | 6.3 | 0.016 | 0.377 | 0.361 | 24 hours | 0.016 | 0 | 6.615 | 6.599 | 6.599 | opened
5 | SS 110/6 kv Energoremont | 10 | 6.4 | 6.4 | 24 hours | 0 | 0 | 10.5 | 10.5 | 10.5 | opened | 5 | SS 110/6 kv Energoremont | 10 | 0 | 6.4 | 6.4 | 24 hours | 0 | 0 | 10.5 | 10.5 | 10.5 | opened
1 | SS 110/6 kv Naytopovichi 8NA | 10 | 0.671 | 0.671 | 24 hours | 0 | 0 | 10.5 | 10.5 | 10.5 | opened | 1 | SS 110/6 kv Naytopovichi 8NA | 10 | 0.045 | 0.716 | 0.671 | 24 hours | 0.045 | 0 | 10.5 | 10.455 | 10.455 | opened
2 | SS 110/10 kv Glybochka | 2.5 | 1.225 | 1.225 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 2 | SS 110/10 kv Glybochka | 2.5 | 0.139 | 1.364 | 1.225 | 24 hours | 0.139 | 0 | 2.625 | 2.486 | 2.486 | opened
3 | SS 110/10 kv Desyatukha | 6.3 | 1.191 | 1.187 | 24 hours | 0.004 | 0 | 6.615 | 6.611 | 6.611 | opened | 3 | SS 110/10 kv Desyatukha | 6.3 | 0.033 | 1.224 | 1.187 | 24 hours | 0.037 | 0 | 6.615 | 6.578 | 6.578 | opened
4 | SS 110/35/10 kv Ivaytenki | 6.3 | 1.6 | 1.6 | 24 hours | 0 | 0 | 6.615 | 6.615 | 5.915 | opened | 4 | SS 110/35/10 kv Ivaytenki | 6.3 | 0.03 | 1.646 | 1.6 | 24 hours | 0.046 | 0 | 6.615 | 6.569 | 5.915 | opened
| Nom. capacity MV, MVA | 6.3 | 0.7 | 0.9 | 24 hours | 0 | 0 | 6.615 | 5.915 |  |  |  | Nom. capacity MV, MVA | 6.3 |  | 0.7 | 0.9 | 24 hours | 0 | 0 | 6.615 | 5.915
| Nom. capacity LV, MVA | 6.3 | 0.9 | 0.7 | 24 hours | 0.2 | 0 | 6.615 | 6.415 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.046 | 0.946 | 0.7 | 24 hours | 0.246 | 0 | 6.615 | 6.369
5 | SS 110/35/10 kv Lugovaya | 16 | 5.4 | 4.7 | 24 hours | 0.7 | 0 | 16.8 | 16.1 | 12.1 | opened | 5 | SS 110/35/10 kv Lugovaya | 16 | 0.077 | 5.477 | 4.7 | 24 hours | 0.777 | 0 | 16.8 | 16.023 | 12.1 | opened
| Nom. capacity MV, MVA | 16 | 4.7 | 3.8 | 24 hours | 0.9 | 0 | 16.8 | 12.1 |  |  |  | Nom. capacity MV, MVA | 16 |  | 4.7 | 3.8 | 24 hours | 0.9 | 0 | 16.8 | 12.1
| Nom. capacity LV, MVA | 16 | 0.7 | 0.9 | 24 hours | 0 | 0 | 16.8 | 16.8 |  |  |  | Nom. capacity LV, MVA | 16 | 0.077 | 0.777 | 0.9 | 24 hours | 0 | 0 | 16.8 | 16.8
6 | SS 110/35/10 kv Plyuskovo | 6.3 | 2.2 | 2.1 | 24 hours | 0.1 | 0 | 6.615 | 6.515 | 5.615 | opened | 6 | SS 110/35/10 kv Plyuskovo | 6.3 | 0.103 | 2.303 | 2.1 | 24 hours | 0.203 | 0 | 6.615 | 6.412 | 5.615 | opened
| Nom. capacity MV, MVA | 6.3 | 1 | 1.1 | 24 hours | 0 | 0 | 6.615 | 5.615 |  |  |  | Nom. capacity MV, MVA | 6.3 |  | 1 | 1.1 | 24 hours | 0 | 0 | 6.615 | 5.615
| Nom. capacity LV, MVA | 6.3 | 1.2 | 1 | 24 hours | 0.2 | 0 | 6.615 | 6.415 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.103 | 1.303 | 1 | 24 hours | 0.303 | 0 | 6.615 | 6.312
7 | SS 35/10 kv Aleshinskaya | 2.5 | 0.4 | 0.4 | 24 hours | 0.4 | 0 | 0.4 | 0 | 0 | opened | 7 | SS 35/10 kv Aleshinskaya | 2.5 | 0.019 | 0.419 | 0.419 | 24 hours | 0.419 | 0 | 0.419 | 0 | 0 | opened
8 | SS 35/10 kv Altukhovskaya | 1.6 | 0.5 | 0.5 | 24 hours | 0.5 | 0 | 0.5 | 0 | 0 | opened | 8 | SS 35/10 kv Altukhovskaya | 1.6 | 0 | 0.5 | 0.5 | 24 hours | 0.5 | 0 | 0.5 | 0 | 0 | opened
9 | SS 35/10 kv Domashovo | 2.5 | 0.522 | 0.522 | 24 hours | 0.522 | 0 | 0.522 | 0 | 0 | opened | 9 | SS 35/10 kv Domashovo | 2.5 | 0.896 | 1.418 | 1.418 | 24 hours | 1.418 | 0 | 1.418 | 0 | 0 | opened
10 | SS 35/6 kv Dronovskaya | 2.5 | 0.6 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0 | 0 | opened | 10 | SS 35/6 kv Dronovskaya | 2.5 | 0.011 | 0.611 | 0.611 | 24 hours | 0.611 | 0 | 0.611 | 0 | 0 | opened
11 | SS 35/10 kv Kokorevskaya | 4 | 0.9 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0 | 0 | opened | 11 | SS 35/10 kv Kokorevskaya | 4 | 0.003 | 0.903 | 0.903 | 24 hours | 0.903 | 0 | 0.903 | 0 | 0 | opened
12 | SS 35/6 kv Malopolpinskaya | 4 | 0.447 | 0.447 | 24 hours | 0.447 | 0 | 0.447 | 0 | 0 | opened | 12 | SS 35/6 kv Malopolpinskaya | 4 | 0.086 | 0.533 | 0.533 | 24 hours | 0.533 | 0 | 0.533 | 0 | 0 | opened
13 | SS 35/10 kv Morachevskaya | 1.6 | 0.316 | 0.316 | 24 hours | 0.316 | 0 | 0.316 | 0 | 0 | opened | 13 | SS 35/10 kv Morachevskaya | 1.6 | 0.741 | 1.057 | 1.057 | 24 hours | 1.057 | 0 | 1.057 | 0 | 0 | opened
14 | SS 35/10 kv Saltanovskaya | 2.5 | 0.66 | 0.66 | 24 hours | 0.66 | 0 | 0.66 | 0 | 0 | opened | 14 | SS 35/10 kv Saltanovskaya | 2.5 | 0.005 | 0.665 | 0.665 | 24 hours | 0.665 | 0 | 0.665 | 0 | 0 | opened
15 | SS 35/10 kv Svetovo | 2.5 | 0.375 | 0.375 | 24 hours | 0.375 | 0 | 0.375 | 0 | 0 | opened | 15 | SS 35/10 kv Svetovo | 2.5 | 0.005 | 0.38 | 0.38 | 24 hours | 0.38 | 0 | 0.38 | 0 | 0 | opened
16 | SS 35/10 kv Seshcha | 2.5 | 0.6 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0 | 0 | opened | 16 | SS 35/10 kv Seshcha | 2.5 | 0.01 | 0.61 | 0.61 | 24 hours | 0.61 | 0 | 0.61 | 0 | 0 | opened
17 | SS 35/10 kv Sovkhoznaya | 4 | 0.4 | 0.4 | 24 hours | 0.4 | 0 | 0.4 | 0 | 0 | opened | 17 | SS 35/10 kv Sovkhoznaya | 4 | 0.005 | 0.405 | 0.405 | 24 hours | 0.405 | 0 | 0.405 | 0 | 0 | opened
18 | SS 35/10 kv Strachevskaya | 2.5 | 0.6 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0 | 0 | opened | 18 | SS 35/10 kv Strachevskaya | 2.5 | 0.054 | 0.654 | 0.654 | 24 hours | 0.654 | 0 | 0.654 | 0 | 0 | opened
19 | SS 35/10 kv Strashevichi | 4 | 0.732 | 0.732 | 24 hours | 0.732 | 0 | 0.732 | 0 | 0 | opened | 19 | SS 35/10 kv Strashevichi | 4 | 1.138 | 1.87 | 1.87 | 24 hours | 1.87 | 0 | 1.87 | 0 | 0 | opened
20 | SS 35/10 kv Usozhskaya | 2.5 | 0.886 | 0.886 | 24 hours | 0.886 | 0 | 0.886 | 0 | 0 | opened | 20 | SS 35/10 kv Usozhskaya | 2.5 | 0.046 | 0.932 | 0.932 | 24 hours | 0.932 | 0 | 0.932 | 0 | 0 | opened
21 | SS 35/10 kv Kharinovskaya | 1 | 0.1 | 0.1 | 24 hours | 0.1 | 0 | 0.1 | 0 | 0 | opened | 21 | SS 35/10 kv Kharinovskaya | 1 | 0 | 0.1 | 0.1 | 24 hours | 0.1 | 0 | 0.1 | 0 | 0 | opened
22 | SS 35/10 kv Kharitonovskaya | 4 | 0.762 | 0.762 | 24 hours | 0.762 | 0 | 0.762 | 0 | 0 | opened | 22 | SS 35/10 kv Kharitonovskaya | 4 | 0.117 | 0.879 | 0.879 | 24 hours | 0.879 | 0 | 0.879 | 0 | 0 | opened
23 | SS 35/10 kv Divovka | 2.5 | 0.632 | 0.632 | 24 hours | 0.632 | 0 | 0.632 | 0 | 0 | opened | 23 | SS 35/10 kv Divovka | 2.5 | 0.005 | 0.637 | 0.637 | 24 hours | 0.637 | 0 | 0.637 | 0 | 0 | opened
24 | SS 35/10 kv Molodkovo | 1 | 0.5 | 0.5 | 24 hours | 0.5 | 0 | 0.5 | 0 | 0 | opened | 24 | SS 35/10 kv Molodkovo | 1 | 0 | 0.5 | 0.5 | 24 hours | 0.5 | 0 | 0.5 | 0 | 0 | opened
25 | SS 35/10 kv Papsuevskaya | 2.5 | 0.412 | 0.412 | 24 hours | 0.412 | 0 | 0.412 | 0 | 0 | opened | 25 | SS 35/10 kv Papsuevskaya | 2.5 | 0.014 | 0.426 | 0.426 | 24 hours | 0.426 | 0 | 0.426 | 0 | 0 | opened
26 | SS 35/10 kv Radutinskaya | 1.6 | 0.539 | 0.539 | 24 hours | 0.539 | 0 | 0.539 | 0 | 0 | opened | 26 | SS 35/10 kv Radutinskaya | 1.6 | 0.056 | 0.595 | 0.595 | 24 hours | 0.595 | 0 | 0.595 | 0 | 0 | opened
27 | SS 35/6 kv Ushchepye | 1.6 | 0.625 | 0.625 | 24 hours | 0.625 | 0 | 0.625 | 0 | 0 | opened | 27 | SS 35/6 kv Ushchepye | 1.6 | 0.017 | 0.642 | 0.642 | 24 hours | 0.642 | 0 | 0.642 | 0 | 0 | opened
28 | SS 35/10 kv Ushchepye | 1.6 | 0.141 | 0.141 | 24 hours | 0.141 | 0 | 0.141 | 0 | 0 | opened | 28 | SS 35/10 kv Ushchepye | 1.6 | 0 | 0.141 | 0.141 | 24 hours | 0.141 | 0 | 0.141 | 0 | 0 | opened
29 | SS 35/10 kv Yakovskaya | 2.5 | 0.583 | 0.583 | 24 hours | 0.583 | 0 | 0.583 | 0 | 0 | opened | 29 | SS 35/10 kv Yakovskaya | 2.5 | 0.05 | 0.633 | 0.633 | 24 hours | 0.633 | 0 | 0.633 | 0 | 0 | opened
30 | SS 110/35/6 kv Aksinino | 40+40 | 21.1 | 0 | 0 | 21.1 | 0 | 42 | 20.9 | 20.9 | opened | 30 | SS 110/35/6 kv Aksinino | 40+40 | 0.014 | 21.114 | 0 | 0 | 21.114 | 0 | 42 | 20.886 | 20.886 | opened
| Nom. capacity MV, MVA | 40+40 | 3.5 | 0 | 0 | 3.5 | 0 | 42 | 38.5 |  |  |  | Nom. capacity MV, MVA | 40+40 |  | 3.5 | 0 | 0 | 3.5 | 0 | 42 | 38.5
| Nom. capacity LV, MVA | 40+40 | 17.6 | 0 | 0 | 17.6 | 0 | 42 | 24.4 |  |  |  | Nom. capacity LV, MVA | 40+40 | 0.014 | 17.614 | 0 | 0 | 17.614 | 0 | 42 | 24.386
31 | SS 110/10 kv Airport | 6,3+6,3 | 0.9 | 0 | 0 | 0.9 | 0 | 6.615 | 5.715 | 5.715 | opened | 31 | SS 110/10 kv Airport | 6,3+6,3 | 0.013 | 0.913 | 0 | 0 | 0.913 | 0 | 6.615 | 5.702 | 5.702 | opened
32 | SS 110/6 kv Bezhitskaya | 25+40 | 34.57 | 0 | 0 | 34.57 | 0 | 26.25 | -8.32 | -8.32 | closed | 32 | SS 110/6 kv Bezhitskaya | 25+40 | 3.182 | 37.752 | 0 | 0 | 37.752 | 0 | 26.25 | -11.502 | -11.502 | closed
33 | SS 110/6 kv Water intake | 6,3+6,3 | 1.938 | 0 | 0 | 1.938 | 0 | 6.615 | 4.677 | 4.677 | opened | 33 | SS 110/6 kv Water intake | 6,3+6,3 | 0.858 | 2.796 | 0 | 0 | 2.796 | 0 | 6.615 | 3.819 | 3.819 | opened
34 | SS 110/6 kv Gorodishchenskaya | 16+16 | 25.56 | 1.5 | 12 hours | 24.06 | 0 | 16.8 | -7.26 | -7.26 | closed | 34 | SS 110/6 kv Gorodishchenskaya | 16+16 | 0.806 | 26.366 | 1.5 | 12 hours | 24.866 | 0 | 16.8 | -8.066 | -8.066 | closed
35 | SS 110/10 kv Dobrunskaya | 6,3+4 | 4.338 | 0 | 0 | 4.338 | 0 | 4.2 | -0.138 | -0.138 | closed | 35 | SS 110/10 kv Dobrunskaya | 6,3+4 | 0.85 | 5.188 | 0 | 0 | 5.188 | 0 | 4.2 | -0.988 | -0.988 | closed
36 | SS 110/35/6 kv Dormashevskaya | 40+63 | 44.04 | 0 | 0 | 44.04 | 0 | 42 | -2.04 | -2.04 | closed | 36 | SS 110/35/6 kv Dormashevskaya | 40+63 | 3.842 | 47.882 | 0 | 0 | 47.882 | 0 | 42 | -5.882 | -5.882 | closed
| Nom. capacity MV, MVA | 40+63 | 22.42 | 0 | 0 | 22.42 | 0 | 42 | 19.58 |  |  |  | Nom. capacity MV, MVA | 40+63 |  | 22.42 | 0 | 0 | 22.42 | 0 | 42 | 19.58
| Nom. capacity LV, MVA | 40+63 | 21.62 | 0 | 0 | 21.62 | 0 | 42 | 20.38 |  |  |  | Nom. capacity LV, MVA | 40+63 | 3.842 | 25.462 | 0 | 0 | 25.462 | 0 | 42 | 16.538
37 | SS 110/35/10 kv Dubrovskaya | 16+16 | 9.37 | 0 | 0 | 9.37 | 0 | 16.8 | 7.43 | 7.43 | opened | 37 | SS 110/35/10 kv Dubrovskaya | 16+16 | 0.058 | 9.428 | 0 | 0 | 9.428 | 0 | 16.8 | 7.372 | 7.372 | opened
| Nom. capacity MV, MVA | 16+16 | 5.47 | 0 | 0 | 5.47 | 0 | 16.8 | 11.33 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 5.47 | 0 | 0 | 5.47 | 0 | 16.8 | 11.33
| Nom. capacity LV, MVA | 16+16 | 3.9 | 0 | 0 | 3.9 | 0 | 16.8 | 12.9 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.058 | 3.958 | 0 | 0 | 3.958 | 0 | 16.8 | 12.842
38 | SS 110/35/6 kv Dyadkovksya | 25+25 | 36.58 | 9.19 | 12 hours | 27.39 | 0 | 26.25 | -1.14 | -1.14 | closed | 38 | SS 110/35/6 kv Dyadkovksya | 25+25 | 0.029 | 36.609 | 8.9 | 12 hours | 27.709 | 0 | 26.25 | -1.459 | -1.459 | closed
| Nom. capacity MV, MVA | 25+25 | 9.19 | 9.19 | 12 hours | 0 | 0 | 26.25 | 17.06 |  |  |  | Nom. capacity MV, MVA | 25+25 |  | 9.19 | 8.9 | 12 hours | 0.29 | 0 | 26.25 | 17.06
| Nom. capacity LV, MVA | 25+25 | 27.39 | 0 | 0 | 27.39 | 0 | 26.25 | -1.14 |  |  |  | Nom. capacity LV, MVA | 25+25 | 0.029 | 27.419 | 0 | 0 | 27.419 | 0 | 26.25 | -1.169
39 | SS 110/35/10 kv Zhukovskaya | 16+25 | 15.7 | 5.2 | 6 hours | 10.5 | 0 | 16.8 | 6.3 | 6.3 | opened | 39 | SS 110/35/10 kv Zhukovskaya | 16+25 | 0.194 | 15.894 | 5.2 | 6 hours | 10.694 | 0 | 16.8 | 6.106 | 6.106 | opened
| Nom. capacity MV, MVA | 16+25 | 7 | 5.2 | 6 hours | 1.8 | 0 | 16.8 | 9.8 |  |  |  | Nom. capacity MV, MVA | 16+25 |  | 7 | 5.2 | 6 hours | 1.8 | 0 | 16.8 | 9.8
| Nom. capacity LV, MVA | 16+25 | 8.7 | 0 | 0 | 8.7 | 0 | 16.8 | 8.1 |  |  |  | Nom. capacity LV, MVA | 16+25 | 0.194 | 8.894 | 0 | 0 | 8.894 | 0 | 16.8 | 7.906
40 | SS 110/6 kv Zarechnaya | 10+10 | 8.27 | 0 | 0 | 8.27 | 0 | 10.5 | 2.23 | 2.23 | opened | 40 | SS 110/6 kv Zarechnaya | 10+10 | 1.183 | 9.453 | 0 | 0 | 9.453 | 0 | 10.5 | 1.047 | 1.047 | opened
41 | SS 110/35/6 kv Ivotskaya | 25+25 | 9.98 | 2.68 | 6 hours | 7.3 | 0 | 26.25 | 18.95 | 18.95 | opened | 41 | SS 110/35/6 kv Ivotskaya | 25+25 | 0 | 9.98 | 2.4 | 6 hours | 7.58 | 0 | 26.25 | 18.67 | 18.67 | opened
| Nom. capacity MV, MVA | 25+25 | 6.36 | 2.68 | 6 hours | 3.68 | 0 | 26.25 | 19.89 |  |  |  | Nom. capacity MV, MVA | 25+25 |  | 6.36 | 2.4 | 6 hours | 3.96 | 0 | 26.25 | 19.89
| Nom. capacity LV, MVA | 25+25 | 3.62 | 0 | 0 | 0 | 0 | 26.25 | 26.25 |  |  |  | Nom. capacity LV, MVA | 25+25 | 0 | 3.62 | 0 | 0 | 0 | 0 | 26.25 | 26.25
42 | SS 110/6 kv Kamvolnaya | 25+25 | 17.92 | 0 | 0 | 17.92 | 0 | 26.25 | 8.33 | 8.33 | opened | 42 | SS 110/6 kv Kamvolnaya | 25+25 | 0.981 | 18.901 | 0 | 0 | 18.901 | 0 | 26.25 | 7.349 | 7.349 | opened
43 | SS 110/6 kv Karachevskaya | 16+25 | 10.9 | 0 | 0 | 10.9 | 0 | 16.8 | 5.9 | 5.9 | opened | 43 | SS 110/6 kv Karachevskaya | 16+25 | 0.366 | 11.266 | 0 | 0 | 11.266 | 0 | 16.8 | 5.534 | 5.534 | opened
44 | SS 110/6 kv Karachizhskaya | 10+10 | 18.28 | 0 | 0 | 18.28 | 0 | 10.5 | -7.78 | -7.78 | closed | 44 | SS 110/6 kv Karachizhskaya | 10+10 | 2.613 | 20.893 | 0 | 0 | 20.893 | 0 | 10.5 | -10.393 | -10.393 | closed
45 | SS 110/35/10 kv Kletnyanskaya | 10+16 | 7.1 | 1.4 | 6 hours | 5.7 | 0 | 10.5 | 4.8 | 4.8 | opened | 45 | SS 110/35/10 kv Kletnyanskaya | 10+16 | 0.188 | 7.288 | 1.4 | 6 hours | 5.888 | 0 | 10.5 | 4.612 | 4.612 | opened
| Nom. capacity MV, MVA | 10+16 | 1.9 | 1.4 | 6 hours | 0.5 | 0 | 10.5 | 8.6 |  |  |  | Nom. capacity MV, MVA | 10+16 |  | 1.9 | 1.4 | 6 hours | 0.5 | 0 | 10.5 | 8.6
| Nom. capacity LV, MVA | 10+16 | 5.2 | 0 | 0 | 5.2 | 0 | 10.5 | 5.3 |  |  |  | Nom. capacity LV, MVA | 10+16 | 0.188 | 5.388 | 0 | 0 | 5.388 | 0 | 10.5 | 5.112
46 | SS 110/35/10 kv Komarichi | 16+16 | 11.6 | 3.7 | 6 hours | 7.9 | 0 | 16.8 | 8.9 | 8.9 | opened | 46 | SS 110/35/10 kv Komarichi | 16+16 | 0.039 | 11.639 | 3.7 | 6 hours | 7.939 | 0 | 16.8 | 8.861 | 8.861 | opened
| Nom. capacity MV, MVA | 16+16 | 6.7 | 3.7 | 6 hours | 3 | 0 | 16.8 | 10.1 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 6.7 | 3.7 | 6 hours | 3 | 0 | 16.8 | 10.1
| Nom. capacity LV, MVA | 16+16 | 4.9 | 0 | 0 | 4.9 | 0 | 16.8 | 11.9 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.039 | 4.939 | 0 | 0 | 4.939 | 0 | 16.8 | 11.861
47 | SS 110/10 kv Letoshniki | 6,3+2,5 | 1.015 | 0 | 0 | 1.015 | 0 | 2.625 | 1.61 | 1.61 | opened | 47 | SS 110/10 kv Letoshniki | 6,3+2,5 | 0.02 | 1.035 | 0 | 0 | 1.035 | 0 | 2.625 | 1.59 | 1.59 | opened
48 | SS 110/6 kv Mamonovskaya | 10+16 | 15.29 | 0 | 0 | 15.29 | 0 | 10.5 | -4.79 | -4.79 | closed | 48 | SS 110/6 kv Mamonovskaya | 10+16 | 2.307 | 17.597 | 0 | 0 | 17.597 | 0 | 10.5 | -7.097 | -7.097 | closed
49 | SS 110/35/10 kv Maritskaya | 10+16 | 5.5 | 4.5 | 6 hours | 1 | 0 | 10.5 | 9.5 | 6.1 | opened | 49 | SS 110/35/10 kv Maritskaya | 10+16 | 0.451 | 5.951 | 4.5 | 6 hours | 1.451 | 0 | 10.5 | 9.049 | 6.1 | opened
| Nom. capacity MV, MVA | 10+16 | 4.4 | 4.5 | 6 hours | 0 | 0 | 10.5 | 6.1 |  |  |  | Nom. capacity MV, MVA | 10+16 |  | 4.4 | 4.5 | 6 hours | 0 | 0 | 10.5 | 6.1
| Nom. capacity LV, MVA | 10+16 | 1.1 | 0 | 0 | 1.1 | 0 | 10.5 | 9.4 |  |  |  | Nom. capacity LV, MVA | 10+16 | 0.451 | 1.551 | 0 | 0 | 1.551 | 0 | 10.5 | 8.949
50 | SS 110/6 kv Michurinskaya | 6,3+10 | 2.504 | 0 | 0 | 2.504 | 0 | 6.615 | 4.111 | 4.111 | opened | 50 | SS 110/6 kv Michurinskaya | 6,3+10 | 0.885 | 3.389 | 0 | 0 | 3.389 | 0 | 6.615 | 3.226 | 3.226 | opened
51 | SS 110/10 kv Molotinskaya | 6,3+6,3 | 2.567 | 0 | 0 | 2.567 | 0 | 6.615 | 4.048 | 4.048 | opened | 51 | SS 110/10 kv Molotinskaya | 6,3+6,3 | 0.188 | 2.755 | 0 | 0 | 2.755 | 0 | 6.615 | 3.86 | 3.86 | opened
52 | SS 110/10 kv Polpinskaya | 16+16 | 4.7 | 0 | 0 | 4.7 | 0 | 16.8 | 12.1 | 12.1 | opened | 52 | SS 110/10 kv Polpinskaya | 16+16 | 0.129 | 4.829 | 0 | 0 | 4.829 | 0 | 16.8 | 11.971 | 11.971 | opened
53 | SS 110/6 kv Sovetskaya | 16+16+25+40 | 36.96 | 0 | 0 | 36.96 | 0 | 59.85 | 22.89 | 22.89 | opened | 53 | SS 110/6 kv Sovetskaya | 16+16+25+40 | 17.866 | 54.826 | 0 | 0 | 54.826 | 0 | 59.85 | 5.024 | 5.024 | opened
54 | SS 110/6 kv Staleliteynaya | 40+31,5+40 | 42.4 | 0 | 0 | 42.4 | 0 | 75.075 | 32.675 | 32.675 | opened | 54 | SS 110/6 kv Staleliteynaya | 40+31,5+40 | 0.178 | 42.578 | 0 | 0 | 42.578 | 0 | 75.075 | 32.497 | 32.497 | opened
55 | SS 110/10 kv Teplichnaya | 10+10 | 4.9 | 0 | 0 | 4.9 | 0 | 10.5 | 5.6 | 5.6 | opened | 55 | SS 110/10 kv Teplichnaya | 10+10 | 0.355 | 5.255 | 0 | 0 | 5.255 | 0 | 10.5 | 5.245 | 5.245 | opened
56 | SS 110/6 kv Uritskaya | 20+20 | 14.38 | 0 | 0 | 14.38 | 0 | 21 | 6.62 | 6.62 | opened | 56 | SS 110/6 kv Uritskaya | 20+20 | 0 | 14.38 | 0 | 0 | 14.38 | 0 | 21 | 6.62 | 6.62 | opened
57 | SS 110/35/10 kv Tsentralnaya | 16+16 | 14.06 | 4.8 | 6 hours | 9.26 | 0 | 16.8 | 7.54 | 7.54 | opened | 57 | SS 110/35/10 kv Tsentralnaya | 16+16 | 0.171 | 14.231 | 4.8 | 6 hours | 9.431 | 0 | 16.8 | 7.369 | 7.369 | opened
| Nom. capacity MV, MVA | 16+16 | 4.82 | 4.8 | 6 hours | 0.02 | 0 | 16.8 | 11.98 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 4.82 | 4.8 | 6 hours | 0.02 | 0 | 16.8 | 11.98
| Nom. capacity LV, MVA | 16+16 | 9.24 | 0 | 0 | 9.24 | 0 | 16.8 | 7.56 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.171 | 9.411 | 0 | 0 | 9.411 | 0 | 16.8 | 7.389
58 | SS 110/6 kv Yuzhnaya | 16+25 | 19.43 | 0 | 0 | 19.43 | 0 | 16.8 | -2.63 | -2.63 | closed | 58 | SS 110/6 kv Yuzhnaya | 16+25 | 0.238 | 19.668 | 0 | 0 | 19.668 | 0 | 16.8 | -2.868 | -2.868 | closed
59 | SS 110/10 kv Bobovichi | 6,3+2,5 | 1.497 | 0 | 0 | 1.497 | 0 | 2.625 | 1.128 | 1.128 | opened | 59 | SS 110/10 kv Bobovichi | 6,3+2,5 | 0.022 | 1.519 | 0 | 0 | 1.519 | 0 | 2.625 | 1.106 | 1.106 | opened
60 | SS 110/6 kv Belaya Berezka | 16+25 | 4.469 | 0 | 0 | 4.469 | 0 | 16.8 | 12.331 | 12.331 | opened | 60 | SS 110/6 kv Belaya Berezka | 16+25 | 0 | 4.469 | 0 | 0 | 4.469 | 0 | 16.8 | 12.331 | 12.331 | opened
61 | SS 110/10 kv Valuets | 4+6,3 | 1.208 | 0 | 0 | 1.208 | 0 | 4.2 | 2.992 | 2.992 | opened | 61 | SS 110/10 kv Valuets | 4+6,3 | 0.125 | 1.333 | 0 | 0 | 1.333 | 0 | 4.2 | 2.867 | 2.867 | opened
62 | SS 110/35/6 kv Vodoochistnaya | 10+6,3 | 2.1 | 0.54 | 3 hours | 1.56 | 0 | 42 | 40.44 | 40.1 | opened | 62 | SS 110/35/6 kv Vodoochistnaya | 10+6,3 | 0 | 2.1 | 0.54 | 3 hours | 1.56 | 0 | 42 | 40.44 | 40.1 | opened
| Nom. capacity MV, MVA | 10+6,3 | 0.2 | 0.54 | 3 hours | 0 | 0 | 42 | 41.8 |  |  |  | Nom. capacity MV, MVA | 10+6,3 |  | 0.2 | 0.54 | 3 hours | 0 | 0 | 42 | 41.8
| Nom. capacity LV, MVA | 10+6,3 | 1.9 | 0 | 0 | 1.9 | 0 | 42 | 40.1 |  |  |  | Nom. capacity LV, MVA | 10+6,3 |  | 1.9 | 0 | 0 | 1.9 | 0 | 42 | 40.1
63 | SS 110/6 kv Vysokoe | 40+40 | 31.467 | 0 | 0 | 31.467 | 0 | 42 | 10.533 | 10.533 | opened | 63 | SS 110/6 kv Vysokoe | 40+40 | 0.036 | 31.503 | 0 | 0 | 31.503 | 0 | 42 | 10.497 | 10.497 | opened
64 | SS 110/10 kv Zalineynaya | 10+6,3 | 3.931 | 0 | 0 | 3.931 | 0 | 6.615 | 2.684 | 2.684 | opened | 64 | SS 110/10 kv Zalineynaya | 10+6,3 | 0.171 | 4.102 | 0 | 0 | 4.102 | 0 | 6.615 | 2.513 | 2.513 | opened
65 | SS 110/6 kv Zapadnaya | 10+10 | 10.5 | 0 | 0 | 10.5 | 0 | 10.5 | 0 | 0 | opened | 65 | SS 110/6 kv Zapadnaya | 10+10 | 0.016 | 10.516 | 0 | 0 | 10.516 | 0 | 10.5 | -0.016 | -0.016 | opened
66 | SS 110/35/10 kv Klimovo | 16+16 | 10.2 | 1.64 | 6 hours | 8.56 | 0 | 42 | 33.44 | 33.44 | opened | 66 | SS 110/35/10 kv Klimovo | 16+16 | 0.193 | 10.393 | 1.64 | 6 hours | 8.753 | 0 | 42 | 33.247 | 33.247 | opened
| Nom. capacity MV, MVA | 16+16 | 3.1 | 1.64 | 6 hours | 1.46 | 0 | 42 | 38.9 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 3.1 | 1.64 | 6 hours | 1.46 | 0 | 42 | 38.9
| Nom. capacity LV, MVA | 16+16 | 7.1 | 0 | 0 | 7.1 | 0 | 42 | 34.9 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.193 | 7.293 | 0 | 0 | 7.293 | 0 | 42 | 34.707
67 | SS 110/35/6 kv Kozhany | 10+10 | 3.864 | 3.12 | 6 hours | 0.744 | 0 | 42 | 41.256 | 38.884 | opened | 67 | SS 110/35/6 kv Kozhany | 10+10 | 0.013 | 3.877 | 3.12 | 6 hours | 0.757 | 0 | 42 | 41.243 | 38.884 | opened
| Nom. capacity MV, MVA | 10+10 | 3.116 | 3.12 | 6 hours | -0.004 | 0 | 42 | 38.884 |  |  |  | Nom. capacity MV, MVA | 10+10 |  | 3.116 | 3.12 | 6 hours | -0.004 | 0 | 42 | 38.884
| Nom. capacity LV, MVA | 10+10 | 0.748 | 0 | 0 | 0.748 | 0 | 42 | 41.252 |  |  |  | Nom. capacity LV, MVA | 10+10 | 0.013 | 0.761 | 0 | 0 | 0.761 | 0 | 42 | 41.239
68 | SS 110/10 kv Krasny Rog | 2,5+2,5 | 1.265 | 0 | 0 | 1.265 | 0 | 2.625 | 1.36 | 1.36 | opened | 68 | SS 110/10 kv Krasny Rog | 2,5+2,5 | 0.139 | 1.404 | 0 | 0 | 1.404 | 0 | 2.625 | 1.221 | 1.221 | opened
69 | SS 110/35/10 kv Pogar | 16+16+16 | 10.552 | 1.8 | 6 hours | 8.752 | 0 | 42 | 33.248 | 33.248 | opened | 69 | SS 110/35/10 kv Pogar | 16+16+16 | 0.772 | 11.324 | 1.8 | 6 hours | 9.524 | 0 | 42 | 32.476 | 32.476 | opened
| Nom. capacity MV, MVA | 16+16 | 1.803 | 1.8 | 6 hours | 0.003 | 0 | 42 | 40.197 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 1.803 | 1.8 | 6 hours | 0.003 | 0 | 42 | 40.197
| Nom. capacity LV, MVA | 16+16 | 8.749 | 0 | 0 | 8.749 | 0 | 42 | 33.251 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.772 | 9.521 | 0 | 0 | 9.521 | 0 | 42 | 32.479
70 | SS 110/35/10 kv Pochepskaya | 25+25 | 12.995 | 2.21 | 3 hours | 10.785 | 0 | 42 | 31.215 | 31.213 | opened | 70 | SS 110/35/10 kv Pochepskaya | 25+25 | 1.957 | 14.952 | 2.21 | 3 hours | 12.742 | 0 | 42 | 29.258 | 29.256 | opened
| Nom. capacity MV, MVA | 25+25 | 2.208 | 2.21 | 3 hours | -0.002 | 0 | 42 | 39.792 |  |  |  | Nom. capacity MV, MVA | 25+25 |  | 2.208 | 2.21 | 3 hours | -0.002 | 0 | 42 | 39.792
| Nom. capacity LV, MVA | 25+25 | 10.787 | 0 | 0 | 10.787 | 0 | 42 | 31.213 |  |  |  | Nom. capacity LV, MVA | 25+25 | 1.957 | 12.744 | 0 | 0 | 12.744 | 0 | 42 | 29.256
71 | SS 110/10 kv Semyachki | 2,5+2,5 | 0.539 | 0 | 0 | 0.539 | 0 | 2.625 | 2.086 | 2.086 | opened | 71 | SS 110/10 kv Semyachki | 2,5+2,5 | 0.006 | 0.545 | 0 | 0 | 0.545 | 0 | 2.625 | 2.08 | 2.08 | opened
72 | SS 110/35/10 kv Starodub | 16+16 | 12.564 | 7.34 | 6 hours | 5.224 | 0 | 42 | 36.776 | 34.665 | opened | 72 | SS 110/35/10 kv Starodub | 16+16 | 0.021 | 12.585 | 7.34 | 6 hours | 5.245 | 0 | 42 | 36.755 | 34.665 | opened
| Nom. capacity MV, MVA | 16+16 | 7.335 | 7.34 | 6 hours | -0.005 | 0 | 42 | 34.665 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 7.335 | 7.34 | 6 hours | -0.005 | 0 | 42 | 34.665
| Nom. capacity LV, MVA | 16+16 | 5.229 | 0 | 0 | 5.229 | 0 | 42 | 36.771 |  |  |  | Nom. capacity LV, MVA | 16+16 | 0.021 | 5.25 | 0 | 0 | 5.25 | 0 | 42 | 36.75
73 | SS 110/10 kv Staroselye | 6,3+6,3 | 0.976 | 0 | 0 | 0.976 | 0 | 6.615 | 5.639 | 5.639 | opened | 73 | SS 110/10 kv Staroselye | 6,3+6,3 | 0.114 | 1.09 | 0 | 0 | 1.09 | 0 | 6.615 | 5.525 | 5.525 | opened
74 | SS 110/35/6 kv Surazh | 16+16 | 18.6 | 3.04 | 6 hours | 15.56 | 0 | 42 | 26.44 | 26.4 | opened | 74 | SS 110/35/6 kv Surazh | 16+16 | 0 | 18.6 | 3.04 | 6 hours | 15.56 | 0 | 42 | 26.44 | 26.4 | opened
| Nom. capacity MV, MVA | 16+16 | 3 | 3.04 | 6 hours | -0.04 | 0 | 42 | 39 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 3 | 3.04 | 6 hours | -0.04 | 0 | 42 | 39
| Nom. capacity LV, MVA | 16+16 | 15.6 | 0 | 0 | 15.6 | 0 | 42 | 26.4 |  |  |  | Nom. capacity LV, MVA | 16+16 |  | 15.6 | 0 | 0 | 15.6 | 0 | 42 | 26.4
75 | SS 110/10 kv Trubchevsk | 16+10 | 7.871 | 0 | 0 | 7.871 | 0 | 10.5 | 2.629 | 2.629 | opened | 75 | SS 110/10 kv Trubchevsk | 16+10 | 0.828 | 8.699 | 0 | 0 | 8.699 | 0 | 10.5 | 1.801 | 1.801 | opened
76 | SS 110/10 kv Shelomy | 6,3+6,3 | 1.005 | 0 | 0 | 1.005 | 0 | 6.615 | 5.61 | 5.61 | opened | 76 | SS 110/10 kv Shelomy | 6,3+6,3 | 0.016 | 1.021 | 0 | 0 | 1.021 | 0 | 6.615 | 5.594 | 5.594 | opened
77 | SS 110/35/6 kv Yubileynaya | 16+16 | 14.3 | 6.45 | 3 hours | 7.85 | 0 | 42 | 34.15 | 34 | opened | 77 | SS 110/35/6 kv Yubileynaya | 16+16 | 3.533 | 17.833 | 6.45 | 3 hours | 11.383 | 0 | 42 | 30.617 | 30.467 | opened
| Nom. capacity MV, MVA | 16+16 | 6.3 | 6.45 | 3 hours | 0 | 0 | 42 | 35.7 |  |  |  | Nom. capacity MV, MVA | 16+16 |  | 6.3 | 6.45 | 3 hours | 0 | 0 | 42 | 35.7
| Nom. capacity LV, MVA | 16+16 | 8 | 0 | 0 | 8 | 0 | 42 | 34 |  |  |  | Nom. capacity LV, MVA | 16+16 | 3.533 | 11.533 | 0 | 0 | 11.533 | 0 | 42 | 30.467
78 | SS 35/6 kv Beloberezhskaya | 6,3+6,3 | 3 | 0 | 0 | 3 | 0 | 6.615 | 3.615 | 3.615 | opened | 78 | SS 35/6 kv Beloberezhskaya | 6,3+6,3 | 0.043 | 3.043 | 0 | 0 | 3.043 | 0 | 6.615 | 3.572 | 3.572 | opened
79 | SS 35/10 kv Brasovskaya | 6,3+6,3 | 3.828 | 0 | 0 | 3.828 | 0 | 6.615 | 2.787 | 2.787 | opened | 79 | SS 35/10 kv Brasovskaya | 6,3+6,3 | 0.008 | 3.836 | 0 | 0 | 3.836 | 0 | 6.615 | 2.779 | 2.779 | opened
80 | SS 35/10 kv Bulshevskaya | 1,6+1,6 | 0.6 | 0 | 0 | 0.6 | 0 | 1.68 | 1.08 | 1.08 | opened | 80 | SS 35/10 kv Bulshevskaya | 1,6+1,6 | 0 | 0.6 | 0 | 0 | 0.6 | 0 | 1.68 | 1.08 | 1.08 | opened
81 | SS 35/6 kv Bytosh | 3,2+6,3 | 2.708 | 0 | 0 | 2.708 | 0 | 3.36 | 0.652 | 0.652 | opened | 81 | SS 35/6 kv Bytosh | 3,2+6,3 | 0 | 2.708 | 0 | 0 | 2.708 | 0 | 3.36 | 0.652 | 0.652 | opened
82 | SS 35/6 kv Velyaminovskaya | 4+4 | 2.021 | 0 | 0 | 2.021 | 0 | 4.2 | 2.179 | 2.179 | opened | 82 | SS 35/6 kv Velyaminovskaya | 4+4 | 0.035 | 2.056 | 0 | 0 | 2.056 | 0 | 4.2 | 2.144 | 2.144 | opened
83 | SS 35/6 kv Vetma | 2,5+2,5 | 0.21 | 0 | 0 | 0.21 | 0 | 2.625 | 2.415 | 2.415 | opened | 83 | SS 35/6 kv Vetma | 2,5+2,5 | 0.016 | 0.226 | 0 | 0 | 0.226 | 0 | 2.625 | 2.399 | 2.399 | opened
84 | SS 35/6 kv Volodarskaya | 10+6,3 | 11.35 | 0 | 0 | 11.35 | 0 | 6.615 | -4.735 | -4.735 | closed | 84 | SS 35/6 kv Volodarskaya | 10+6,3 | 0 | 11.35 | 0 | 0 | 11.35 | 0 | 6.615 | -4.735 | -4.735 | closed
85 | SS 35/10 kv Glodnevskaya | 4+2,5 | 1.353 | 0 | 0 | 1.353 | 0 | 2.625 | 1.272 | 1.272 | opened | 85 | SS 35/10 kv Glodnevskaya | 4+2,5 | 0.02 | 1.373 | 0 | 0 | 1.373 | 0 | 2.625 | 1.252 | 1.252 | opened
86 | SS 35/6 kv Gorodskaya | 10+10 | 12.14 | 0 | 0 | 12.14 | 0 | 10.5 | -1.64 | -1.64 | closed | 86 | SS 35/6 kv Gorodskaya | 10+10 | 0 | 12.14 | 0 | 0 | 12.14 | 0 | 10.5 | -1.64 | -1.64 | closed
87 | SS 35/10 kv Grishina Sloboda | 4+4 | 0.6 | 0 | 0 | 0.6 | 0 | 4.2 | 3.6 | 3.6 | opened | 87 | SS 35/10 kv Grishina Sloboda | 4+4 | 0.043 | 0.643 | 0 | 0 | 0.643 | 0 | 4.2 | 3.557 | 3.557 | opened
88 | SS 35/10 kv Dobrovodye | 1,6+1,6 | 0.316 | 0 | 0 | 0.316 | 0 | 1.68 | 1.364 | 1.364 | opened | 88 | SS 35/10 kv Dobrovodye | 1,6+1,6 | 0 | 0.316 | 0 | 0 | 0.316 | 0 | 1.68 | 1.364 | 1.364 | opened
89 | SS 35/10 kv Zhiryatinskaya | 4+4 | 1.7 | 0 | 0 | 1.7 | 0 | 4.2 | 2.5 | 2.5 | opened | 89 | SS 35/10 kv Zhiryatinskaya | 4+4 | 0.062 | 1.762 | 0 | 0 | 1.762 | 0 | 4.2 | 2.438 | 2.438 | opened
90 | SS 35/10 kv Igritskaya | 4+6,3 | 2.084 | 0 | 0 | 2.084 | 0 | 4.2 | 2.116 | 2.116 | opened | 90 | SS 35/10 kv Igritskaya | 4+6,3 | 0.097 | 2.181 | 0 | 0 | 2.181 | 0 | 4.2 | 2.019 | 2.019 | opened
91 | SS 35/10 kv Kasilovskaya | 2,5+1 | 0.141 | 0 | 0 | 0.141 | 0 | 1.05 | 0.909 | 0.909 | opened | 91 | SS 35/10 kv Kasilovskaya | 2,5+1 | 0.008 | 0.149 | 0 | 0 | 0.149 | 0 | 1.05 | 0.901 | 0.901 | opened
92 | SS 35/10 kv Kositskaya | 2,5+2,5 | 0.3 | 0 | 0 | 0.3 | 0 | 2.625 | 2.325 | 2.325 | opened | 92 | SS 35/10 kv Kositskaya | 2,5+2,5 | 0.01 | 0.31 | 0 | 0 | 0.31 | 0 | 2.625 | 2.315 | 2.315 | opened
93 | SS 35/10 kv Krupets | 2,5+2,5 | 0.825 | 0 | 0 | 0.825 | 0 | 2.625 | 1.8 | 1.8 | opened | 93 | SS 35/10 kv Krupets | 2,5+2,5 | 0.202 | 1.027 | 0 | 0 | 1.027 | 0 | 2.625 | 1.598 | 1.598 | opened
94 | SS 35/10 kv Luna | 1,6+1,6 | 1.105 | 0 | 0 | 1.105 | 0 | 1.68 | 0.575 | 0.575 | opened | 94 | SS 35/10 kv Luna | 1,6+1,6 | 0 | 1.105 | 0 | 0 | 1.105 | 0 | 1.68 | 0.575 | 0.575 | opened
95 | SS 35/6 kv Lyubokhna | 6,3+6,3 | 6.18 | 0 | 0 | 6.18 | 0 | 6.615 | 0.435 | 0.435 | opened | 95 | SS 35/6 kv Lyubokhna | 6,3+6,3 | 0.028 | 6.208 | 0 | 0 | 6.208 | 0 | 6.615 | 0.407 | 0.407 | opened
96 | SS 35/10 kv Mareevskaya | 1,6+1,6 | 0.8 | 0 | 0 | 0.8 | 0 | 1.68 | 0.88 | 0.88 | opened | 96 | SS 35/10 kv Mareevskaya | 1,6+1,6 | 0.087 | 0.887 | 0 | 0 | 0.887 | 0 | 1.68 | 0.793 | 0.793 | opened
97 | SS 35/10 kv Nevdolsk | 1,6+1,6 | 0.212 | 0 | 0 | 0.212 | 0 | 1.68 | 1.468 | 1.468 | opened | 97 | SS 35/10 kv Nevdolsk | 1,6+1,6 | 0.005 | 0.217 | 0 | 0 | 0.217 | 0 | 1.68 | 1.463 | 1.463 | opened
98 | SS 35/10 kv Norinskaya | 4+4 | 0.6 | 0 | 0 | 0.6 | 0 | 4.2 | 3.6 | 3.6 | opened | 98 | SS 35/10 kv Norinskaya | 4+4 | 0.02 | 0.62 | 0 | 0 | 0.62 | 0 | 4.2 | 3.58 | 3.58 | opened
99 | SS 35/6 kv Paltso | 4+2,5 | 0.447 | 0 | 0 | 0.447 | 0 | 2.625 | 2.178 | 2.178 | opened | 99 | SS 35/6 kv Paltso | 4+2,5 | 0.007 | 0.454 | 0 | 0 | 0.454 | 0 | 2.625 | 2.171 | 2.171 | opened
100 | SS 35/6 kv Pobeda | 4+4 | 3.67 | 0 | 0 | 3.67 | 0 | 4.2 | 0.53 | 0.53 | opened | 100 | SS 35/6 kv Pobeda | 4+4 | 0.435 | 4.105 | 0 | 0 | 4.105 | 0 | 4.2 | 0.095 | 0.095 | opened
101 | SS 35/10 kv Pogreby | 4+4 | 1 | 0 | 0 | 1 | 0 | 4.2 | 3.2 | 3.2 | opened | 101 | SS 35/10 kv Pogreby | 4+4 | 0.057 | 1.057 | 0 | 0 | 1.057 | 0 | 4.2 | 3.143 | 3.143 | opened
102 | SS 35/10 kv Privolskaya | 2,5+1,6 | 1 | 0 | 0 | 1 | 0 | 1.68 | 0.68 | 0.68 | opened | 102 | SS 35/10 kv Privolskaya | 2,5+1,6 | 0.353 | 1.353 | 0 | 0 | 1.353 | 0 | 1.68 | 0.327 | 0.327 | opened
103 | SS 35/10 kv Rzhanitskaya | 2,5+2,5 | 0.7 | 0 | 0 | 0.7 | 0 | 2.625 | 1.925 | 1.925 | opened | 103 | SS 35/10 kv Rzhanitskaya | 2,5+2,5 | 0 | 0.7 | 0 | 0 | 0.7 | 0 | 2.625 | 1.925 | 1.925 | opened
104 | SS 35/10 kv Rognedinskaya | 4+6,3 | 1.6 | 0 | 0 | 1.6 | 0 | 4.2 | 2.6 | 2.6 | opened | 104 | SS 35/10 kv Rognedinskaya | 4+6,3 | 0.025 | 1.625 | 0 | 0 | 1.625 | 0 | 4.2 | 2.575 | 2.575 | opened
105 | SS 35/10,5 kv Ruzhnenskaya | 4+4 | 0.86 | 0 | 0 | 0.86 | 0 | 4.2 | 3.34 | 3.34 | opened | 105 | SS 35/10,5 kv Ruzhnenskaya | 4+4 | 0.01 | 0.87 | 0 | 0 | 0.87 | 0 | 4.2 | 3.33 | 3.33 | opened
106 | SS 35/10 kv Sevskaya | 6,3+6,3 | 3.8 | 0 | 0 | 3.8 | 0 | 6.615 | 2.815 | 2.815 | opened | 106 | SS 35/10 kv Sevskaya | 6,3+6,3 | 0.244 | 4.044 | 0 | 0 | 4.044 | 0 | 6.615 | 2.571 | 2.571 | opened
107 | SS 35/6 kc Seshcha | 1,6+4 | 2 | 0 | 0 | 2 | 0 | 1.68 | -0.32 | -0.32 | closed | 107 | SS 35/6 kc Seshcha | 1,6+4 | 0.076 | 2.076 | 0 | 0 | 2.076 | 0 | 1.68 | -0.396 | -0.396 | closed
108 | SS 35/6 kv Star | 10+10 | 3.84 | 0 | 0 | 3.84 | 0 | 10.5 | 6.66 | 6.66 | opened | 108 | SS 35/6 kv Star | 10+10 | 0 | 3.84 | 0 | 0 | 3.84 | 0 | 10.5 | 6.66 | 6.66 | opened
109 | SS 35/10 kv Teplovskaya | 2,5+2,5 | 0.721 | 0 | 0 | 0.721 | 0 | 2.625 | 1.904 | 1.904 | opened | 109 | SS 35/10 kv Teplovskaya | 2,5+2,5 | 0.196 | 0.917 | 0 | 0 | 0.917 | 0 | 2.625 | 1.708 | 1.708 | opened
110 | SS 35/10 kv Fedorovskaya | 1,6+1,8 | 0.584 | 0 | 0 | 0.584 | 0 | 1.68 | 1.096 | 1.096 | opened | 110 | SS 35/10 kv Fedorovskaya | 1,6+1,8 | 0.075 | 0.659 | 0 | 0 | 0.659 | 0 | 1.68 | 1.021 | 1.021 | opened
111 | SS 35/6 kv Fokinskaya | 16+16+16 | 22.62 | 0 | 0 | 22.62 | 0 | 33.6 | 10.98 | 10.98 | opened | 111 | SS 35/6 kv Fokinskaya | 16+16+16 | 1.226 | 23.846 | 0 | 0 | 23.846 | 0 | 33.6 | 9.754 | 9.754 | opened
112 | SS 35/6 kv Fosforitnaya | 6,3+5,6+16 | 8.3 | 0 | 0 | 8.3 | 0 | 12.495 | 4.195 | 4.195 | opened | 112 | SS 35/6 kv Fosforitnaya | 6,3+5,6+16 | 3.785 | 12.085 | 0 | 0 | 12.085 | 0 | 12.495 | 0.41 | 0.41 | opened
113 | SS 35/10 kv Khvoshchevskaya | 2,5+2,5 | 0.93 | 0 | 0 | 0.93 | 0 | 2.625 | 1.695 | 1.695 | opened | 113 | SS 35/10 kv Khvoshchevskaya | 2,5+2,5 | 0.062 | 0.992 | 0 | 0 | 0.992 | 0 | 2.625 | 1.633 | 1.633 | opened
114 | SS 35/10 kv Abarinskaya | 4+4 | 0.835 | 0 | 0 | 0.835 | 0 | 4.2 | 3.365 | 3.365 | opened | 114 | SS 35/10 kv Abarinskaya | 4+4 | 0.09 | 0.925 | 0 | 0 | 0.925 | 0 | 4.2 | 3.275 | 3.275 | opened
115 | SS 35/10 kv Andreykovichi | 2,5+2,5 | 0.93 | 0 | 0 | 0.93 | 0 | 2.625 | 1.695 | 1.695 | opened | 115 | SS 35/10 kv Andreykovichi | 2,5+2,5 | 0.008 | 0.938 | 0 | 0 | 0.938 | 0 | 2.625 | 1.687 | 1.687 | opened
116 | SS 35/10 kv Borshchevo | 1,6+1,6 | 1.08 | 0 | 0 | 1.08 | 0 | 1.68 | 0.6 | 0.6 | opened | 116 | SS 35/10 kv Borshchevo | 1,6+1,6 | 0.043 | 1.123 | 0 | 0 | 1.123 | 0 | 1.68 | 0.557 | 0 | opened
117 | SS 35/10 kv Vlazovichi | 2,5+1,6 | 0.5 | 0 | 0 | 0.5 | 0 | 1.68 | 1.18 | 1.18 | открыт | 117 | SS 35/10 kv Vlazovichi | 2,5+1,6 | 0.048 | 0.548 | 0 | 0 | 0.548 | 0 | 1.68 | 1.132 | 1.132 | opened
118 | SS 35/6 kv Water intake | 2,5+2,5 | 0.36 | 0 | 0 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | opened | 118 | SS 35/6 kv Water intake | 2,5+2,5 | 0 | 0.36 | 0 | 0 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | opened
119 | SS 35/10 kv Voronok | 2,5+3,2 | 1.47 | 0 | 0 | 1.47 | 0 | 2.625 | 1.155 | 1.155 | opened | 119 | SS 35/10 kv Voronok | 2,5+3,2 | 0.033 | 1.503 | 0 | 0 | 1.503 | 0 | 2.625 | 1.122 | 1.122 | opened
120 | SS 35/10 kv Gordeevka | 4+4 | 2.3 | 0 | 0 | 2.3 | 0 | 4.2 | 1.9 | 1.9 | opened | 120 | SS 35/10 kv Gordeevka | 4+4 | 0.089 | 2.389 | 0 | 0 | 2.389 | 0 | 4.2 | 1.811 | 1.811 | opened
121 | SS 35/10 kv Gridenki | 2,5+3,2 | 1.533 | 0 | 0 | 1.533 | 0 | 2.625 | 1.092 | 1.092 | opened | 121 | SS 35/10 kv Gridenki | 2,5+3,2 | 0.116 | 1.649 | 0 | 0 | 1.649 | 0 | 2.625 | 0.976 | 0.976 | opened
122 | SS 35/10 kv Zavodskaya | 4+2,5 | 1.12 | 0 | 0 | 1.12 | 0 | 2.625 | 1.505 | 1.505 | opened | 122 | SS 35/10 kv Zavodskaya | 4+2,5 | 0.005 | 1.125 | 0 | 0 | 1.125 | 0 | 2.625 | 1.5 | 1.5 | opened
123 | SS 35/10 kv Istopki | 1,6+1,6 | 1.106 | 0 | 0 | 1.106 | 0 | 1.68 | 0.574 | 0.574 | opened | 123 | SS 35/10 kv Istopki | 1,6+1,6 | 0.021 | 1.127 | 0 | 0 | 1.127 | 0 | 1.68 | 0.553 | 0.553 | opened
124 | SS 35/10 kv Katashin | 1,6+1,6 | 0.899 | 0 | 0 | 0.899 | 0 | 1.68 | 0.781 | 0.781 | opened | 124 | SS 35/10 kv Katashin | 1,6+1,6 | 0.029 | 0.928 | 0 | 0 | 0.928 | 0 | 1.68 | 0.752 | 0.752 | opened
125 | SS 35/10 kv Kivay | 2,5+2,5 | 1.931 | 0 | 0 | 1.931 | 0 | 2.625 | 0.694 | 0.694 | opened | 125 | SS 35/10 kv Kivay | 2,5+2,5 | 0.064 | 1.995 | 0 | 0 | 1.995 | 0 | 2.625 | 0.63 | 0.63 | opened
126 | SS 35/10 kv Krutoyar | 2,5+1,6 | 0.762 | 0 | 0 | 0.762 | 0 | 1.68 | 0.918 | 0.918 | opened | 126 | SS 35/10 kv Krutoyar | 2,5+1,6 | 0.052 | 0.814 | 0 | 0 | 0.814 | 0 | 1.68 | 0.866 | 0.866 | opened
127 | SS 35/10 kv Logovatoe | 2,5+1,6 | 1.329 | 0 | 0 | 1.329 | 0 | 1.68 | 0.351 | 0.351 | opened | 127 | SS 35/10 kv Logovatoe | 2,5+1,6 | 0.018 | 1.347 | 0 | 0 | 1.347 | 0 | 1.68 | 0.333 | 0.333 | opened
128 | SS 35/10 kv Lopazna | 2,5+2,5 | 0.36 | 0 | 0 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | opened | 128 | SS 35/10 kv Lopazna | 2,5+2,5 | 0.025 | 0.385 | 0 | 0 | 0.385 | 0 | 2.625 | 2.24 | 2.24 | opened
129 | SS 35/10 kv Mglinskaya | 4+4 | 3.899 | 0 | 0 | 3.899 | 0 | 4.2 | 0.301 | 0.301 | opened | 129 | SS 35/10 kv Mglinskaya | 4+4 | 0.072 | 3.971 | 0 | 0 | 3.971 | 0 | 4.2 | 0.229 | 0.229 | opened
130 | SS 35/10 kv Mishkovka | 2,5+1,6 | 0.632 | 0 | 0 | 0.632 | 0 | 1.68 | 1.048 | 1.048 | opened | 130 | SS 35/10 kv Mishkovka | 2,5+1,6 | 0.021 | 0.653 | 0 | 0 | 0.653 | 0 | 1.68 | 1.027 | 1.027 | opened
131 | SS 35/10 kv Novo-Drokov | 2,5+2,5 | 0.58 | 0 | 0 | 0.58 | 0 | 2.625 | 2.045 | 2.045 | opened | 131 | SS 35/10 kv Novo-Drokov | 2,5+2,5 | 0.017 | 0.597 | 0 | 0 | 0.597 | 0 | 2.625 | 2.028 | 2.028 | opened
132 | SS 35/10 kv Putevaya | 6,3+6,3 | 5.767 | 0 | 0 | 5.767 | 0 | 6.615 | 0.848 | 0.848 | opened | 132 | SS 35/10 kv Putevaya | 6,3+6,3 | 0.065 | 5.832 | 0 | 0 | 5.832 | 0 | 6.615 | 0.783 | 0.783 | opened
133 | SS 35/10 kv Selishchanskaya | 2,5+2,5 | 1.369 | 0 | 0 | 1.369 | 0 | 2.625 | 1.256 | 1.256 | opened | 133 | SS 35/10 kv Selishchanskaya | 2,5+2,5 | 0.121 | 1.49 | 0 | 0 | 1.49 | 0 | 2.625 | 1.135 | 1.135 | opened
134 | SS 35/10 kv Slava | 2,5+1,6 | 1.325 | 0 | 0 | 1.325 | 0 | 1.68 | 0.355 | 0.355 | opened | 134 | SS 35/10 kv Slava | 2,5+1,6 | 0.034 | 1.359 | 0 | 0 | 1.359 | 0 | 1.68 | 0.321 | 0.321 | opened
135 | SS 35/10 kv Smolevichi | 6,3+6,3 | 3.22 | 0 | 0 | 3.22 | 0 | 6.615 | 3.395 | 3.395 | opened | 135 | SS 35/10 kv Smolevichi | 6,3+6,3 | 0.114 | 3.334 | 0 | 0 | 3.334 | 0 | 6.615 | 3.281 | 3.281 | opened
136 | SS 35/10 kv Solovyevka | 1,6+1,6 | 0.45 | 0 | 0 | 0.45 | 0 | 1.68 | 1.23 | 1.23 | opened | 136 | SS 35/10 kv Solovyevka | 1,6+1,6 | 0.005 | 0.455 | 0 | 0 | 0.455 | 0 | 1.68 | 1.225 | 1.225 | opened
137 | SS 35/10 kv Sytaya Buda | 2,5+2,5 | 0.447 | 0 | 0 | 0.447 | 0 | 2.625 | 2.178 | 2.178 | opened | 137 | SS 35/10 kv Sytaya Buda | 2,5+2,5 | 0.399 | 0.846 | 0 | 0 | 0.846 | 0 | 2.625 | 1.779 | 1.779 | opened
138 | SS 35/6 kv Tembr | 4+4+3,2 | 6.93 | 0 | 0 | 6.93 | 0 | 7.56 | 0.63 | 0.63 | opened | 138 | SS 35/6 kv Tembr | 4+4+3,2 | 0.09 | 7.02 | 0 | 0 | 7.02 | 0 | 7.56 | 0.54 | 0.54 | opened
139 | SS 35/10 kv Churovichi | 2,5+4 | 0.978 | 0 | 0 | 0.978 | 0 | 2.625 | 1.647 | 1.647 | opened | 139 | SS 35/10 kv Churovichi | 2,5+4 | 0.06 | 1.038 | 0 | 0 | 1.038 | 0 | 2.625 | 1.587 | 1.587 | opened
140 | SS 35/10 kv Shcherbinichi | 2,5+2,5 | 1.03 | 0 | 0 | 1.03 | 0 | 2.625 | 1.595 | 1.595 | opened | 140 | SS 35/10 kv Shcherbinichi | 2,5+2,5 | 0.056 | 1.086 | 0 | 0 | 1.086 | 0 | 2.625 | 1.539 | 1.539 | opened
| Total: | 2292.8 | 776.924 | [8 empty] | 2: Total:; 3: 2292.8; 4: 58.848; 5: 835.788
| deficit | [8 empty] | -40.793 |  | 2: deficit; Min. 12: -55.026
| proficit | [8 empty] | 681.83 |  | 2: proficit; Min. 12: 674.001