## табл.1+табл.2
| Form of calculation of transmission capacity of Main substations of IDGC of Centre division - Kurskenergo for August 2010 - Current deficit | [11 empty] | Form of calculation of transmission capacity of Main substations of IDGC of Centre division - Kurskenergo for August 2010 - Expected deficit
[9 empty] | table 1 | [12 empty] | table 2
No. | Object of main substation, voltage class | Current deficit | [8 empty] | note | No. | Object of main substation, voltage class | Expected deficit/proficit | [9 empty] | note
|  | Installed power capacity of transformers Sуst. Including their number, pcs/ MVA | Summary total capacity of central substation following the results of measurements of load maximal Sмах , MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit /proficit of main substation, MVA |  |  |  |  | Installed power capacity of transformers Sуst. Including their number, pcs/ MVA | Additional capacity according to provided technical specifications | Expected load at main substation | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit /proficit of main substation, MVA
|  |  |  | MVA | Min. | [11 empty] | МВА | Мин.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
One-transformer substations | [11 empty] | 1: One-transformer substations
1 | SS 110/35/10 Artyukhovka | 1*6,3 | 1.64 | 6.3 | 24 hours | 6.3 | 0 | 6.3 | 4.66 | 1.2 | opened | 1 | SS 110/35/10 Artyukhovka | 1*6,3 | 0.018 | 1.658 | 6.3 | 24 hours | 6.3 | 0 | 6.3 | 4.642 | 1.189 | opened
| Nom. capacity MV, MVA | 6.3 | 1.1 | 2.3 | 24 hours | 2.3 | 0 | 2.3 | 1.2 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.011 | 1.111 | 2.3 | 24 hours | 2.3 | 0 | 2.3 | 1.189
| Nom. capacity MV, MVA | 6.3 | 0.54 | 4 | 24 hours | 4 | 0 | 4 | 3.46 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.007 | 0.547 | 4 | 24 hours | 4 | 0 | 4 | 3.453
2 | SS 110/10 Beketovo | 1*6,3 | 0.39 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.76 | 1.76 | opened | 2 | SS 110/10 Beketovo | 1*6,3 | 0.032 | 0.422 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.728 | 1.728 | opened
3 | SS 110/35/10 Besedino | 1*6,3 | 2.84 | 6.8 | 24 hours | 6.8 | 0 | 6.8 | 3.96 | 0.26 | opened | 3 | SS 110/35/10 Besedino | 1*6,3 | 0.181 | 3.021 | 6.8 | 24 hours | 6.8 | 0 | 6.8 | 3.779 | 0.112 | opened
| Nom. capacity MV, MVA | 6.3 | 0.5 | 4.2 | 24 hours | 4.2 | 0 | 4.2 | 3.7 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.033 | 0.533 | 4.2 | 24 hours | 4.2 | 0 | 4.2 | 3.667
| Nom. capacity LV, MVA | 6.3 | 2.34 | 2.6 | 24 hours | 2.6 | 0 | 2.6 | 0.26 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.148 | 2.488 | 2.6 | 24 hours | 2.6 | 0 | 2.6 | 0.112
4 | SS 110/10 Voskhod | 1*10,0 | 0.8 | 2.5 | 24 hours | 2.5 | 0 | 2.5 | 1.7 | 1.7 | opened | 4 | SS 110/10 Voskhod | 1*10,0 | 0.055 | 0.855 | 2.5 | 24 hours | 2.5 | 0 | 2.5 | 1.645 | 1.645 | opened
5 | SS 110/35/10 Zhuryatino | 1*6,3 | 0.82 | 6 | 24 hours | 6 | 0 | 6 | 5.18 | 1.48 | opened | 5 | SS 110/35/10 Zhuryatino | 1*6,3 | 0.037 | 0.857 | 6 | 24 hours | 6 | 0 | 6 | 5.143 | 1.443 | opened
| Nom. capacity MV, MVA | 6.3 | 0 | 3.7 | 24 hours | 3.7 | 0 | 3.7 | 3.7 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0 | 0 | 3.7 | 24 hours | 3.7 | 0 | 3.7 | 3.7
| Nom. capacity LV, MVA | 6.3 | 0.82 | 2.3 | 24 hours | 2.3 | 0 | 2.3 | 1.48 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.037 | 0.857 | 2.3 | 24 hours | 2.3 | 0 | 2.3 | 1.443
6 | SS 110/35/10 Zhukovka | 1*10,0 | 1.1 | 5.16 | 120 | 5.16 | 0 | 5.16 | 4.06 | 0.49 | opened | 6 | SS 110/35/10 Zhukovka | 1*10,0 | 0.091 | 1.191 | 5.16 | 120 | 5.16 | 0 | 5.16 | 3.969 | 0.49 | opened
| Nom. capacity MV, MVA | 10 | 0.93 | 4.5 | 24 hours | 4.5 | 0 | 4.5 | 3.57 |  |  |  | Nom. capacity MV, MVA | 10 | 0.091 | 1.021 | 4.5 | 24 hours | 4.5 | 0 | 4.5 | 3.479
| Nom. capacity LV, MVA | 10 | 0.17 | 0.66 | 120 | 0.66 | 0 | 0.66 | 0.49 |  |  |  | Nom. capacity LV, MVA | 10 |  | 0.17 | 0.66 | 120 | 0.66 | 0 | 0.66 | 0.49
7 | SS 110/10 Zabelye | 1*2,5 | 0.31 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.84 | 1.84 | opened | 7 | SS 110/10 Zabelye | 1*2,5 | 0.028 | 0.338 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.812 | 1.812 | opened
8 | SS 110/10 Ivnitsa | 1*6,3 | 0.4 | 0.45 | 24 hours | 0.45 | 0 | 0.45 | 0.05 | 0.05 | opened | 8 | SS 110/10 Ivnitsa | 1*6,3 |  | 0.4 | 0.45 | 24 hours | 0.45 | 0 | 0.45 | 0.05 | 0.05 | opened
9 | SS 110/35/10 Lachinovo | 1*10,0 | 1.28 | 5.13 | 24 hours | 5.13 | 0 | 5.13 | 3.85 | 1 | opened | 9 | SS 110/35/10 Lachinovo | 1*10,0 | 0.49 | 1.77 | 5.13 | 24 hours | 5.13 | 0 | 5.13 | 3.36 | 0.51 | opened
| Nom. capacity MV, MVA | 10 | 0.75 | 3.6 | 24 hours | 3.6 | 0 | 3.6 | 2.85 |  |  |  | Nom. capacity MV, MVA | 10 | 0 | 0.75 | 3.6 | 24 hours | 3.6 | 0 | 3.6 | 2.85
| Nom. capacity LV, MVA | 10 | 0.53 | 1.53 | 24 hours | 1.53 | 0 | 1.53 | 1 |  |  |  | Nom. capacity LV, MVA | 10 | 0.49 | 1.02 | 1.53 | 24 hours | 1.53 | 0 | 1.53 | 0.51
10 | SS 110/10 Malaya Loknya | 1*10,0 | 1.2 | 1.21 | 24 hours | 1.21 | 0 | 1.21 | 0.01 | 0.01 | opened | 10 | SS 110/10 Malaya Loknya | 1*10,0 |  | 1.2 | 1.21 | 24 hours | 1.21 | 0 | 1.21 | 0.01 | 0.01 | opened
11 | SS 110/35/10 Maritsa | 1*2,5 | 0.99 | 1.92 | 24 hours | 1.92 | 0 | 1.92 | 0.93 | 0.93 | opened | 11 | SS 110/35/10 Maritsa | 1*6,3 | 0.01 | 1 | 1.92 | 24 hours | 1.92 | 0 | 1.92 | 0.92 | 0.92 | opened
12 | SS 110/35/10 Raskhovets | 1 х 6,3 | 0.56 | 5.89 | 24 hours | 5.89 | 0 | 5.89 | 5.33 | 1.97 | opened | 12 | SS 110/35/10 Raskhovets | 1 х 6,3 | 0.014 | 0.574 | 5.89 | 24 hours | 5.89 | 0 | 5.89 | 5.316 | 1.97 | opened
| Nom. capacity MV, MVA | 6.3 | 0.38 | 3.74 | 24 hours | 3.74 | 0 | 3.74 | 3.36 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.014 | 0.394 | 3.74 | 24 hours | 3.74 | 0 | 3.74 | 3.346
| Nom. capacity LV, MVA | 6.3 | 0.18 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.97 |  |  |  | Nom. capacity LV, MVA | 6.3 |  | 0.18 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.97
13 | SS 110/10 Semyonovskaya | 1 х 2,5 | 0.4 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1 | 1 | opened | 13 | SS 110/10 Semyonovskaya | 1 х 2,5 | 0.003 | 0.403 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 0.997 | 1.097 | opened
14 | SS 110/6 Teplichnaya | 1 х 16,0 | 4.1 | 6.64 | 24 hours | 6.64 | 0 | 6.64 | 2.54 | 2.54 | opened | 14 | SS 110/6 Teplichnaya | 1 х 16,0 | 5.7 | 9.8 | 6.64 | 24 hours | 6.64 | 0 | 6.64 | -3.16 | -3.16 | closed
15 | SS 110/35/10 Troitskaya | 1 х 10,0 | 3.01 | 7.5 | 24 hours | 7.5 | 0 | 7.5 | 4.49 | 0.79 | opened | 15 | SS 110/35/10 Troitskaya | 1 х 10,0 | 1.613 | 4.623 | 7.5 | 24 hours | 7.5 | 0 | 7.5 | 2.877 | 0.754 | opened
| Nom. capacity MV, MVA | 10 | 2.7 | 6.4 | 24 hours | 6.4 | 0 | 6.4 | 3.7 |  |  |  | Nom. capacity MV, MVA | 10 | 1.577 | 4.277 | 6.4 | 24 hours | 6.4 | 0 | 6.4 | 2.123
| Nom. capacity LV, MVA | 10 | 0.31 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.79 |  |  |  | Nom. capacity LV, MVA | 10 | 0.036 | 0.346 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.754
16 | SS 35/10 Avtodor | 1 х 2,5 | 0.46 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.34 | 0.34 | opened | 16 | SS 35/10 Avtodor | 1 х 2,5 | 0.043 | 0.503 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.297 | 0.297 | opened
17 | SS 35/10 Agronom | 1 х 1,8 | 0.7 | 0.95 | 24 hours | 0.95 | 0 | 0.95 | 0.25 | 0.25 | opened | 17 | SS 35/10 Agronom | 1 х 1,8 | 0.195 | 0.895 | 0.95 | 24 hours | 0.95 | 0 | 0.95 | 0.055 | 0.055 | opened
18 | SS 35/10 Akimovka | 1 х 2,5 | 0.25 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.43 | 0.43 | opened | 18 | SS 35/10 Akimovka | 1 х 2,5 |  | 0.25 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.43 | 0.43 | opened
19 | SS 35/10 Alekseevka | 1 х 2,5 | 0.28 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.15 | 1.15 | opened | 19 | SS 35/10 Alekseevka | 1 х 2,5 | 0.015 | 0.295 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.135 | 1.135 | opened
20 | SS 35/10 Afanasyevka (WPS) | 1 х 4,0 | 0.55 | 1.34 | 24 hours | 1.34 | 0 | 1.34 | 0.79 | 0.79 | opened | 20 | SS 35/10 Afanasyevka (WPS) | 1 х 4,0 | 0.029 | 0.579 | 1.34 | 24 hours | 1.34 | 0 | 1.34 | 0.761 | 0.761 | opened
21 | SS 35/10 B. Gneushevo | 1 х 2,5 | 0.77 | 0.96 | 24 hours | 0.96 | 0 | 0.96 | 0.19 | 0.19 | opened | 21 | SS 35/10 B. Gneushevo | 1 х 2,5 |  | 0.77 | 0.96 | 24 hours | 0.96 | 0 | 0.96 | 0.19 | 0.19 | opened
22 | SS 35/10 B.Soldatskoe1 | 1 х 3,2 | 1 | 2.83 | 24 hours | 2.83 | 0 | 2.83 | 1.83 | 1.83 | opened | 22 | SS 35/10 B.Soldatskoe1 | 1 х 3,2 | 0.231 | 1.231 | 2.83 | 24 hours | 2.83 | 0 | 2.83 | 1.599 | 1.599 | opened
23 | SS 35/10 Banishchi | 1 х 1,6 | 0.22 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.42 | 0.42 | opened | 23 | SS 35/10 Banishchi | 1 х 1,6 | 0.015 | 0.235 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.405 | 0.405 | opened
24 | SS 35/10 Baranovo | 1 х 4,0 | 0.46 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 0.97 | 0.97 | opened | 24 | SS 35/10 Baranovo | 1 х 4,0 | 0.105 | 0.565 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 0.865 | 0.865 | opened
25 | SS 35/10 Belgorodka | 1 х 2,5 | 0.27 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.88 | 1.88 | opened | 25 | SS 35/10 Belgorodka | 1 х 2,5 | 0.015 | 0.285 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.865 | 1.865 | opened
26 | SS 35/10 Belitsa | 1 х 4,0 | 0.6 | 1.76 | 24 hours | 1.76 | 0 | 1.76 | 1.16 | 1.16 | opened | 26 | SS 35/10 Belitsa | 1 х 4,0 | 0.262 | 0.862 | 1.76 | 24 hours | 1.76 | 0 | 1.76 | 0.898 | 0.898 | opened
27 | SS 35/10 Biryukovka | 1х1,6 | 0.6 | 0.76 | 24 hours | 0.76 | 0 | 0.76 | 0.16 | 0.16 | opened | 27 | SS 35/10 Biryukovka | 1х1,6 |  | 0.6 | 0.76 | 24 hours | 0.76 | 0 | 0.76 | 0.16 | 0.16 | opened
28 | SS 35/10 Bobrovka | 1 х 1,6 | 0.24 | 0.67 | 24 hours | 0.67 | 0 | 0.67 | 0.43 | 0.43 | opened | 28 | SS 35/10 Bobrovka | 1 х 1,6 |  | 0.24 | 0.67 | 24 hours | 0.67 | 0 | 0.67 | 0.43 | 0.43 | opened
29 | SS 35/10 Bobrovo | 1 х 2,5 | 0.42 | 0.76 | 24 hours | 0.76 | 0 | 0.76 | 0.34 | 0.34 | opened | 29 | SS 35/10 Bobrovo | 1 х 2,5 |  | 0.42 | 0.76 | 24 hours | 0.76 | 0 | 0.76 | 0.34 | 0.34 | opened
30 | SS 35/10 Budki | 1 х 1,0 | 0.68 | 0.74 | 24 hours | 0.74 | 0 | 0.74 | 0.06 | 0.06 | opened | 30 | SS 35/10 Budki | 1 х 1,0 |  | 0.68 | 0.74 | 24 hours | 0.74 | 0 | 0.74 | 0.06 | 0.06 | opened
31 | SS 35/10 Bukreevka (CPS) | 1 х 1,8 | 0.59 | 1.6 | 50 | 1.6 | 0 | 1.6 | 1.01 | 1.01 | opened | 31 | SS 35/10 Bukreevka (CPS) | 1 х 1,8 | 0.037 | 0.627 | 1.6 | 50 | 1.6 | 0 | 1.6 | 0.973 | 0.973 | opened
32 | SS 35/10 Bukreevka (WPS) | 1 х 1,6 | 0.95 | 1 | 24 hours | 1 | 0 | 1 | 0.05 | 0.05 | opened | 32 | SS 35/10 Bukreevka (WPS) | 1 х 1,6 | 0.037 | 0.987 | 1 | 24 hours | 1 | 0 | 1 | 0.013 | 0.013 | opened
33 | SS 35/10 Burtsevka | 1 х 1,6 | 0.18 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.25 | 1.25 | opened | 33 | SS 35/10 Burtsevka | 1 х 1,6 | 0.04 | 0.22 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.21 | 1.21 | opened
34 | SS 35/10 Bykovo | 1 х 4,0 | 0.89 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 0.54 | 0.54 | opened | 34 | SS 35/10 Bykovo | 1 х 4,0 | 0.205 | 1.095 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 0.335 | 0.335 | opened
35 | SS 35/10 V. Shchigor | 1 х 2,5 | 0.12 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 2.03 | 2.03 | opened | 35 | SS 35/10 V. Shchigor | 1 х 2,5 |  | 0.12 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 2.03 | 2.03 | opened
36 | SS 35/10 Vanino | 1 х 2,5 | 0.41 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.39 | 0.39 | opened | 36 | SS 35/10 Vanino | 1 х 2,5 | 0.065 | 0.475 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.325 | 0.325 | opened
37 | SS 35/10 Vasilyevka | 1 х 2,5 | 0.64 | 1.05 | 24 hours | 1.05 | 0 | 1.05 | 0.41 | 0.41 | opened | 37 | SS 35/10 Vasilyevka | 1 х 2,5 | 0.035 | 0.675 | 1.05 | 24 hours | 1.05 | 0 | 1.05 | 0.375 | 0.375 | opened
38 | SS 35/10 Water storage | 1 х 4,0 | 1.58 | 2.72 | 24 hours | 2.72 | 0 | 2.72 | 1.14 | 1.14 | opened | 38 | SS 35/10 Water storage | 1 х 4,0 | 3.54 | 5.12 | 2.72 | 24 hours | 2.72 | 0 | 2.72 | -2.4 | -2.4 | closed
39 | SS 35/10 Volokonsk | 1 х 2,5 | 0.3 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.8 | 0.8 | opened | 39 | SS 35/10 Volokonsk | 1 х 2,5 |  | 0.3 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.8 | 0.8 | opened
40 | SS 35/10 Vorobyovka | 1 х 2,5 | 0.65 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.25 | 0.25 | opened | 40 | SS 35/10 Vorobyovka | 1 х 2,5 | 0.014 | 0.664 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.236 | 0.236 | opened
41 | SS 35/10 Voronok | 1 х 4,0 | 0.86 | 2.1 | 24 hours | 2.1 | 0 | 2.1 | 1.24 | 1.24 | opened | 41 | SS 35/10 Voronok | 1 х 4,0 | 0.013 | 0.873 | 2.1 | 24 hours | 2.1 | 0 | 2.1 | 1.227 | 1.227 | opened
42 | SS 35/10 Vyazovoe | 1 х 2,5 | 0.66 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.49 | 1.49 | opened | 42 | SS 35/10 Vyazovoe | 1 х 2,5 | 0.005 | 0.665 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.485 | 1.485 | opened
43 | SS 35/10 Gakhovo | 1 х 2,5 | 0.21 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1.59 | 1.59 | opened | 43 | SS 35/10 Gakhovo | 1 х 2,5 | 0.02 | 0.23 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1.57 | 1.57 | opened
44 | SS 35/10 Generalshino | 1 х 2,5 | 0.25 | 1.5 | 24 hours | 1.5 | 0 | 1.5 | 1.25 | 1.25 | opened | 44 | SS 35/10 Generalshino | 1 х 2,5 | 0.01 | 0.26 | 1.5 | 24 hours | 1.5 | 0 | 1.5 | 1.24 | 1.24 | opened
45 | SS 35/10 Glazovo | 1 х 2,5 | 0.94 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.16 | 0.16 | opened | 45 | SS 35/10 Glazovo | 1 х 2,5 | 0.02 | 0.96 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.14 | 0.14 | opened
46 | SS 35/10 Glebovo | 1 х 2,5 | 0.49 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 0.91 | 0.91 | opened | 46 | SS 35/10 Glebovo | 1 х 2,5 | 0.018 | 0.508 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 0.892 | 0.892 | opened
47 | SS 35/10 Gordeevka | 1 х 1,6 | 0.12 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.58 | 0.58 | opened | 47 | SS 35/10 Gordeevka | 1 х 1,6 | 0.07 | 0.19 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.51 | 0.51 | opened
48 | SS 35/10 Gorodensk | 1 х 1,6 | 0.59 | 0.76 | 24 hours | 0.76 | 0 | 0.76 | 0.17 | 0.17 | opened | 48 | SS 35/10 Gorodensk | 1 х 1,6 | 0.044 | 0.634 | 0.76 | 24 hours | 0.76 | 0 | 0.76 | 0.126 | 0.126 | opened
49 | SS 35/10 Goryainovo | 1 х 2,5 | 0.5 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.6 | 0.6 | opened | 49 | SS 35/10 Goryainovo | 1 х 2,5 | 0.025 | 0.525 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.575 | 0.575 | opened
50 | SS 35/10 12th State stud farm | 1 х 2,5 | 0.53 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 0.9 | 0.9 | opened | 50 | SS 35/10 12th State stud farm | 1 х 2,5 |  | 0.53 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 0.9 | 0.9 | opened
51 | SS 35/10 Grayvoronka | 1 х 2,5 | 0.5 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 0.93 | 0.93 | opened | 51 | SS 35/10 Grayvoronka | 1 х 2,5 | 0.042 | 0.542 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 0.888 | 0.888 | opened
52 | SS 35/10 Grinyovka | 1 х 2,5 | 0.28 | 2.85 | 24 hours | 2.85 | 0 | 2.85 | 2.57 | 2.57 | opened | 52 | SS 35/10 Grinyovka | 1 х 2,5 | 0.014 | 0.294 | 2.85 | 24 hours | 2.85 | 0 | 2.85 | 2.556 | 2.556 | opened
53 | SS 35/10 Gustomoy | 1 х 1,6 | 0.21 | 0.94 | 24 hours | 0.94 | 0 | 0.94 | 0.73 | 0.73 | opened | 53 | SS 35/10 Gustomoy | 1 х 1,6 | 0.009 | 0.219 | 0.94 | 24 hours | 0.94 | 0 | 0.94 | 0.721 | 0.721 | opened
54 | SS 35/10 Daryino | 1 х 2,5 | 0.4 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1.4 | 1.4 | opened | 54 | SS 35/10 Daryino | 1 х 2,5 | 0.032 | 0.432 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1.368 | 1.368 | opened
55 | SS 35/10 Demyakino | 1 х 2,5 | 0.43 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.37 | 0.37 | opened | 55 | SS 35/10 Demyakino | 1 х 2,5 | 0.04 | 0.47 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.33 | 0.33 | opened
56 | SS 35/10 Efrosimovka | 1 х 1,8 | 0.38 | 1.07 | 24 hours | 1.07 | 0 | 1.07 | 0.69 | 0.69 | opened | 56 | SS 35/10 Efrosimovka | 1 х 1,8 | 0.025 | 0.405 | 1.07 | 24 hours | 1.07 | 0 | 1.07 | 0.665 | 0.665 | opened
57 | SS 35/10 Zhdanovo | 1 х 2,5 | 0.38 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.47 | 0.47 | opened | 57 | SS 35/10 Zhdanovo | 1 х 2,5 | 0.038 | 0.418 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.432 | 0.432 | opened
58 | SS 35/10 Zashchitnoe | 1 х 1,6 | 0.32 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.83 | 1.83 | opened | 58 | SS 35/10 Zashchitnoe | 1 х 1,6 | 0.011 | 0.331 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.819 | 1.819 | opened
59 | SS 35/10 Zvannoe | 1 х 2,5 | 0.6 | 0.84 | 24 hours | 0.84 | 0 | 0.84 | 0.24 | 0.24 | opened | 59 | SS 35/10 Zvannoe | 1 х 2,5 | 0.043 | 0.643 | 0.84 | 24 hours | 0.84 | 0 | 0.84 | 0.197 | 0.197 | opened
60 | SS 35/10 Znamenka | 1 х 1,8 | 1.01 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.14 | 1.14 | opened | 60 | SS 35/10 Znamenka | 1 х 1,8 |  | 1.01 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.14 | 1.14 | opened
61 | SS 35/10 Iskra | 1 х 2,5 | 0.26 | 0.58 | 24 hours | 0.58 | 0 | 0.58 | 0.32 | 0.32 | opened | 61 | SS 35/10 Iskra | 1 х 2,5 | 0.033 | 0.293 | 0.58 | 24 hours | 0.58 | 0 | 0.58 | 0.287 | 0.287 | opened
62 | SS 35/10 Kazanka | 1 х 4,0 | 0.33 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.47 | 0.47 | opened | 62 | SS 35/10 Kazanka | 1 х 4,0 | 0.009 | 0.339 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.461 | 0.461 | opened
63 | SS 35/10 Kalinovka (new) | 1 х 2,5 | 0.18 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1.62 | 1.62 | opened | 63 | SS 35/10 Kalinovka (new) | 1 х 2,5 | 0.01 | 0.19 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1.61 | 1.61 | opened
64 | SS 35/10 Karyzh | 1 х 1,6 | 0.18 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.46 | 0.46 | opened | 64 | SS 35/10 Karyzh | 1 х 1,6 | 0.01 | 0.19 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.45 | 0.45 | opened
65 | SS 35/10 Kitaevka | 1 х 1,6 | 0.26 | 0.74 | 24 hours | 0.74 | 0 | 0.74 | 0.48 | 0.48 | opened | 65 | SS 35/10 Kitaevka | 1 х 1,6 | 0.257 | 0.517 | 0.74 | 24 hours | 0.74 | 0 | 0.74 | 0.223 | 0.223 | opened
66 | SS 35/10 Kobylki | 1 х 2,5 | 0.68 | 1.53 | 24 hours | 1.53 | 0 | 1.53 | 0.85 | 0.85 | opened | 66 | SS 35/10 Kobylki | 1 х 2,5 | 0.031 | 0.711 | 1.53 | 24 hours | 1.53 | 0 | 1.53 | 0.819 | 0.819 | opened
67 | SS 35/10 Kolontaevka | 1 х 2,5 | 0.26 | 0.84 | 24 hours | 0.84 | 0 | 0.84 | 0.58 | 0.58 | opened | 67 | SS 35/10 Kolontaevka | 1 х 2,5 |  | 0.26 | 0.84 | 24 hours | 0.84 | 0 | 0.84 | 0.58 | 0.58 | opened
68 | SS 35/10 Kondratovka | 1 х 1,8 | 0.55 | 1.42 | 24 hours | 1.42 | 0 | 1.42 | 0.87 | 0.87 | opened | 68 | SS 35/10 Kondratovka | 1 х 1,8 | 0.024 | 0.574 | 1.42 | 24 hours | 1.42 | 0 | 1.42 | 0.846 | 0.846 | opened
69 | SS 35/10 Korovyakovka | 1 х 1,6 | 0.21 | 0.76 | 24 hours | 0.76 | 0 | 0.76 | 0.55 | 0.55 | opened | 69 | SS 35/10 Korovyakovka | 1 х 1,6 | 0.017 | 0.227 | 0.76 | 24 hours | 0.76 | 0 | 0.76 | 0.533 | 0.533 | opened
70 | SS 35/10 Lezhenki | 1 х 2,5 | 0.09 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.34 | 1.34 | opened | 70 | SS 35/10 Lezhenki | 1 х 2,5 | 0.014 | 0.104 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.326 | 1.326 | opened
71 | SS 35/10 Leninskaya | 1 х 1,8 | 0.78 | 0.83 | 24 hours | 0.83 | 0 | 0.83 | 0.05 | 0.05 | opened | 71 | SS 35/10 Leninskaya | 1 х 1,8 | 0.035 | 0.815 | 0.83 | 24 hours | 0.83 | 0 | 0.83 | 0.015 | 0.015 | opened
72 | SS 35/10 Lobazovka | 1 х 2,5 | 0.86 | 1.09 | 24 hours | 1.09 | 0 | 1.09 | 0.23 | 0.23 | opened | 72 | SS 35/10 Lobazovka | 1 х 2,5 | 0.011 | 0.871 | 1.09 | 24 hours | 1.09 | 0 | 1.09 | 0.219 | 0.219 | opened
73 | SS 35/10 Lugovka | 1 х 1,6 | 0.54 | 1.29 | 24 hours | 1.29 | 0 | 1.29 | 0.75 | 0.75 | opened | 73 | SS 35/10 Lugovka | 1 х 1,6 | 0.035 | 0.575 | 1.29 | 24 hours | 1.29 | 0 | 1.29 | 0.715 | 0.715 | opened
74 | SS 35/10 Lyubava | 1 х 6,3 | 0.35 | 1.15 | 24 hours | 1.15 | 0 | 1.15 | 0.8 | 0.8 | opened | 74 | SS 35/10 Lyubava | 1 х 6,3 | 0.011 | 0.361 | 1.15 | 24 hours | 1.15 | 0 | 1.15 | 0.789 | 0.789 | opened
75 | SS 35/10 Lyubimovka-1 | 1 х 3,2 | 0 | 0.96 | 24 hours | 0.96 | 0 | 0.96 | 0.96 | 0.96 | opened | 75 | SS 35/10 Lyubimovka-1 | 1 х 3,2 | 0.041 | 0.041 | 0.96 | 24 hours | 0.96 | 0 | 0.96 | 0.919 | 0.919 | opened
76 | SS 35/10 M. Kamenets | 1 х 1,6 | 0.6 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.5 | 0.5 | opened | 76 | SS 35/10 M. Kamenets | 1 х 1,6 | 0.059 | 0.659 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.441 | 0.441 | opened
77 | SS 35/10 М. Gneushevo | 1 х 4,0 | 0.7 | 1.28 | 24 hours | 1.28 | 0 | 1.28 | 0.58 | 0.58 | opened | 77 | SS 35/10 М. Gneushevo | 1 х 4,0 | 0.015 | 0.715 | 1.28 | 24 hours | 1.28 | 0 | 1.28 | 0.565 | 0.565 | opened
78 | SS 35/10 М. Kryuki | 1 х 2,5 | 0.4 | 1.19 | 24 hours | 1.19 | 0 | 1.19 | 0.79 | 0.79 | opened | 78 | SS 35/10 М. Kryuki | 1 х 2,5 | 0.01 | 0.41 | 1.19 | 24 hours | 1.19 | 0 | 1.19 | 0.78 | 0.78 | opened
79 | SS 35/10 Markovo | 1 х 2,5 | 0.65 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.15 | 0.15 | opened | 79 | SS 35/10 Markovo | 1 х 2,5 | 0.01 | 0.66 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.14 | 0.14 | opened
80 | SS 35/10 Marmyzhi | 1 х 2,5 | 0.21 | 1.33 | 24 hours | 1.33 | 0 | 1.33 | 1.12 | 1.12 | opened | 80 | SS 35/10 Marmyzhi | 1 х 2,5 |  | 0.21 | 1.33 | 24 hours | 1.33 | 0 | 1.33 | 1.12 | 1.12 | opened
81 | SS 35/10 Melovoe | 1 х 4,0 | 0.99 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.16 | 1.16 | opened | 81 | SS 35/10 Melovoe | 1 х 4,0 | 0.013 | 1.003 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.147 | 1.147 | opened
82 | SS 35/10 Mokva | 1 х 4,0 | 0.5 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.65 | 1.65 | opened | 82 | SS 35/10 Mokva | 1 х 4,0 | 0.057 | 0.557 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.593 | 1.593 | opened
83 | SS 35/10 Mokrusheno | 1 х 1,6 | 0.6 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.5 | 0.5 | opened | 83 | SS 35/10 Mokrusheno | 1 х 1,6 | 0.026 | 0.626 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.474 | 0.474 | opened
84 | SS 35/10 Molotychi | 1 х 2,5 | 0.4 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.5 | 0.5 | opened | 84 | SS 35/10 Molotychi | 1 х 2,5 |  | 0.4 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.5 | 0.5 | opened
85 | SS 35/10 Mochaki | 1 х 2,5 | 0.03 | 1.07 | 24 hours | 1.07 | 0 | 1.07 | 1.04 | 1.04 | opened | 85 | SS 35/10 Mochaki | 1 х 2,5 |  | 0.03 | 1.07 | 24 hours | 1.07 | 0 | 1.07 | 1.04 | 1.04 | opened
86 | SS 35/10 N. Vladimirovka | 1 х 2,5 | 0.19 | 4.3 | 24 hours | 4.3 | 0 | 4.3 | 4.11 | 4.11 | opened | 86 | SS 35/10 N. Vladimirovka | 1 х 2,5 |  | 0.19 | 4.3 | 24 hours | 4.3 | 0 | 4.3 | 4.11 | 4.11 | opened
87 | SS 35/10 N. Gurovo | 1 х 4,0 | 0.73 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.42 | 1.42 | opened | 87 | SS 35/10 N. Gurovo | 1 х 4,0 | 0.008 | 0.738 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.412 | 1.412 | opened
88 | SS 35/10 Nadeyka | 1 х 2,5 | 0.16 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.24 | 1.24 | opened | 88 | SS 35/10 Nadeyka | 1 х 2,5 | 0.008 | 0.168 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.232 | 1.232 | opened
89 | SS 35/10 Niva | 1 х 2,5 | 0.5 | 1.56 | 24 hours | 1.56 | 0 | 1.56 | 1.06 | 1.06 | opened | 89 | SS 35/10 Niva | 1 х 2,5 | 0.015 | 0.515 | 1.56 | 24 hours | 1.56 | 0 | 1.56 | 1.045 | 1.045 | opened
90 | SS 35/10 Olgovka | 1 х 2,5 | 0.41 | 0.97 | 24 hours | 0.97 | 0 | 0.97 | 0.56 | 0.56 | opened | 90 | SS 35/10 Olgovka | 1 х 2,5 | 0.032 | 0.442 | 0.97 | 24 hours | 0.97 | 0 | 0.97 | 0.528 | 0.528 | opened
91 | SS 35/10 Olkhovatka | 1 х 4,0 | 0.38 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.26 | 0.26 | opened | 91 | SS 35/10 Olkhovatka | 1 х 4,0 | 0.08 | 0.46 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.18 | 0.18 | opened
92 | SS 35/10 Orositelnaya | 1 х 4,0 | 1.05 | 2.97 | 24 hours | 2.97 | 0 | 2.97 | 1.92 | 1.92 | opened | 92 | SS 35/10 Orositelnaya | 1 х 4,0 | 0.858 | 1.908 | 2.97 | 24 hours | 2.97 | 0 | 2.97 | 1.062 | 1.062 | opened
93 | SS 35/10 Peny-2 | 1 х 2,5 | 0.6 | 2.32 | 24 hours | 2.32 | 0 | 2.32 | 1.72 | 1.72 | opened | 93 | SS 35/10 Peny-2 | 1 х 2,5 | 0.41 | 1.01 | 2.32 | 24 hours | 2.32 | 0 | 2.32 | 1.31 | 1.31 | opened
94 | SS 35/10 Perestuplino (old) | 1 х 2,5 | 0.16 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.24 | 1.24 | opened | 94 | SS 35/10 Perestuplino (old) | 1 х 2,5 |  | 0.16 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.24 | 1.24 | opened
95 | SS 35/10 Perestuplino (new) | 1 х 2,5 | 0.36 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.04 | 1.04 | opened | 95 | SS 35/10 Perestuplino (new) | 1 х 2,5 |  | 0.36 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.04 | 1.04 | opened
96 | SS 35/10 Petrovo | 1 х 6,3 | 1 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.15 | 1.15 | opened | 96 | SS 35/10 Petrovo | 1 х 6,3 | 0.099 | 1.099 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.051 | 1.051 | opened
97 | SS 35/10 Petrovskaya | 1 х 2,5 | 0.03 | 0.74 | 24 hours | 0.74 | 0 | 0.74 | 0.71 | 0.71 | opened | 97 | SS 35/10 Petrovskaya | 1 х 2,5 |  | 0.03 | 0.74 | 24 hours | 0.74 | 0 | 0.74 | 0.71 | 0.71 | opened
98 | SS 35/10 Pokrovskoe | 1 х 2,5 | 0.27 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.88 | 1.88 | opened | 98 | SS 35/10 Pokrovskoe | 1 х 2,5 | 0.015 | 0.285 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.865 | 1.865 | opened
99 | SS 35/10 Prilepy | 1 х 1,6 | 0.53 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.62 | 1.62 | opened | 99 | SS 35/10 Prilepy | 1 х 1,6 | 0.009 | 0.539 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.611 | 1.611 | opened
100 | SS 35/10 Pristen | 1 х 4,0 | 2.3 | 3.3 | 24 hours | 3.3 | 0 | 3.3 | 1 | 1 | opened | 100 | SS 35/10 Pristen | 1 х 4,0 | 0.047 | 2.347 | 3.3 | 24 hours | 3.3 | 0 | 3.3 | 0.953 | 0.953 | opened
101 | SS 35/10 R. Budy 35/10 | 1 х 4,0 | 0 | 0.74 | 24 hours | 0.74 | 0 | 0.74 | 0.74 | 0.74 | opened | 101 | SS 35/10 R. Budy 35/10 | 1 х 4,0 | 0.018 | 0.018 | 0.74 | 24 hours | 0.74 | 0 | 0.74 | 0.722 | 0.722 | opened
102 | SS 35/10 Reut | 1 х 2,5 | 0.16 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.94 | 0.94 | opened | 102 | SS 35/10 Reut | 1 х 2,5 | 0.816 | 0.976 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.124 | 0.124 | opened
103 | SS 35/10 Rovenka | 1 х 1,6 | 0.16 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.27 | 1.27 | opened | 103 | SS 35/10 Rovenka | 1 х 1,6 | 0.015 | 0.175 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.255 | 1.255 | opened
104 | SS 35/10 Rodina (NPC) | 1 х 2,5 | 0.17 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.53 | 0.53 | opened | 104 | SS 35/10 Rodina (NPC) | 1 х 2,5 | 0.033 | 0.203 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.497 | 0.497 | opened
105 | SS 35/10 Rodina (EPS) | 1 х 4,0 | 0.5 | 2.3 | 24 hours | 2.3 | 0 | 2.3 | 1.8 | 1.8 | opened | 105 | SS 35/10 Rodina (EPS) | 1 х 4,0 |  | 0.5 | 2.3 | 24 hours | 2.3 | 0 | 2.3 | 1.8 | 1.8 | opened
106 | SS 35/10 Rubanshchina | 1 х 2,5 | 0.4 | 1.31 | 24 hours | 1.31 | 0 | 1.31 | 0.91 | 0.91 | opened | 106 | SS 35/10 Rubanshchina | 1 х 2,5 | 0.003 | 0.403 | 1.31 | 24 hours | 1.31 | 0 | 1.31 | 0.907 | 0.907 | opened
107 | SS 35/10 Rusanovo | 1 х 1,8 | 0.39 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.04 | 1.04 | opened | 107 | SS 35/10 Rusanovo | 1 х 1,8 | 0.024 | 0.414 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.016 | 1.016 | opened
108 | SS 35/10 Ryshkovo | 1 х 2,5 | 0.56 | 0.94 | 24 hours | 0.94 | 0 | 0.94 | 0.38 | 0.38 | opened | 108 | SS 35/10 Ryshkovo | 1 х 2,5 | 0.038 | 0.598 | 0.94 | 24 hours | 0.94 | 0 | 0.94 | 0.342 | 0.342 | opened
109 | SS 35/10 Ryazanovo | 1 х 1,6 | 0.58 | 1.15 | 24 hours | 1.15 | 0 | 1.15 | 0.57 | 0.57 | opened | 109 | SS 35/10 Ryazanovo | 1 х 1,6 | 0.009 | 0.589 | 1.15 | 24 hours | 1.15 | 0 | 1.15 | 0.561 | 0.561 | opened
110 | SS 35/10 Sazanovka | 1 х 2,5 | 0.3 | 1.25 | 24 hours | 1.25 | 0 | 1.25 | 0.95 | 0.95 | opened | 110 | SS 35/10 Sazanovka | 1 х 2,5 |  | 0.3 | 1.25 | 24 hours | 1.25 | 0 | 1.25 | 0.95 | 0.95 | opened
111 | SS 35/10 Sergievka | 1 х 2,5 | 0.4 | 2.7 | 24 hours | 2.7 | 0 | 2.7 | 2.3 | 2.3 | opened | 111 | SS 35/10 Sergievka | 1 х 2,5 | 0.009 | 0.409 | 2.7 | 24 hours | 2.7 | 0 | 2.7 | 2.291 | 2.291 | opened
112 | SS 35/10 Sokolye | 1 х 2,5 | 0.3 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.13 | 1.13 | opened | 112 | SS 35/10 Sokolye | 1 х 2,5 | 0.058 | 0.358 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.072 | 1.072 | opened
113 | SS 35/10 Solntsevo | 1 х 2,5 | 0.9 | 1.76 | 24 hours | 1.76 | 0 | 1.76 | 0.86 | 0.86 | opened | 113 | SS 35/10 Solntsevo | 1 х 2,5 | 0.09 | 0.99 | 1.76 | 24 hours | 1.76 | 0 | 1.76 | 0.77 | 0.77 | opened
114 | SS 35/10 Spasskoe | 1 х 1,6 | 0.22 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.88 | 0.88 | opened | 114 | SS 35/10 Spasskoe | 1 х 1,6 |  | 0.22 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.88 | 0.88 | opened
115 | SS 35/10 Sr. Olshanka | 1 х 2,5 | 0.3 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.1 | 1.1 | opened | 115 | SS 35/10 Sr. Olshanka | 1 х 2,5 | 0.004 | 0.304 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.096 | 1.096 | opened
116 | SS 35/10 Streletskaya | 1 х 2,5 | 0.35 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 0.95 | 0.95 | opened | 116 | SS 35/10 Streletskaya | 1 х 2,5 | 0.038 | 0.388 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 0.912 | 0.912 | opened
117 | SS 35/10 Subbotino | 1 х 2,5 | 0.6 | 1.34 | 24 hours | 1.34 | 0 | 1.34 | 0.74 | 0.74 | opened | 117 | SS 35/10 Subbotino | 1 х 2,5 | 0.015 | 0.615 | 1.34 | 24 hours | 1.34 | 0 | 1.34 | 0.725 | 0.725 | opened
118 | SS 35/10 Sukhaya | 1 х 1,6 | 0.44 | 0.71 | 24 hours | 0.71 | 0 | 0.71 | 0.27 | 0.27 | opened | 118 | SS 35/10 Sukhaya | 1 х 1,6 | 0.009 | 0.449 | 0.71 | 24 hours | 0.71 | 0 | 0.71 | 0.261 | 0.261 | opened
119 | SS 35/10 Telmana | 1 х 2,5 | 0.3 | 1.15 | 24 hours | 1.15 | 0 | 1.15 | 0.85 | 0.85 | opened | 119 | SS 35/10 Telmana | 1 х 2,5 | 0.009 | 0.309 | 1.15 | 24 hours | 1.15 | 0 | 1.15 | 0.841 | 0.841 | opened
120 | SS 35/10 Terebuzh | 1 х 2,5 | 0.46 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 0.97 | 0.97 | opened | 120 | SS 35/10 Terebuzh | 1 х 2,5 | 0.035 | 0.495 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 0.935 | 0.935 | opened
121 | SS 35/10 Fateevka | 1 х 2,5 | 0.08 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.62 | 0.62 | opened | 121 | SS 35/10 Fateevka | 1 х 2,5 | 0.008 | 0.088 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.612 | 0.612 | opened
122 | SS 35/10 Fentisovo | 1 х 1,6 | 0.17 | 1.72 | 24 hours | 1.72 | 0 | 1.72 | 1.55 | 1.55 | opened | 122 | SS 35/10 Fentisovo | 1 х 1,6 | 0.021 | 0.191 | 1.72 | 24 hours | 1.72 | 0 | 1.72 | 1.529 | 1.529 | opened
123 | SS 35/10 Chapaevskaya | 1 х 2,5 | 0.2 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.9 | 0.9 | opened | 123 | SS 35/10 Chapaevskaya | 1 х 2,5 | 0.017 | 0.217 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.883 | 0.883 | opened
124 | SS 35/10 Chemerki | 1 х 1,6 | 0.06 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.79 | 0.79 | opened | 124 | SS 35/10 Chemerki | 1 х 1,6 |  | 0.06 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.79 | 0.79 | opened
125 | SS 35/10 Chizhovka | 1 х 1,6 | 0.35 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.08 | 1.08 | opened | 125 | SS 35/10 Chizhovka | 1 х 1,6 | 0.033 | 0.383 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.047 | 1.047 | opened
126 | SS 35/10 Shatilovka | 1 х 2,5 | 0.16 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.27 | 1.27 | opened | 126 | SS 35/10 Shatilovka | 1 х 2,5 | 0.019 | 0.179 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.251 | 1.251 | opened
127 | SS 35/10 Sheptukhovka | 1 х 2,5 | 0.75 | 1.47 | 24 hours | 1.47 | 0 | 1.47 | 0.72 | 0.72 | opened | 127 | SS 35/10 Sheptukhovka | 1 х 2,5 | 0.013 | 0.763 | 1.47 | 24 hours | 1.47 | 0 | 1.47 | 0.707 | 0.707 | opened
128 | SS 35/10 Shuklino | 1 х 2,5 | 0.25 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.6 | 0.6 | opened | 128 | SS 35/10 Shuklino | 1 х 2,5 |  | 0.25 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.6 | 0.6 | opened
129 | SS 35/10 Elevator | 1х6,3 | 0.31 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0.29 | 0.29 | opened | 129 | SS 35/10 Elevator | 1х6,3 | 0.015 | 0.325 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0.275 | 0.275 | opened
130 | SS 35/10 Yankovo | 1 х 1,6 | 0.25 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.39 | 0.39 | opened | 130 | SS 35/10 Yankovo | 1 х 1,6 |  | 0.25 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.39 | 0.39 | opened
131 | SS 35/10 Yasenki | 1 х 2,5 | 0.48 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.67 | 1.67 | opened | 131 | SS 35/10 Yasenki | 1 х 2,5 | 0.038 | 0.518 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.632 | 1.632 | opened
Two- and more transformer substations | [11 empty] | 1: Two- and more transformer substations
1 | SS 110/6 Akkumulyatornaya | 2*25 | 10.47 | 0 | 0 | 10.47 | 0 | 26.25 | 15.78 | 15.78 | opened | 1 | SS 110/6 Akkumulyatornaya | 2*25 |  | 10.47 | 0 | 0 | 10.47 | 0 | 26.25 | 15.78 | 15.78 | opened
2 | SS 110/10 ARZ | 6,3+10,0 | 2.62 | 0.9 | 45 | 1.72 | 0 | 6.615 | 4.895 | 4.895 | opened | 2 | SS 110/10 ARZ | 6,3+10,0 |  | 2.62 | 0.9 | 45 | 1.72 | 0 | 6.615 | 4.895 | 4.895 | opened
3 | SS 110/35/10 Atomgrad | 2*25 | 13.07 | 20.2 | 120 | -7.13 | 0 | 26.25 | 33.38 | 26.02 | opened | 3 | SS 110/35/10 Atomgrad | 2*25 | 0.251 | 13.321 | 20.2 | 120 | -6.879 | 0 | 26.25 | 33.129 | 25.938 | opened
| Nom. capacity MV, MVA | 25 | 3.334 | 10.6 | 120 | -7.266 | 0 | 26.25 | 33.516 |  |  |  | Nom. capacity MV, MVA | 25 | 0.169 | 3.503 | 10.6 | 120 | -7.097 | 0 | 26.25 | 33.347
| Nom. capacity lV, MVA | 25 | 9.83 | 9.6 | 120 | 0.23 | 0 | 26.25 | 26.02 |  |  |  | Nom. capacity lV, MVA | 25 | 0.082 | 9.912 | 9.6 | 120 | 0.312 | 0 | 26.25 | 25.938
4 | SS 110/10 B. Zhirovo | 2*6,3 | 0.36 | 0.6 | 120 | -0.24 | 0 | 6.615 | 6.855 | 6.855 | opened | 4 | SS 110/10 B. Zhirovo | 2*6,3 |  | 0.36 | 0.6 | 120 | -0.24 | 0 | 6.615 | 6.855 | 6.855 | opened
5 | SS 110/35/10 Basovo | 5,6+10,0 | 1.19 | 6.19 | 15 | -5 | 0 | 5.88 | 10.88 | 5.38 | opened | 5 | SS 110/35/10 Basovo | 5,6+10,0 | 0.023 | 1.213 | 6.19 | 15 | -4.977 | 0 | 5.88 | 10.857 | 5.368 | opened
| Nom. capacity MV, MVA | 5,6+10,0 | 0.5 | 6 |  | -5.5 | 0 | 5.88 | 11.38 |  |  |  | Nom. capacity MV, MVA | 5,6+10,0 | 0.011 | 0.511 | 6 |  | -5.489 | 0 | 5.88 | 11.369
| Nom. capacity LV, MVA | 5,6+10,0 | 0.69 | 0.19 | 120 | 0.5 | 0 | 5.88 | 5.38 |  |  |  | Nom. capacity LV, MVA | 5,6+10,0 | 0.012 | 0.702 | 0.19 | 120 | 0.512 | 0 | 5.88 | 5.368
6 | SS 110/35/10 Belaya | 2*16,0 | 8.4 | 12 | 120 | -3.6 | 0 | 16.8 | 20.4 | 13.4 | opened | 6 | SS 110/35/10 Belaya | 2*16,0 | 1.145 | 9.545 | 12 | 120 | -2.455 | 0 | 16.8 | 19.255 | 12.678 | opened
| Nom. capacity MV, MVA | 16 | 3.4 | 0 |  | 3.4 | 0 | 16.8 | 13.4 |  |  |  | Nom. capacity MV, MVA | 16 | 0.722 | 4.122 | 0 |  | 4.122 | 0 | 16.8 | 12.678
| Nom. capacity LV, MVA | 16 | 5 | 12 | 120 | -7 | 0 | 16.8 | 23.8 |  |  |  | Nom. capacity LV, MVA | 16 | 0.423 | 5.423 | 12 | 120 | -6.577 | 0 | 16.8 | 23.377
7 | SS 110/35/10 Bobryshovo | 2*6,3 | 1.2 | 1.3 | 120 | -0.1 | 0 | 6.615 | 6.715 | 6.015 | opened | 7 | SS 110/35/10 Bobryshovo | 2*6,3 | 0.041 | 1.241 | 1.3 | 120 | -0.059 | 0 | 6.615 | 6.674 | 6.011 | opened
| Nom. capacity MV, MVA | 6.3 | 0.6 |  |  | 0.6 | 0 | 6.615 | 6.015 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.004 | 0.604 |  |  | 0.604 | 0 | 6.615 | 6.011
| Nom. capacity LV, MVA | 6.3 | 0.65 | 1.3 | 120 | -0.65 | 0 | 6.615 | 7.265 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.037 | 0.687 | 1.3 | 120 | -0.613 | 0 | 6.615 | 7.228
8 | SS 110/10 Vinnikovo | 2,5+6,3 | 2.31 | 1.17 | 45 | 1.14 | 0 | 2.625 | 1.485 | 1.485 | opened | 8 | SS 110/10 Vinnikovo | 2,5+6,3 | 0.05 | 2.36 | 1.17 | 45 | 1.19 | 0 | 2.625 | 1.435 | 1.435 | opened
9 | SS 110/35/6 Volokno | 40,0+2*40,5 | 37.58 | 16.8 | 0 | 20.78 | 0 | 84.525 | 63.745 | 61.275 | opened | 9 | SS 110/35/6 Volokno | 40,0+2*40,5 | 1.543 | 39.123 | 16.8 | 0 | 22.323 | 0 | 84.525 | 62.202 | 61.191 | opened
| Nom. capacity MV, MVA | 40,0+2*40,5 | 14.33 | 16.8 | 0 | -2.47 | 0 | 84.525 | 86.995 |  |  |  | Nom. capacity MV, MVA | 40,0+2*40,5 | 1.459 | 15.789 | 16.8 | 0 | -1.011 | 0 | 84.525 | 85.536
| Nom. capacity MV, MVA | 40,0+2*40,5 | 23.25 | 0 | 0 | 23.25 | 0 | 84.525 | 61.275 |  |  |  | Nom. capacity MV, MVA | 40,0+2*40,5 | 0.084 | 23.334 | 0 | 0 | 23.334 | 0 | 84.525 | 61.191
10 | SS 110/10 Vysokaya* | 2*16,0 | 28.27 | 3.2 | 15 | 25.07 | 0 | 16.8 | -8.27 | -8.27 | opened | 10 | SS 110/10 Vysokaya | 2*16,0 |  | 28.27 | 3.2 | 15 | 25.07 | 0 | 16.8 | -8.27 | -8.27 | closed
11 | SS 110/35/10 Glushkovo | 2*10,0 | 8.7 | 8.04 | 120 | 0.66 | 0 | 10.5 | 9.84 | 8.44 | opened | 11 | SS 110/35/10 Glushkovo | 2*10,0 | 0.5615 | 9.2615 | 8.04 | 120 | 1.2215 | 0 | 10.5 | 9.2785 | 8.4345 | opened
| Nom. capacity MV, MVA | 10 | 5.2 | 6.6 | 120 | -1.4 | 0 | 10.5 | 11.9 |  |  |  | Nom. capacity MV, MVA | 10 | 0.556 | 5.756 | 6.6 | 120 | -0.844 | 0 | 10.5 | 11.344
| Nom. capacity LV, MVA | 10 | 3.5 | 1.44 | 80 | 2.06 | 0 | 10.5 | 8.44 |  |  |  | Nom. capacity LV, MVA | 10 | 0.0055 | 3.5055 | 1.44 | 80 | 2.0655 | 0 | 10.5 | 8.4345
12 | SS 110/10 Gorodskaya | 2*25,0 | 10.4 | 0 | 0 | 10.4 | 0 | 26.25 | 15.85 | 15.85 | opened | 12 | SS 110/10 Gorodskaya | 2*25,0 | 4.53 | 14.93 | 0 | 0 | 14.93 | 0 | 26.25 | 11.32 | 11.32 | opened
13 | SS 110/35/10 Gorshechnoe | 10+16,0 | 9.41 | 6.52 | 120 | 2.89 | 0 | 10.5 | 7.61 | 6.25 | opened | 13 | SS 110/35/10 Gorshechnoe | 10+16,0 | 0.743 | 10.153 | 6.52 | 120 | 3.633 | 0 | 10.5 | 6.867 | 5.821 | opened
| Nom. capacity MV, MVA | 10+16,0 | 6.13 | 6.06 |  | 0.07 | 0 | 10.5 | 10.43 |  |  |  | Nom. capacity MV, MVA | 10+16,0 | 0.314 | 6.444 | 6.06 |  | 0.384 | 0 | 10.5 | 10.116
| Nom. capacity LV, MVA | 10+16,0 | 4.71 | 0.46 | 120 | 4.25 | 0 | 10.5 | 6.25 |  |  |  | Nom. capacity LV, MVA | 10+16,0 | 0.429 | 5.139 | 0.46 | 120 | 4.679 | 0 | 10.5 | 5.821
14 | SS 110/35/10 Dmitriev | 2*10,0 | 7.09 | 10.4 | 120 | -3.31 | 0 | 10.5 | 13.81 | 8.43 | opened | 14 | SS 110/35/10 Dmitriev | 2*10,0 | 0.235 | 7.325 | 10.4 | 120 | -3.075 | 0 | 10.5 | 13.575 | 8.219 | opened
| Nom. capacity MV, MVA | 10 | 2.02 | 7.4 |  | -5.38 | 0 | 10.5 | 15.88 |  |  |  | Nom. capacity MV, MVA | 10 | 0.024 | 2.044 | 7.4 |  | -5.356 | 0 | 10.5 | 15.856
| Nom. capacity LV, MVA | 10 | 5.07 | 3 | 80 | 2.07 | 0 | 10.5 | 8.43 |  |  |  | Nom. capacity LV, MVA | 10 | 0.211 | 5.281 | 3 | 80 | 2.281 | 0 | 10.5 | 8.219
15 | SS 110/6 Dolgie Budy | 2*10,0 | 0.8 | 0.5 | 120 | 0.3 | 0 | 10.5 | 10.2 | 10.2 | opened | 15 | SS 110/6 Dolgie Budy | 2*10,0 | 0.017 | 0.817 | 0.5 | 120 | 0.317 | 0 | 10.5 | 10.183 | 10.183 | opened
16 | SS 110/35/10 Zolotukhino | 2*25,0 | 6.76 | 22.1 | 80 | -15.34 | 0 | 26.25 | 41.59 | 25.59 | opened | 16 | SS 110/35/10 Zolotukhino | 2*25,0 | 0.33 | 7.09 | 22.1 | 80 | -15.01 | 0 | 26.25 | 41.26 | 25.358 | opened
| Nom. capacity MV, MVA | 25 | 2.8 | 18.8 |  | -16 | 0 | 26.25 | 42.25 |  |  |  | Nom. capacity MV, MVA | 25 | 0.098 | 2.898 | 18.8 |  | -15.902 | 0 | 26.25 | 42.152
| Nom. capacity LV, MVA | 25 | 3.96 | 3.3 | 120 | 0.66 | 0 | 26.25 | 25.59 |  |  |  | Nom. capacity LV, MVA | 25 | 0.232 | 4.192 | 3.3 | 120 | 0.892 | 0 | 26.25 | 25.358
17 | SS 110/35/10 Kamyshi | 2*6,3 | 8.59 | 5.45 | 20 | 3.14 | 0 | 6.615 | 3.475 | 3.065 | opened | 17 | SS 110/35/10 Kamyshi | 2*6,3 | 4.124 | 12.714 | 5.45 | 20 | 7.264 | 0 | 6.615 | -0.649 | -0.97 | closed
| Nom. capacity MV, MVA | 6.3 | 7 | 3.45 |  | 3.55 | 0 | 6.615 | 3.065 |  |  |  | Nom. capacity MV, MVA | 6.3 | 4.035 | 11.035 | 3.45 |  | 7.585 | 0 | 6.615 | -0.97
| Nom. capacity LV, MVA | 6.3 | 1.732 | 2 | 20 | -0.268 | 0 | 6.615 | 6.883 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.089 | 1.821 | 2 | 20 | -0.179 | 0 | 6.615 | 6.794
18 | SS 110/35/10 Kastornoe | 15,0+16,0 | 14.13 | 6.97 | 120 | 7.16 | 0 | 15.75 | 8.59 | 8.59 | opened | 18 | SS 110/35/10 Kastornoe | 15,0+16,0 | 0.46 | 14.59 | 6.97 | 120 | 7.62 | 0 | 15.75 | 8.13 | 8.13 | opened
| Nom. capacity MV, MVA | 15,0+16,0 | 10.63 | 6.6 |  | 4.03 | 0 | 15.75 | 11.72 |  |  |  | Nom. capacity MV, MVA | 15,0+16,0 | 0.362 | 10.992 | 6.6 |  | 4.392 | 0 | 15.75 | 11.358
| Nom. capacity LV, MVA | 15,0+16,0 | 3.5 | 0.37 | 120 | 3.13 | 0 | 15.75 | 12.62 |  |  |  | Nom. capacity LV, MVA | 15,0+16,0 | 0.098 | 3.598 | 0.37 | 120 | 3.228 | 0 | 15.75 | 12.522
19 | SS 110/35/10 Kilikino | 2*16,0 | 2.53 | 6.9 | 120 | -4.37 | 0 | 16.8 | 21.17 | 18.51 | opened | 19 | SS 110/35/10 Kilikino | 2*16,0 | 0.071 | 2.601 | 6.9 | 120 | -4.299 | 0 | 16.8 | 21.099 | 18.51 | opened
| Nom. capacity MV, MVA | 16 | 2.34 | 5 |  | -2.66 | 0 | 16.8 | 19.46 |  |  |  | Nom. capacity MV, MVA | 16 | 0.071 | 2.411 | 5 |  | -2.589 | 0 | 16.8 | 19.389
| Nom. capacity LV, MVA | 16 | 0.19 | 1.9 | 120 | -1.71 | 0 | 16.8 | 18.51 |  |  |  | Nom. capacity LV, MVA | 16 |  | 0.19 | 1.9 | 120 | -1.71 | 0 | 16.8 | 18.51
20 | SS 110/35/6 Kirovskaya | 2*40,0 | 53.66 | 16.36 | 120 | 37.3 | 0 | 42 | 4.7 | 4.7 | opened | 20 | SS 110/35/6 Kirovskaya | 2*40,0 | 2.57 | 56.23 | 16.36 | 120 | 39.87 | 0 | 42 | 2.13 | 2.13 | opened
| Nom. capacity MV, MVA | 40 | 26.67 | 13.06 | 120 | 13.61 | 0 | 42 | 28.39 |  |  |  | Nom. capacity MV, MVA | 40 |  | 26.67 | 13.06 | 120 | 13.61 | 0 | 42 | 28.39
| Nom. capacity LV, MVA | 40 | 26.99 | 3.3 | 120 | 23.69 | 0 | 42 | 18.31 |  |  |  | Nom. capacity LV, MVA | 40 | 2.57 | 29.56 | 3.3 | 120 | 26.26 | 0 | 42 | 15.74
21 | SS 110/35/10 Klyukva | 2*16,0 | 3.28 | 1.2 | 120 | 2.08 | 0 | 16.8 | 14.72 | 14.72 | opened | 21 | SS 110/35/10 Klyukva | 2*16,0 | 0.385 | 3.665 | 1.2 | 120 | 2.465 | 0 | 16.8 | 14.335 | 14.335 | opened
| Nom. capacity MV, MVA | 16 | 0 |  |  | 0 | 0 | 16.8 | 16.8 |  |  | 2: Nom. capacity MV, MVA; 3: 16; 5: 0; Мин. 8: 0; Мин. 9: 0; Мин. 10: 16.8; Мин. 11: 16.8
| Nom. capacity LV, MVA | 16 | 3.28 | 1.2 | 120 | 2.08 | 0 | 16.8 | 14.72 |  |  |  | Nom. capacity LV, MVA | 16 | 0.385 | 3.665 | 1.2 | 120 | 2.465 | 0 | 16.8 | 14.335
22 | SS 110/10 Kompressornaya | 2*40,0 | 1.11 | 0 | 0 | 1.11 | 0 | 42 | 40.89 | 40.89 | opened | 22 | SS 110/10 Kompressornaya | 2*40,0 |  | 1.11 | 0 | 0 | 1.11 | 0 | 42 | 40.89 | 40.89 | opened
23 | SS 110/35/10 Konyshevka | 10,0+16,0 | 9.06 | 8 | 120 | 1.06 | 0 | 10.5 | 9.44 | 9.44 | opened | 23 | SS 110/35/10 Konyshevka | 10,0+16,0 | 1.1 | 10.16 | 8 | 120 | 2.16 | 0 | 10.5 | 8.34 | 8.34 | opened
| Nom. capacity MV, MVA | 10,0+16,0 | 6.94 | 5.9 |  | 1.04 | 0 | 10.5 | 9.46 |  |  |  | Nom. capacity MV, MVA | 10,0+16,0 | 0.111 | 7.051 | 5.9 |  | 1.151 | 0 | 10.5 | 9.349
| Nom. capacity LV, MVA | 10,0+16,0 | 2.12 | 2.1 |  | 0.02 | 0 | 10.5 | 10.48 |  |  |  | Nom. capacity LV, MVA | 10,0+16,0 | 0.989 | 3.109 | 2.1 |  | 1.009 | 0 | 10.5 | 9.491
24 | SS 110/10 Kotelnaya | 10,0+25,0 | 7.8 | 2.1 | 0 | 5.7 | 0 | 10.5 | 4.8 | 4.8 | opened | 24 | SS 110/10 Kotelnaya | 10,0+25,0 | 3.621 | 11.421 | 2.1 | 0 | 9.321 | 0 | 10.5 | 1.179 | 1.179 | opened
25 | SS 110/35/10 Kshen | 2*10,0 | 8.73 | 6.63 | 10 | 2.1 | 0 | 10.5 | 8.4 | 6.59 | opened | 25 | SS 110/35/10 Kshen | 2*10,0 | 1.91 | 10.64 | 6.63 | 10 | 4.01 | 0 | 10.5 | 6.49 | 5.108 | opened
| Nom. capacity MV, MVA | 10 | 4.25 | 6.06 |  | -1.81 | 0 | 10.5 | 12.31 |  |  |  | Nom. capacity MV, MVA | 10 | 0.428 | 4.678 | 6.06 |  | -1.382 | 0 | 10.5 | 11.882
| Nom. capacity LV, MVA | 10 | 4.48 | 0.57 | 120 | 3.91 | 0 | 10.5 | 6.59 |  |  |  | Nom. capacity LV, MVA | 10 | 1.482 | 5.962 | 0.57 | 120 | 5.392 | 0 | 10.5 | 5.108
26 | SS 110/6 Lesnaya | 2*40,0 | 2.37 | 0 | 0 | 2.37 | 0 | 42 | 39.63 | 39.63 | opened | 26 | SS 110/6 Lesnaya | 2*40,0 | 0.9 | 3.27 | 0 | 0 | 3.27 | 0 | 42 | 38.73 | 38.73 | opened
27 | SS 110/35/10 Lgov | 2*25,0 | 13.14 | 4 | 120 | 9.14 | 0 | 26.25 | 17.11 | 17.11 | opened | 27 | SS 110/35/10 Lgov | 2*25,0 | 0.345 | 13.485 | 4 | 120 | 9.485 | 0 | 26.25 | 16.765 | 16.765 | opened
| Nom. capacity MV, MVA | 25 | 1.66 |  |  | 1.66 | 0 | 26.25 | 24.59 |  |  |  | Nom. capacity MV, MVA | 25 | 0 | 1.66 |  |  | 1.66 | 0 | 26.25 | 24.59
| Nom. capacity LV, MVA | 25 | 11.48 | 4 | 120 | 7.48 | 0 | 26.25 | 18.77 |  |  |  | Nom. capacity LV, MVA | 25 | 0.345 | 11.825 | 4 | 120 | 7.825 | 0 | 26.25 | 18.425
28 | SS 110/35/10 Lukashevka | 2*16,0 | 8.27 | 10.6 | 120 | -2.33 | 0 | 16.8 | 19.13 | 17.03 | opened | 28 | SS 110/35/10 Lukashevka | 2*16,0 | 0.085 | 8.355 | 10.6 | 120 | -2.245 | 0 | 16.8 | 19.045 | 16.945 | opened
| Nom. capacity MV, MVA | 16 | 5.07 | 5.3 |  | -0.23 | 0 | 16.8 | 17.03 |  |  |  | Nom. capacity MV, MVA | 16 | 0.085 | 5.155 | 5.3 |  | -0.145 | 0 | 16.8 | 16.945
| Nom. capacity LV, MVA | 16 | 3.2 | 5.3 | 120 | -2.1 | 0 | 16.8 | 18.9 |  |  |  | Nom. capacity LV, MVA | 16 |  | 3.2 | 5.3 | 120 | -2.1 | 0 | 16.8 | 18.9
29 | SS 110/35/10 Lyubostan | 6,3+10,0 | 5.6 | 13.1 | 120 | -7.5 | 0 | 6.615 | 14.115 | 7.285 | opened | 29 | SS 110/35/10 Lyubostan | 6,3+10,0 | 0.138 | 5.738 | 13.1 | 120 | -7.362 | 0 | 6.615 | 13.977 | 7.276 | opened
| Nom. capacity MV, MVA | 6,3+10,0 | 5 | 11.8 |  | -6.8 | 0 | 6.615 | 13.415 |  |  |  | Nom. capacity MV, MVA | 6,3+10,0 | 0.129 | 5.129 | 11.8 |  | -6.671 | 0 | 6.615 | 13.286
| Nom. capacity LV, MVA | 6,3+10,0 | 0.63 | 1.3 |  | -0.67 | 0 | 6.615 | 7.285 |  |  |  | Nom. capacity LV, MVA | 6,3+10,0 | 0.009 | 0.639 | 1.3 |  | -0.661 | 0 | 6.615 | 7.276
30 | SS 110/35/6 Manturovo | 2*16,0 | 6.58 | 9.35 | 10 | -2.77 | 0 | 16.8 | 19.57 | 16.86 | opened | 30 | SS 110/35/6 Manturovo | 2*16,0 | 0.45 | 7.03 | 9.35 | 10 | -2.32 | 0 | 16.8 | 19.12 | 16.835 | opened
| Nom. capacity MV, MVA | 16 | 6.38 | 9.09 |  | -2.71 | 0 | 16.8 | 19.51 |  |  |  | Nom. capacity MV, MVA | 16 | 0.425 | 6.805 | 9.09 |  | -2.285 | 0 | 16.8 | 19.085
| Nom. capacity LV, MVA | 16 | 0.2 | 0.26 | 120 | -0.06 | 0 | 16.8 | 16.86 |  |  |  | Nom. capacity LV, MVA | 16 | 0.025 | 0.225 | 0.26 | 120 | -0.035 | 0 | 16.8 | 16.835
31 | SS 110/35/10 8th Marta | 6,3+10,0 | 7.07 | 9.6 | 120 | -2.53 | 0 | 6.615 | 9.145 | 7.405 | opened | 31 | SS 110/35/10 8th Marta | 6,3+10,0 | 3.972 | 11.042 | 9.6 | 120 | 1.442 | 0 | 6.615 | 5.173 | 3.442 | opened
| Nom. capacity MV, MVA | 6,3+10,0 | 5.81 | 6.6 | 120 | -0.79 | 0 | 6.615 | 7.405 |  |  |  | Nom. capacity MV, MVA | 6,3+10,0 | 3.963 | 9.773 | 6.6 | 120 | 3.173 | 0 | 6.615 | 3.442
| Nom. capacity LV, MVA | 6,3+10,0 | 1.26 | 3 | 45 | -1.74 | 0 | 6.615 | 8.355 |  |  |  | Nom. capacity LV, MVA | 6,3+10,0 | 0.009 | 1.269 | 3 | 45 | -1.731 | 0 | 6.615 | 8.346
32 | SS 110/10 Martovskaya | 2*6,3 | 0.74 | 0.55 | 120 | 0.19 | 0 | 6.615 | 6.425 | 6.425 | opened | 32 | SS 110/10 Martovskaya | 2*6,3 | 0.288 | 1.028 | 0.55 | 120 | 0.478 | 0 | 6.615 | 6.137 | 6.137 | opened
33 | SS 110/35/10 Maryino | 10,0+25,0 | 6.15 | 8.11 | 120 | -1.96 | 0 | 10.5 | 12.46 | 11.27 | opened | 33 | SS 110/35/10 Maryino | 10,0+25,0 | 0.109 | 6.259 | 8.11 | 120 | -1.851 | 0 | 10.5 | 12.351 | 11.25 | opened
| Nom. capacity MV, MVA | 10,0+25,0 | 3.71 | 4.9 |  | -1.19 | 0 | 10.5 | 11.69 |  |  |  | Nom. capacity MV, MVA | 10,0+25,0 | 0.089 | 3.799 | 4.9 |  | -1.101 | 0 | 10.5 | 11.601
| Nom. capacity LV, MVA | 10,0+25,0 | 2.44 | 3.21 |  | -0.77 | 0 | 10.5 | 11.27 |  |  |  | Nom. capacity LV, MVA | 10,0+25,0 | 0.02 | 2.46 | 3.21 |  | -0.75 | 0 | 10.5 | 11.25
34 | SS 110/35/10 Medvenka | 2*10,0 | 5.95 | 19.22 | 120 | -13.27 | 0 | 10.5 | 23.77 | 8.74 | opened | 34 | SS 110/35/10 Medvenka | 2*10,0 | 0.446 | 6.396 | 19.22 | 120 | -12.824 | 0 | 10.5 | 23.324 | 8.605 | opened
| Nom. capacity MV, MVA | 10 | 2.07 | 17.1 |  | -15.03 | 0 | 10.5 | 25.53 |  |  |  | Nom. capacity MV, MVA | 10 | 0.311 | 2.381 | 17.1 |  | -14.719 | 0 | 10.5 | 25.219
| Nom. capacity LV, MVA | 10 | 3.88 | 2.12 | 120 | 1.76 | 0 | 10.5 | 8.74 |  |  |  | Nom. capacity LV, MVA | 10 | 0.135 | 4.015 | 2.12 | 120 | 1.895 | 0 | 10.5 | 8.605
35 | SS 110/6 Neftyanaya | 2*10,0 | 0.28 |  |  | 0.28 | 0 | 10.5 | 10.22 | 10.22 | opened | 35 | SS 110/6 Neftyanaya | 2*10,0 |  | 0.28 |  |  | 0.28 | 0 | 10.5 | 10.22 | 10.22 | opened
36 | SS 110/35/10 Oboyan | 16,0 + 25,0 | 16.1 | 26.86 | 120 | -10.76 | 0 | 16.8 | 27.56 | 12.16 | opened | 36 | SS 110/35/10 Oboyan | 16,0 + 25,0 | 1.031 | 17.131 | 26.86 | 120 | -9.729 | 0 | 16.8 | 26.529 | 11.19 | opened
| Nom. capacity MV, MVA | 16,0 + 25,0 | 2 | 17.4 | 0 | -15.4 | 0 | 16.8 | 32.2 |  |  |  | Nom. capacity MV, MVA | 16,0 + 25,0 | 0.061 | 2.061 | 17.4 | 0 | -15.339 | 0 | 16.8 | 32.139
| Nom. capacity LV, MVA | 16,0 + 25,0 | 14.1 | 9.46 |  | 4.64 | 0 | 16.8 | 12.16 |  |  |  | Nom. capacity LV, MVA | 16,0 + 25,0 | 0.97 | 15.07 | 9.46 |  | 5.61 | 0 | 16.8 | 11.19
37 | SS 110/35/10 Oktyabrskaya | 2 х 16,0 | 8.62 | 15.5 | 120 | -6.88 | 0 | 16.8 | 23.68 | 14.72 | opened | 37 | SS 110/35/10 Oktyabrskaya | 2 х 16,0 | 0.392 | 9.012 | 15.5 | 120 | -6.488 | 0 | 16.8 | 23.288 | 14.437 | opened
| Nom. capacity MV, MVA | 16 | 5.54 | 14.5 |  | -8.96 | 0 | 16.8 | 25.76 |  |  |  | Nom. capacity MV, MVA | 16 | 0.109 | 5.649 | 14.5 |  | -8.851 | 0 | 16.8 | 25.651
| Nom. capacity LV, MVA | 16 | 3.08 | 1 | 120 | 2.08 | 0 | 16.8 | 14.72 |  |  |  | Nom. capacity LV, MVA | 16 | 0.283 | 3.363 | 1 | 120 | 2.363 | 0 | 16.8 | 14.437
38 | SS 110/35/10 Olkhovka | 2 х 6,3 | 1.92 | 6.31 | 120 | -4.39 | 0 | 6.615 | 11.005 | 7.705 | opened | 38 | SS 110/35/10 Olkhovka | 2 х 6,3 | 0.052 | 1.972 | 6.31 | 120 | -4.338 | 0 | 6.615 | 10.953 | 7.686 | opened
| Nom. capacity MV, MVA | 6.3 | 1.7 | 5 | 120 | -3.3 | 0 | 6.615 | 9.915 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.033 | 1.733 | 5 | 120 | -3.267 | 0 | 6.615 | 9.882
| Nom. capacity LV, MVA | 6.3 | 0.22 | 1.31 | 120 | -1.09 | 0 | 6.615 | 7.705 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.019 | 0.239 | 1.31 | 120 | -1.071 | 0 | 6.615 | 7.686
39 | SS 110/10 Paniki | 2 х 2,5 | 0.79 | 0.1 | 120 | 0.69 | 0 | 2.625 | 1.935 | 1.935 | opened | 39 | SS 110/10 Paniki | 2 х 2,5 |  | 0.79 | 0.1 | 120 | 0.69 | 0 | 2.625 | 1.935 | 1.935 | opened
40 | SS 110/35/10 Peny | 2 х 16,0 | 9.63 | 6.9 | 120 | 2.73 | 0 | 16.8 | 14.07 | 14.07 | opened | 40 | SS 110/35/10 Peny | 2 х 16,0 | 0.179 | 9.809 | 6.9 | 120 | 2.909 | 0 | 16.8 | 13.891 | 13.891 | opened
| Nom. capacity MV, MVA | 16 | 4.37 | 3.5 |  | 0.87 | 0 | 16.8 | 15.93 |  |  |  | Nom. capacity MV, MVA | 16 | 0.159 | 4.529 | 3.5 |  | 1.029 | 0 | 16.8 | 15.771
| Nom. capacity LV, MVA | 16 | 5.26 | 3.4 | 120 | 1.86 | 0 | 16.8 | 14.94 |  |  |  | Nom. capacity LV, MVA | 16 | 0.02 | 5.28 | 3.4 | 120 | 1.88 | 0 | 16.8 | 14.92
41 | SS 110/35/10 Pribor | 2 х 25,0 | 32.12 | 6.5 | 0 | 25.62 | 0 | 26.25 | 0.63 | 0.63 | opened | 41 | SS 110/35/10 Pribor | 2 х 25,0 | 0 | 32.12 | 6.5 | 0 | 25.62 | 0 | 26.25 | 0.63 | 0.63 | opened
| Nom. capacity MV, MVA | 25 | 0 |  |  | 0 | 0 | 26.25 | 26.25 |  |  | 2: Nom. capacity MV, MVA; 3: 25; 5: 0; Мин. 8: 0; Мин. 9: 0; Мин. 10: 26.25; Мин. 11: 26.25
| Nom. capacity LV, MVA | 25 | 32.12 | 6.5 | 0 | 25.62 | 0 | 26.25 | 0.63 |  |  |  | Nom. capacity LV, MVA | 25 |  | 32.12 | 6.5 | 0 | 25.62 | 0 | 26.25 | 0.63
42 | SS 110/10 Progress | 2 х 63,0 | 23.2 | 0 | 0 | 23.2 | 0 | 66.15 | 42.95 | 42.95 | opened | 42 | SS 110/10 Progress | 2 х 63,0 |  | 23.2 | 0 | 0 | 23.2 | 0 | 66.15 | 42.95 | 42.95 | opened
43 | SS 110/10 Poultry plant | 6,3 + 10,0 | 5.92 | 0 | 0 | 5.92 | 0 | 6.615 | 0.695 | 0.695 | opened | 43 | SS 110/10 Poultry plant | 6,3 + 10,0 |  | 5.92 | 0 | 0 | 5.92 | 0 | 6.615 | 0.695 | 0.695 | opened
44 | SS 110/35/10 R. Budy | 2 х 10,0 | 3.4 | 15.7 | 120 | -12.3 | 0 | 10.5 | 22.8 | 15.5 | opened | 44 | SS 110/35/10 R. Budy | 2 х 10,0 | 0.007 | 3.407 | 15.7 | 120 | -12.293 | 0 | 10.5 | 22.793 | 15.493 | opened
| Nom. capacity MV, MVA | 10 | 2 | 9.3 |  | -7.3 | 0 | 10.5 | 17.8 |  |  |  | Nom. capacity MV, MVA | 10 | 0 | 2 | 9.3 |  | -7.3 | 0 | 10.5 | 17.8
| Nom. capacity LV, MVA | 10 | 1.4 | 6.4 |  | -5 | 0 | 10.5 | 15.5 |  |  |  | Nom. capacity LV, MVA | 10 | 0.007 | 1.407 | 6.4 |  | -4.993 | 0 | 10.5 | 15.493
45 | SS 110/35/10 Razinkovo | 6,3 + 10,0 | 2.9 | 21.4 | 45 | -18.5 | 0 | 6.615 | 25.115 | 9.005 | opened | 45 | SS 110/35/10 Razinkovo | 6,3 + 10,0 | 1.515 | 4.415 | 21.4 | 45 | -16.985 | 0 | 6.615 | 23.6 | 8.907 | opened
| Nom. capacity MV, MVA | 6,3 + 10,0 | 1.95 | 17.8 |  | -15.85 | 0 | 6.615 | 22.465 |  |  |  | Nom. capacity MV, MVA | 6,3 + 10,0 | 1.417 | 3.367 | 17.8 |  | -14.433 | 0 | 6.615 | 21.048
| Nom. capacity LV, MVA | 6,3 + 10,0 | 1.21 | 3.6 | 45 | -2.39 | 0 | 6.615 | 9.005 |  |  |  | Nom. capacity LV, MVA | 6,3 + 10,0 | 0.098 | 1.308 | 3.6 | 45 | -2.292 | 0 | 6.615 | 8.907
46 | SS 110/35/10 Rudnaya | 2 х 31,5 | 20.09 | 3.25 | 10 | 16.84 | 0 | 33.075 | 16.235 | 16.235 | opened | 46 | SS 110/35/10 Rudnaya | 2 х 31,5 | 0.554 | 20.644 | 3.25 | 10 | 17.394 | 0 | 33.075 | 15.681 | 15.681 | opened
| Nom. capacity MV, MVA | 31.5 | 14.23 | 1.7 |  | 12.53 | 0 | 33.075 | 20.545 |  |  |  | Nom. capacity MV, MVA | 31.5 | 0.536 | 14.766 | 1.7 |  | 13.066 | 0 | 33.075 | 20.009
| Nom. capacity LV, MVA | 31.5 | 5.86 | 1.55 | 120 | 4.31 | 0 | 33.075 | 28.765 |  |  |  | Nom. capacity LV, MVA | 31.5 | 0.018 | 5.878 | 1.55 | 120 | 4.328 | 0 | 33.075 | 28.747
47 | SS 110/35/10 Rylsk | 16,0 + 25,0 | 18.95 | 11 | 120 | 7.95 | 0 | 16.8 | 8.85 | 8.85 | opened | 47 | SS 110/35/10 Rylsk | 16,0 + 25,0 | 4.243 | 23.193 | 11 | 120 | 12.193 | 0 | 16.8 | 4.607 | 4.607 | opened
| Nom. capacity MV, MVA | 16,0 + 25,0 | 12.9 | 7 |  | 5.9 | 0 | 16.8 | 10.9 |  |  |  | Nom. capacity MV, MVA | 16,0 + 25,0 | 4.185 | 17.085 | 7 |  | 10.085 | 0 | 16.8 | 6.715
| Nom. capacity LV, MVA | 16,0 + 25,0 | 6.05 | 4 | 120 | 2.05 | 0 | 16.8 | 14.75 |  |  |  | Nom. capacity LV, MVA | 16,0 + 25,0 | 0.058 | 6.108 | 4 | 120 | 2.108 | 0 | 16.8 | 14.692
48 | SS 110/10 Solovyinaya | 2 х 25,0 | 6.91 | 0 | 0 | 6.91 | 0 | 26.25 | 19.34 | 19.34 | opened | 48 | SS 110/10 Solovyinaya | 2 х 25,0 |  | 6.91 | 0 | 0 | 6.91 | 0 | 26.25 | 19.34 | 19.34 | opened
49 | SS 110/10 STK | 2 х 10,0 | 1.19 | 0 | 0 | 1.19 | 0 | 10.5 | 9.31 | 9.31 | opened | 49 | SS 110/10 STK | 2 х 10,0 |  | 1.19 | 0 | 0 | 1.19 | 0 | 10.5 | 9.31 | 9.31 | opened
50 | SS 110/10 Studenok | 2 х 6,3 | 3.62 | 0.7 | 120 | 2.92 | 0 | 6.615 | 3.695 | 3.695 | opened | 50 | SS 110/10 Studenok | 2 х 6,3 | 0.117 | 3.737 | 0.7 | 120 | 3.037 | 0 | 6.615 | 3.578 | 3.578 | opened
51 | SS 110/35/10 Sudzha | 2 х 25,0 | 16.5 | 29 | 120 | -12.5 | 0 | 26.25 | 38.75 | 28.05 | opened | 51 | SS 110/35/10 Sudzha | 2 х 25,0 | 1.309 | 17.809 | 29 | 120 | -11.191 | 0 | 26.25 | 37.441 | 27.25 | opened
| Nom. capacity MV, MVA | 25 | 6.4 | 17.1 |  | -10.7 | 0 | 26.25 | 36.95 |  |  |  | Nom. capacity MV, MVA | 25 | 0.509 | 6.909 | 17.1 |  | -10.191 | 0 | 26.25 | 36.441
| Nom. capacity LV, MVA | 25 | 10.1 | 11.9 |  | -1.8 | 0 | 26.25 | 28.05 |  |  |  | Nom. capacity LV, MVA | 25 | 0.8 | 10.9 | 11.9 |  | -1 | 0 | 26.25 | 27.25
52 | SS 110/35/10 Schyotmash | 2 х 25,0 | 13.6 | 0 | 0 | 13.6 | 0 | 26.25 | 12.65 | 12.65 | opened | 52 | SS 110/35/10 Schyotmash | 2 х 25,0 | 6.661 | 20.261 | 0 | 0 | 20.261 | 0 | 26.25 | 5.989 | 5.989 | opened
| Nom. capacity MV, MVA | 25 | 3.9 |  |  | 3.9 | 0 | 26.25 | 22.35 |  |  |  | Nom. capacity MV, MVA | 25 | 1.161 | 5.061 |  |  | 5.061 | 0 | 26.25 | 21.189
| Nom. capacity LV, MVA | 25 | 9.7 | 0 | 0 | 9.7 | 0 | 26.25 | 16.55 |  |  |  | Nom. capacity LV, MVA | 25 | 5.5 | 15.2 | 0 | 0 | 15.2 | 0 | 26.25 | 11.05
53 | SS 110/35/10 Tyotkino | 2 х 10,0 | 5.51 | 3.44 | 120 | 2.07 | 0 | 10.5 | 8.43 | 7.63 | opened | 53 | SS 110/35/10 Tyotkino | 2 х 10,0 | 0.059 | 5.569 | 3.44 | 120 | 2.129 | 0 | 10.5 | 8.371 | 7.588 | opened
| Nom. capacity MV, MVA | 10 | 1.2 | 2 |  | -0.8 | 0 | 10.5 | 11.3 |  |  |  | Nom. capacity MV, MVA | 10 | 0.017 | 1.217 | 2 |  | -0.783 | 0 | 10.5 | 11.283
| Nom. capacity LV, MVA | 10 | 4.31 | 1.44 |  | 2.87 | 0 | 10.5 | 7.63 |  |  |  | Nom. capacity LV, MVA | 10 | 0.042 | 4.352 | 1.44 |  | 2.912 | 0 | 10.5 | 7.588
54 | SS 110/35/10 Tim | 6,3 + 16,0 | 5.7 | 9.59 | 120 | -3.89 | 0 | 6.615 | 10.505 | 5.015 | opened | 54 | SS 110/35/10 Tim | 6,3 + 16,0 | 0.462 | 6.162 | 9.59 | 120 | -3.428 | 0 | 6.615 | 10.043 | 4.922 | opened
| Nom. capacity MV, MVA | 6,3 + 16,0 | 3.6 | 9.09 |  | -5.49 | 0 | 6.615 | 12.105 |  |  |  | Nom. capacity MV, MVA | 6,3 + 16,0 | 0.369 | 3.969 | 9.09 |  | -5.121 | 0 | 6.615 | 11.736
| Nom. capacity LV, MVA | 6,3 + 16,0 | 2.1 | 0.5 | 120 | 1.6 | 0 | 6.615 | 5.015 |  |  |  | Nom. capacity LV, MVA | 6,3 + 16,0 | 0.093 | 2.193 | 0.5 | 120 | 1.693 | 0 | 6.615 | 4.922
55 | SS 110/35/10 Uyutnoe | 10,0 + 16,0 | 1.01 | 0.5 | 120 | 0.51 | 0 | 10.5 | 9.99 | 9.83 | opened | 55 | SS 110/35/10 Uyutnoe | 10,0 + 16,0 | 0.038 | 1.048 | 0.5 | 120 | 0.548 | 0 | 10.5 | 9.952 | 9.822 | opened
| Nom. capacity MV, MVA | 10,0 + 16,0 | 0.67 |  |  | 0.67 | 0 | 10.5 | 9.83 |  |  |  | Nom. capacity MV, MVA | 10,0 + 16,0 | 0.008 | 0.678 |  |  | 0.678 | 0 | 10.5 | 9.822
| Nom. capacity LV, MVA | 10,0 + 16,0 | 0.34 | 0.5 | 120 | -0.16 | 0 | 10.5 | 10.66 |  |  |  | Nom. capacity LV, MVA | 10,0 + 16,0 | 0.03 | 0.37 | 0.5 | 120 | -0.13 | 0 | 10.5 | 10.63
56 | SS 110/35/10 Fatezh | 2 х 16,0 | 6.32 | 17.4 | 120 | -11.08 | 0 | 16.8 | 27.88 | 17.08 | opened | 56 | SS 110/35/10 Fatezh | 2 х 16,0 | 2.475 | 8.795 | 17.4 | 120 | -8.605 | 0 | 16.8 | 25.405 | 16.955 | opened
| Nom. capacity MV, MVA | 16 | 2 | 12.8 |  | -10.8 | 0 | 16.8 | 27.6 |  |  |  | Nom. capacity MV, MVA | 16 | 2.35 | 4.35 | 12.8 |  | -8.45 | 0 | 16.8 | 25.25
| Nom. capacity LV, MVA | 16 | 4.32 | 4.6 | 120 | -0.28 | 0 | 16.8 | 17.08 |  |  |  | Nom. capacity LV, MVA | 16 | 0.125 | 4.445 | 4.6 | 120 | -0.155 | 0 | 16.8 | 16.955
57 | SS 110/35/10 Fosforitnaya | 2 х 25,0 | 5.44 | 12.34 | 120 | -6.9 | 0 | 26.25 | 33.15 | 24.41 | opened | 57 | SS 110/35/10 Fosforitnaya | 2 х 25,0 | 0.239 | 5.679 | 12.34 | 120 | -6.661 | 0 | 26.25 | 32.911 | 24.36 | opened
| Nom. capacity MV, MVA | 25 | 3.38 | 12.12 |  | -8.74 | 0 | 26.25 | 34.99 |  |  |  | Nom. capacity MV, MVA | 25 | 0.189 | 3.569 | 12.12 |  | -8.551 | 0 | 26.25 | 34.801
| Nom. capacity LV, MVA | 25 | 2.06 | 0.22 | 10 | 1.84 | 0 | 26.25 | 24.41 |  |  |  | Nom. capacity LV, MVA | 25 | 0.05 | 2.11 | 0.22 | 10 | 1.89 | 0 | 26.25 | 24.36
58 | SS 110/35/10 Khomutovka | 7,5 + 10,0 | 5.69 | 6.3 | 80 | -0.61 | 0 | 7.875 | 8.485 | 5.315 | opened | 58 | SS 110/35/10 Khomutovka | 7,5 + 10,0 | 0.151 | 5.841 | 6.3 | 80 | -0.459 | 0 | 7.875 | 8.334 | 5.191 | opened
| Nom. capacity MV, MVA | 7,5 + 10,0 | 0.73 | 3.9 |  | -3.17 | 0 | 7.875 | 11.045 |  |  |  | Nom. capacity MV, MVA | 7,5 + 10,0 | 0.027 | 0.757 | 3.9 |  | -3.143 | 0 | 7.875 | 11.018
| Nom. capacity LV, MVA | 7,5 + 10,0 | 4.96 | 2.4 | 80 | 2.56 | 0 | 7.875 | 5.315 |  |  |  | Nom. capacity LV, MVA | 7,5 + 10,0 | 0.124 | 5.084 | 2.4 | 80 | 2.684 | 0 | 7.875 | 5.191
59 | SS 110/35/10 Cheremisinovo | 2 х 16,0 | 6.15 | 9.38 | 10 | -3.23 | 0 | 16.8 | 20.03 | 15.06 | opened | 59 | SS 110/35/10 Cheremisinovo | 2 х 16,0 | 0.403 | 6.553 | 9.38 | 10 | -2.827 | 0 | 16.8 | 19.627 | 14.846 | opened
| Nom. capacity MV, MVA | 16 | 4.12 | 9.09 |  | -4.97 | 0 | 16.8 | 21.77 |  |  |  | Nom. capacity MV, MVA | 16 | 0.189 | 4.309 | 9.09 |  | -4.781 | 0 | 16.8 | 21.581
| Nom. capacity LV, MVA | 16 | 2.03 | 0.29 | 120 | 1.74 | 0 | 16.8 | 15.06 |  |  |  | Nom. capacity LV, MVA | 16 | 0.214 | 2.244 | 0.29 | 120 | 1.954 | 0 | 16.8 | 14.846
60 | SS 110/35/10 Cheremoshki | 2 х 6,3 | 3.34 | 8.25 | 120 | -4.91 | 0 | 6.615 | 11.525 | 7.085 | opened | 60 | SS 110/35/10 Cheremoshki | 2 х 6,3 | 0.064 | 3.404 | 8.25 | 120 | -4.846 | 0 | 6.615 | 11.461 | 7.08 | opened
| Nom. capacity MV, MVA | 6.3 | 2.56 | 7 |  | -4.44 | 0 | 6.615 | 11.055 |  |  |  | Nom. capacity MV, MVA | 6.3 | 0.059 | 2.619 | 7 |  | -4.381 | 0 | 6.615 | 10.996
| Nom. capacity LV, MVA | 6.3 | 0.78 | 1.25 | 129 | -0.47 | 0 | 6.615 | 7.085 |  |  |  | Nom. capacity LV, MVA | 6.3 | 0.005 | 0.785 | 1.25 | 129 | -0.465 | 0 | 6.615 | 7.08
61 | SS 110/35/10 Shumakovo | 2 х 10,0 | 4.4 | 13.73 | 120 | -9.33 | 0 | 10.5 | 19.83 | 12.03 | opened | 61 | SS 110/35/10 Shumakovo | 2 х 10,0 | 0.355 | 4.755 | 13.73 | 120 | -8.975 | 0 | 10.5 | 19.475 | 11.938 | opened
| Nom. capacity MV, MVA | 10 | 3.8 | 11.2 |  | -7.4 | 0 | 10.5 | 17.9 |  |  |  | Nom. capacity MV, MVA | 10 | 0.263 | 4.063 | 11.2 |  | -7.137 | 0 | 10.5 | 17.637
| Nom. capacity LV, MVA | 10 | 1 | 2.53 | 120 | -1.53 | 0 | 10.5 | 12.03 |  |  |  | Nom. capacity LV, MVA | 10 | 0.092 | 1.092 | 2.53 | 120 | -1.438 | 0 | 10.5 | 11.938
62 | SS 110/35/10 Shchigry | 2 х 25,0 | 11.28 | 12.9 | 120 | -1.62 | 0 | 26.25 | 27.87 | 21.3 | opened | 62 | SS 110/35/10 Shchigry | 2 х 25,0 | 0.582 | 11.862 | 12.9 | 120 | -1.038 | 0 | 26.25 | 27.288 | 21.091 | opened
| Nom. capacity MV, MVA | 25 | 5.55 | 12.12 |  | -6.57 | 0 | 26.25 | 32.82 |  |  |  | Nom. capacity MV, MVA | 25 | 0.373 | 5.923 | 12.12 |  | -6.197 | 0 | 26.25 | 32.447
| Nom. capacity LV, MVA | 25 | 5.73 | 0.78 | 120 | 4.95 | 0 | 26.25 | 21.3 |  |  |  | Nom. capacity LV, MVA | 25 | 0.209 | 5.939 | 0.78 | 120 | 5.159 | 0 | 26.25 | 21.091
63 | SS 110/35/10 Yastrebovka | 7,5 + 10,0 | 2.56 | 6.31 | 10 | -3.75 | 0 | 7.875 | 11.625 | 6.94 | opened | 63 | SS 110/35/10 Yastrebovka | 7,5 + 10,0 | 0.235 | 2.795 | 6.31 | 10 | -3.515 | 0 | 7.875 | 11.39 | 6.89 | opened
| Nom. capacity MV, MVA | 7,5 + 10,0 | 1.38 | 6.06 |  | -4.68 | 0 | 7.88 | 12.56 |  |  |  | Nom. capacity MV, MVA | 7,5 + 10,0 | 0.185 | 1.565 | 6.06 |  | -4.495 | 0 | 7.88 | 12.375
| Nom. capacity LV, MVA | 7,5 + 10,0 | 1.19 | 0.25 | 10 | 0.94 | 0 | 7.88 | 6.94 |  |  |  | Nom. capacity LV, MVA | 7,5 + 10,0 | 0.05 | 1.24 | 0.25 | 10 | 0.99 | 0 | 7.88 | 6.89
64 | SS 35/10 Amosovka | 2 х 2,5 | 0.42 | 0.2 | 120 | 0.22 | 0 | 2.625 | 2.405 | 2.405 | opened | 64 | SS 35/10 Amosovka | 2 х 2,5 | 0.008 | 0.428 | 0.2 | 120 | 0.228 | 0 | 2.625 | 2.397 | 2.397 | opened
65 | SS 35/10 Afanasyevka (SPS) | 1,6 + 2,5 | 0.5 | 0.37 | 120 | 0.13 | 0 | 1.68 | 1.55 | 1.55 | opened | 65 | SS 35/10 Afanasyevka (SPS) | 1,6 + 2,5 |  | 0.5 | 0.37 | 120 | 0.13 | 0 | 1.68 | 1.55 | 1.55 | opened
66 | SS 35/10 B.Soldatskoe 2 | 2 х 4,0 | 1.4 | 1.1 | 80 | 0.3 | 0 | 4.2 | 3.9 | 3.9 | opened | 66 | SS 35/10 B.Soldatskoe 2 | 2 х 4,0 |  | 1.4 | 1.1 | 80 | 0.3 | 0 | 4.2 | 3.9 | 3.9 | opened
67 | SS 35/10 B.Zmeinets | 2 х 1,6 | 0.23 | 1.43 | 120 | -1.2 | 0 | 1.68 | 2.88 | 2.88 | opened | 67 | SS 35/10 B.Zmeinets | 2 х 1,6 | 0.05 | 0.28 | 1.43 | 120 | -1.15 | 0 | 1.68 | 2.83 | 2.83 | opened
68 | SS 35/10 Bezlesnaya | 2 х 4,0 | 1.26 | 6.1 | 0 | -4.84 | 0 | 4.2 | 9.04 | 9.04 | opened | 68 | SS 35/10 Bezlesnaya | 2 х 4,0 | 0.253 | 1.513 | 6.1 | 0 | -4.587 | 0 | 4.2 | 8.787 | 8.787 | opened
69 | SS 35/10 Bereza | 1,0 + 2,5 | 0.49 | 0.15 | 120 | 0.34 | 0 | 1.05 | 0.71 | 0.71 | opened | 69 | SS 35/10 Bereza | 1,0 + 2,5 | 0.016 | 0.506 | 0.15 | 120 | 0.356 | 0 | 1.05 | 0.694 | 0.694 | opened
70 | SS 35/10 Blagodat | 2,5 + 4,0 | 0.99 | 0.29 | 120 | 0.7 | 0 | 2.625 | 1.925 | 1.925 | opened | 70 | SS 35/10 Blagodat | 2,5 + 4,0 | 0.076 | 1.066 | 0.29 | 120 | 0.776 | 0 | 2.625 | 1.849 | 1.849 | opened
71 | SS 35/10 Bykanovo | 2 х 2,5 | 0.5 | 0.41 | 120 | 0.09 | 0 | 2.625 | 2.535 | 2.535 | opened | 71 | SS 35/10 Bykanovo | 2 х 2,5 | 0.029 | 0.529 | 0.41 | 120 | 0.119 | 0 | 2.625 | 2.506 | 2.506 | opened
72 | SS 35/10 V. Lyubazh | 4,0 + 10,0 | 1.17 | 0.4 | 120 | 0.77 | 0 | 4.2 | 3.43 | 3.43 | opened | 72 | SS 35/10 V. Lyubazh | 4,0 + 10,0 | 0.55 | 1.72 | 0.4 | 120 | 1.32 | 0 | 4.2 | 2.88 | 2.88 | opened
73 | SS 35/10 Vesyoloe | 2 х 1,6 | 0.8 | 0.22 | 120 | 0.58 | 0 | 1.68 | 1.1 | 1.1 | opened | 73 | SS 35/10 Vesyoloe | 2 х 1,6 | 0.453 | 1.253 | 0.22 | 120 | 1.033 | 0 | 1.68 | 0.647 | 0.647 | opened
74 | SS 35/10 Volobuevka | 2,5 + 4,0 | 0.57 | 0.46 | 120 | 0.11 | 0 | 2.625 | 2.515 | 2.515 | opened | 74 | SS 35/10 Volobuevka | 2,5 + 4,0 | 0.044 | 0.614 | 0.46 | 120 | 0.154 | 0 | 2.625 | 2.471 | 2.471 | opened
75 | SS 35/10 Voropaevo | 2 х 4,0 | 0.87 | 0 | 0 | 0.87 | 0 | 4.2 | 3.33 | 3.33 | opened | 75 | SS 35/10 Voropaevo | 2 х 4,0 | 0.025 | 0.895 | 0 | 0 | 0.895 | 0 | 4.2 | 3.305 | 3.305 | opened
76 | SS 35/10 Vostochnaya | 2 х 6,3 | 4.13 | 0.46 | 120 | 3.67 | 0 | 6.615 | 2.945 | 2.945 | opened | 76 | SS 35/10 Vostochnaya | 2 х 6,3 | 0.189 | 4.319 | 0.46 | 120 | 3.859 | 0 | 6.615 | 2.756 | 2.756 | opened
77 | SS 35/10 Vygornoe | 2 х 2,5 | 1.22 | 0.51 | 120 | 0.71 | 0 | 2.625 | 1.915 | 1.915 | opened | 77 | SS 35/10 Vygornoe | 2 х 2,5 | 0.145 | 1.365 | 0.51 | 120 | 0.855 | 0 | 2.625 | 1.77 | 1.77 | opened
78 | SS 35/10 Gastomlya | 2 х 1,6 | 0.3 | 0.17 | 120 | 0.13 | 0 | 1.68 | 1.55 | 1.55 | opened | 78 | SS 35/10 Gastomlya | 2 х 1,6 | 0.009 | 0.309 | 0.17 | 120 | 0.139 | 0 | 1.68 | 1.541 | 1.541 | opened
79 | SS 35/10 Gorodok | 2 х 4,0 | 1.6 | 0.7 | 45 | 0.9 | 0 | 4.2 | 3.3 | 3.3 | opened | 79 | SS 35/10 Gorodok | 2 х 4,0 |  | 1.6 | 0.7 | 45 | 0.9 | 0 | 4.2 | 3.3 | 3.3 | opened
80 | SS 35/10 Guevo | 2 х 2,5 | 1.2 | 1.69 | 20 | -0.49 | 0 | 2.625 | 3.115 | 3.115 | opened | 80 | SS 35/10 Guevo | 2 х 2,5 | 0.04 | 1.24 | 1.69 | 20 | -0.45 | 0 | 2.625 | 3.075 | 3.075 | opened
81 | SS 35/10 Dolzhenkovo | 2 х 1,6 | 0.4 | 0.38 | 120 | 0.02 | 0 | 1.68 | 1.66 | 1.66 | opened | 81 | SS 35/10 Dolzhenkovo | 2 х 1,6 | 0.042 | 0.442 | 0.38 | 120 | 0.062 | 0 | 1.68 | 1.618 | 1.618 | opened
82 | SS 35/6 Dukhovets | 2,5 + 4,0 | 3.33 | 3.5 | 0 | -0.17 | 0 | 2.625 | 2.795 | 2.795 | opened | 82 | SS 35/6 Dukhovets | 2,5 + 4,0 | 0.115 | 3.445 | 3.5 | 0 | -0.055 | 0 | 2.625 | 2.68 | 2.68 | opened
83 | SS 35/10 Zhernovets | 2 х 2,5 | 0.4 | 0.26 | 120 | 0.14 | 0 | 2.625 | 2.485 | 2.485 | opened | 83 | SS 35/10 Zhernovets | 2 х 2,5 | 0.005 | 0.405 | 0.26 | 120 | 0.145 | 0 | 2.625 | 2.48 | 2.48 | opened
84 | SS 35/6 Zapadnaya | 2 х 10,0 | 12.57 | 2.5 | 0 | 10.07 | 0 | 10.5 | 0.43 | 0.43 | opened | 84 | SS 35/6 Zapadnaya | 2 х 10,0 | 0.01 | 12.58 | 2.5 | 0 | 10.08 | 0 | 10.5 | 0.42 | 0.42 | opened
85 | SS 35/10 Zolotukhinskaya KRS | 2 х 4,0 | 1.1 | 1.67 | 0 | -0.57 | 0 | 4.2 | 4.77 | 4.77 | opened | 85 | SS 35/10 Zolotukhinskaya KRS | 2 х 4,0 | 0.625 | 1.725 | 1.67 | 0 | 0.055 | 0 | 4.2 | 4.145 | 4.145 | opened
86 | SS 35/10 Zuevka | 1,6 + 2,5 | 0.9 | 0.93 | 45 | -0.03 | 0 | 1.68 | 1.71 | 1.71 | opened | 86 | SS 35/10 Zuevka | 1,6 + 2,5 | 0.109 | 1.009 | 0.93 | 45 | 0.079 | 0 | 1.68 | 1.601 | 1.601 | opened
87 | SS 35/10 Ivanino | 2 х 6,3 | 2.19 | 2.69 | 80 | -0.5 | 0 | 6.615 | 7.115 | 7.115 | opened | 87 | SS 35/10 Ivanino | 2 х 6,3 | 0.077 | 2.267 | 2.69 | 80 | -0.423 | 0 | 6.615 | 7.038 | 7.038 | opened
88 | SS 35/10 Kalinovka | 1,8 + 2,5 | 0.68 | 0.5 | 120 | 0.18 | 0 | 1.89 | 1.71 | 1.71 | opened | 88 | SS 35/10 Kalinovka | 1,8 + 2,5 |  | 0.68 | 0.5 | 120 | 0.18 | 0 | 1.89 | 1.71 | 1.71 | opened
89 | SS 35/10 Kirilovka | 2 х 1,6 | 0.29 | 0.52 | 120 | -0.23 | 0 | 1.68 | 1.91 | 1.91 | opened | 89 | SS 35/10 Kirilovka | 2 х 1,6 | 0.015 | 0.305 | 0.52 | 120 | -0.215 | 0 | 1.68 | 1.895 | 1.895 | opened
90 | SS 35/6 Kislinskaya | 2 х 10,0 | 16.7 | 6.25 | 20 | 10.45 | 0 | 10.5 | 0.05 | 0.05 | opened | 90 | SS 35/6 Kislinskaya | 2 х 10,0 | 0.409 | 17.109 | 6.25 | 20 | 10.859 | 0 | 10.5 | -0.359 | -0.359 | closed
91 | SS 35/10 Fodder plant | 4,0+6,3 | 0.29 | 0 | 0 | 0.29 | 0 | 4.2 | 3.91 | 3.91 | opened | 91 | SS 35/10 Fodder plant | 4,0+6,3 |  | 0.29 | 0 | 0 | 0.29 | 0 | 4.2 | 3.91 | 3.91 | opened
92 | SS 35/10 Mixed fodder plant | 2 х 6,3 | 3.31 | 0.21 | 120 | 3.1 | 0 | 6.615 | 3.515 | 3.515 | opened | 92 | SS 35/10 Mixed fodder plant | 2 х 6,3 | 0.083 | 3.393 | 0.21 | 120 | 3.183 | 0 | 6.615 | 3.432 | 3.432 | opened
93 | SS 35/10 Kommunalnaya | 3,2 + 4,0 | 2.66 | 1.14 | 80 | 1.52 | 0 | 3.36 | 1.84 | 1.84 | opened | 93 | SS 35/10 Kommunalnaya | 3,2 + 4,0 |  | 2.66 | 1.14 | 80 | 1.52 | 0 | 3.36 | 1.84 | 1.84 | opened
94 | SS 35/10 Korenevo | 4,0 + 6,3 | 3.45 | 1.56 | 80 | 1.89 | 0 | 4.2 | 2.31 | 2.31 | opened | 94 | SS 35/10 Korenevo | 4,0 + 6,3 | 3.77 | 7.22 | 1.56 | 80 | 5.66 | 0 | 4.2 | -1.46 | -1.46 | closed
95 | SS 35/10 Kremyanoe | 2,5 + 4,0 | 0.41 | 0.24 | 120 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | opened | 95 | SS 35/10 Kremyanoe | 2,5 + 4,0 |  | 0.41 | 0.24 | 120 | 0.17 | 0 | 2.625 | 2.455 | 2.455 | opened
96 | SS 35/10 Krupets | 1,8 + 2,5 | 1.6 | 0.42 | 120 | 1.18 | 0 | 1.89 | 0.71 | 0.71 | opened | 96 | SS 35/10 Krupets | 1,8 + 2,5 | 0.164 | 1.764 | 0.42 | 120 | 1.344 | 0 | 1.89 | 0.546 | 0.546 | opened
97 | SS 35/10 Kulbaki | 2 х 2,5 | 0.88 | 0.6 | 120 | 0.28 | 0 | 2.625 | 2.345 | 2.345 | opened | 97 | SS 35/10 Kulbaki | 2 х 2,5 | 0.009 | 0.889 | 0.6 | 120 | 0.289 | 0 | 2.625 | 2.336 | 2.336 | opened
98 | SS 35/10 Kultprosvet | 2 х 2,5 | 0.22 | 0.17 | 120 | 0.05 | 0 | 2.625 | 2.575 | 2.575 | opened | 98 | SS 35/10 Kultprosvet | 2 х 2,5 | 0.003 | 0.223 | 0.17 | 120 | 0.053 | 0 | 2.625 | 2.572 | 2.572 | opened
99 | SS 35/10 Kurchatov | 2 х 10,0 | 5.143 | 4.5 | 80 | 0.643 | 0 | 10.5 | 9.857 | 9.857 | opened | 99 | SS 35/10 Kurchatov | 2 х 10,0 | 0.005 | 5.148 | 4.5 | 80 | 0.648 | 0 | 10.5 | 9.852 | 9.852 | opened
100 | SS 35/10 Kutok | 2 х 2,5 | 0.17 | 0.05 | 120 | 0.12 | 0 | 2.625 | 2.505 | 2.505 | opened | 100 | SS 35/10 Kutok | 2 х 2,5 | 0.009 | 0.179 | 0.05 | 120 | 0.129 | 0 | 2.625 | 2.496 | 2.496 | opened
101 | SS 35/10 Linets | 2 х 2,5 | 0.67 | 0.25 | 120 | 0.42 | 0 | 2.625 | 2.205 | 2.205 | opened | 101 | SS 35/10 Linets | 2 х 2,5 | 1.11 | 1.78 | 0.25 | 120 | 1.53 | 0 | 2.625 | 1.095 | 1.095 | opened
102 | SS 35/10 Luch | 2 х 6,3 | 2.83 | 0.23 | 120 | 2.6 | 0 | 6.615 | 4.015 | 4.015 | opened | 102 | SS 35/10 Luch | 2 х 6,3 | 0.308 | 3.138 | 0.23 | 120 | 2.908 | 0 | 6.615 | 3.707 | 3.707 | opened
103 | SS 35/10 Lyubimovka-2 | 2 х 4,0 | 0.75 | 1.59 | 80 | -0.84 | 0 | 4.2 | 5.04 | 5.04 | opened | 103 | SS 35/10 Lyubimovka-2 | 2 х 4,0 | 0.029 | 0.779 | 1.59 | 80 | -0.811 | 0 | 4.2 | 5.011 | 5.011 | opened
104 | SS 35/10 Matveevka | 2 х 2,5 | 0.67 | 0.08 | 120 | 0.59 | 0 | 2.625 | 2.035 | 2.035 | opened | 104 | SS 35/10 Matveevka | 2 х 2,5 | 0.02 | 0.69 | 0.08 | 120 | 0.61 | 0 | 2.625 | 2.015 | 2.015 | opened
105 | SS 35/10 Mayak | 2 х 2,5 | 0.41 | 0.3 | 120 | 0.11 | 0 | 2.625 | 2.515 | 2.515 | opened | 105 | SS 35/10 Mayak | 2 х 2,5 | 0.011 | 0.421 | 0.3 | 120 | 0.121 | 0 | 2.625 | 2.504 | 2.504 | opened
106 | SS 35/10 Mikhailovka | 4,0 + 6,3 | 2.15 | 1.7 | 80 | 0.45 | 0 | 4.2 | 3.75 | 3.75 | opened | 106 | SS 35/10 Mikhailovka | 4,0 + 6,3 | 0.148 | 2.298 | 1.7 | 80 | 0.598 | 0 | 4.2 | 3.602 | 3.602 | opened
107 | SS 35/10 Murynovka | 2 х 4,0 | 0.69 | 0.3 | 120 | 0.39 | 0 | 4.2 | 3.81 | 3.81 | opened | 107 | SS 35/10 Murynovka | 2 х 4,0 | 0.195 | 0.885 | 0.3 | 120 | 0.585 | 0 | 4.2 | 3.615 | 3.615 | opened
108 | SS 35/10 N. Borki | 2 х 2,5 | 0.5 | 0.63 | 120 | -0.13 | 0 | 2.625 | 2.755 | 2.755 | opened | 108 | SS 35/10 N. Borki | 2 х 2,5 | 0.013 | 0.513 | 0.63 | 120 | -0.117 | 0 | 2.625 | 2.742 | 2.742 | opened
109 | SS 35/10 Nikolskaya | 1,6 + 1,8 | 0.63 | 0.03 | 80 | 0.6 | 0 | 1.68 | 1.08 | 1.08 | opened | 109 | SS 35/10 Nikolskaya | 1,6 + 1,8 |  | 0.63 | 0.03 | 80 | 0.6 | 0 | 1.68 | 1.08 | 1.08 | opened
110 | SS 35/10 Novaya | 2 х 2,5 | 1.08 | 0.4 | 120 | 0.68 | 0 | 2.625 | 1.945 | 1.945 | opened | 110 | SS 35/10 Novaya | 2 х 2,5 | 0.246 | 1.326 | 0.4 | 120 | 0.926 | 0 | 2.625 | 1.699 | 1.699 | opened
111 | SS 35/10 Orekhovo | 2 х 2,5 | 0.73 | 0.19 | 120 | 0.54 | 0 | 2.625 | 2.085 | 2.085 | opened | 111 | SS 35/10 Orekhovo | 2 х 2,5 | 0.041 | 0.771 | 0.19 | 120 | 0.581 | 0 | 2.625 | 2.044 | 2.044 | opened
112 | SS 35/10 Orlovka | 2 х 2,5 | 0.17 | 0.52 | 120 | -0.35 | 0 | 2.625 | 2.975 | 2.975 | opened | 112 | SS 35/10 Orlovka | 2 х 2,5 | 0.03 | 0.2 | 0.52 | 120 | -0.32 | 0 | 2.625 | 2.945 | 2.945 | opened
113 | SS 35/10 Osotskoe | 2 х 2,5 | 0.19 | 0.2 | 120 | -0.01 | 0 | 2.625 | 2.635 | 2.635 | opened | 113 | SS 35/10 Osotskoe | 2 х 2,5 |  | 0.19 | 0.2 | 120 | -0.01 | 0 | 2.625 | 2.635 | 2.635 | opened
114 | SS 35/10 Okhochevka | 4,0 + 6,3 | 1.27 | 0.74 | 120 | 0.53 | 0 | 4.2 | 3.67 | 3.67 | opened | 114 | SS 35/10 Okhochevka | 4,0 + 6,3 | 0.172 | 1.442 | 0.74 | 120 | 0.702 | 0 | 4.2 | 3.498 | 3.498 | opened
115 | SS 35/10 Panino | 2 х 2,5 | 0.26 | 0.11 | 80 | 0.15 | 0 | 2.625 | 2.475 | 2.475 | opened | 115 | SS 35/10 Panino | 2 х 2,5 | 0.005 | 0.265 | 0.11 | 80 | 0.155 | 0 | 2.625 | 2.47 | 2.47 | opened
116 | SS 35/10 Pervoavgustovka | 2,5 + 3,2 | 0.74 | 0.52 | 120 | 0.22 | 0 | 2.625 | 2.405 | 2.405 | opened | 116 | SS 35/10 Pervoavgustovka | 2,5 + 3,2 | 0.045 | 0.785 | 0.52 | 120 | 0.265 | 0 | 2.625 | 2.36 | 2.36 | opened
117 | SS 35/10 Petrinka | 2,5 + 4,0 | 1.1 | 0.3 | 120 | 0.8 | 0 | 2.625 | 1.825 | 1.825 | opened | 117 | SS 35/10 Petrinka | 2,5 + 4,0 | 0.716 | 1.816 | 0.3 | 120 | 1.516 | 0 | 2.625 | 1.109 | 1.109 | opened
118 | SS 35/10 Platava | 2 х 2,5 | 1.07 | 0.26 | 120 | 0.81 | 0 | 2.625 | 1.815 | 1.815 | opened | 118 | SS 35/10 Platava | 2 х 2,5 | 0.014 | 1.084 | 0.26 | 120 | 0.824 | 0 | 2.625 | 1.801 | 1.801 | opened
119 | SS 35/10 Pogozhee | 2 х 1,6 | 0.23 | 0.46 | 120 | -0.23 | 0 | 1.68 | 1.91 | 1.91 | opened | 119 | SS 35/10 Pogozhee | 2 х 1,6 | 0.047 | 0.277 | 0.46 | 120 | -0.183 | 0 | 1.68 | 1.863 | 1.863 | opened
120 | SS 35/10 Porechnoe | 2 х 4,0 | 0.5 | 1.16 | 120 | -0.66 | 0 | 4.2 | 4.86 | 4.86 | opened | 120 | SS 35/10 Porechnoe | 2 х 4,0 | 0.008 | 0.508 | 1.16 | 120 | -0.652 | 0 | 4.2 | 4.852 | 4.852 | opened
121 | SS 35/10 Pochepnoe | 2 х 6,3 | 0.13 | 0.08 | 120 | 0.05 | 0 | 6.615 | 6.565 | 6.565 | opened | 121 | SS 35/10 Pochepnoe | 2 х 6,3 |  | 0.13 | 0.08 | 120 | 0.05 | 0 | 6.615 | 6.565 | 6.565 | opened
122 | SS 35/10 Prigorodnoe | 2 х 2,5 | 0.8 | 0.3 | 80 | 0.5 | 0 | 2.625 | 2.125 | 2.125 | opened | 122 | SS 35/10 Prigorodnoe | 2 х 2,5 | 0.274 | 1.074 | 0.3 | 80 | 0.774 | 0 | 2.625 | 1.851 | 1.851 | opened
123 | SS 35/10 Pselets | 2 х 1,6 | 0.2 | 0.24 | 120 | -0.04 | 0 | 1.68 | 1.72 | 1.72 | opened | 123 | SS 35/10 Pselets | 2 х 1,6 |  | 0.2 | 0.24 | 120 | -0.04 | 0 | 1.68 | 1.72 | 1.72 | opened
124 | SS 35/10 Puzachi | 1,6 + 4,0 | 0.4 | 0.43 | 120 | -0.03 | 0 | 1.68 | 1.71 | 1.71 | opened | 124 | SS 35/10 Puzachi | 1,6 + 4,0 | 0.04 | 0.44 | 0.43 | 120 | 0.01 | 0 | 1.68 | 1.67 | 1.67 | opened
125 | SS 35/10 Pushkarnoe | 2 х 2,5 | 0.91 | 0.32 | 120 | 0.59 | 0 | 2.625 | 2.035 | 2.035 | opened | 125 | SS 35/10 Pushkarnoe | 2 х 2,5 | 0.179 | 1.089 | 0.32 | 120 | 0.769 | 0 | 2.625 | 1.856 | 1.856 | opened
126 | SS 35/10 R.Kolodets | 2 х 2,5 | 0.6 | 0.44 | 120 | 0.16 | 0 | 2.625 | 2.465 | 2.465 | opened | 126 | SS 35/10 R.Kolodets | 2 х 2,5 | 0.339 | 0.939 | 0.44 | 120 | 0.499 | 0 | 2.625 | 2.126 | 2.126 | opened
127 | SS 35/10 Razvetye | 2 х 4,0 | 2.38 | 1.03 | 120 | 1.35 | 0 | 4.2 | 2.85 | 2.85 | opened | 127 | SS 35/10 Razvetye | 2 х 4,0 | 0.388 | 2.768 | 1.03 | 120 | 1.738 | 0 | 4.2 | 2.462 | 2.462 | opened
128 | SS 35/10 V. Reutets | 2 х 4,0 | 0.3 | 0.11 | 120 | 0.19 | 0 | 4.2 | 4.01 | 4.01 | opened | 128 | SS 35/10 V. Reutets | 2 х 4,0 | 0.017 | 0.317 | 0.11 | 120 | 0.207 | 0 | 4.2 | 3.993 | 3.993 | opened
129 | SS 35/10 Rozhdestvenka | 2 х 1,6 | 0.3 | 0.29 | 120 | 0.01 | 0 | 1.68 | 1.67 | 1.67 | opened | 129 | SS 35/10 Rozhdestvenka | 2 х 1,6 | 0.061 | 0.361 | 0.29 | 120 | 0.071 | 0 | 1.68 | 1.609 | 1.609 | opened
130 | SS 35/10 Rubilnik | 2 х 2,5 | 0.78 | 1.18 | 80 | -0.4 | 0 | 2.625 | 3.025 | 3.025 | opened | 130 | SS 35/10 Rubilnik | 2 х 2,5 | 0.045 | 0.825 | 1.18 | 80 | -0.355 | 0 | 2.625 | 2.98 | 2.98 | opened
131 | SS 35/10 Ryzhkovo | 2 х 1,6 | 0.23 | 0.08 | 20 | 0.15 | 0 | 1.68 | 1.53 | 1.53 | opened | 131 | SS 35/10 Ryzhkovo | 2 х 1,6 | 0.007 | 0.237 | 0.08 | 20 | 0.157 | 0 | 1.68 | 1.523 | 1.523 | opened
132 | SS 35/10 Sapogovo | 2 х 2,5 | 1.57 | 0.6 | 20 | 0.97 | 0 | 2.625 | 1.655 | 1.655 | opened | 132 | SS 35/10 Sapogovo | 2 х 2,5 | 0.308 | 1.878 | 0.6 | 20 | 1.278 | 0 | 2.625 | 1.347 | 1.347 | opened
133 | SS 35/10 Svoboda-selskaya | 2 х 6,3 | 4.01 | 2.25 | 80 | 1.76 | 0 | 6.615 | 4.855 | 4.855 | opened | 133 | SS 35/10 Svoboda-selskaya | 2 х 6,3 | 0.263 | 4.273 | 2.25 | 80 | 2.023 | 0 | 6.615 | 4.592 | 4.592 | opened
134 | SS 35/10 Selektsionnaya | 2 х 4,0 | 1.56 | 1.4 | 45 | 0.16 | 0 | 4.2 | 4.04 | 4.04 | opened | 134 | SS 35/10 Selektsionnaya | 2 х 4,0 | 0.031 | 1.591 | 1.4 | 45 | 0.191 | 0 | 4.2 | 4.009 | 4.009 | opened
135 | SS 35/10 Semyonovka | 2 х 2,5 | 0.5 | 0 | - | 0.5 | 0 | 2.625 | 2.125 | 2.125 | opened | 135 | SS 35/10 Semyonovka | 2 х 2,5 | 0.056 | 0.556 | 0 | - | 0.556 | 0 | 2.625 | 2.069 | 2.069 | opened
136 | SS 35/10 Seed plant | 2 х 2,5 | 0.6 | 0.6 | 120 | 0 | 0 | 2.625 | 2.625 | 2.625 | opened | 136 | SS 35/10 Seed plant | 2 х 2,5 | 0.049 | 0.649 | 0.6 | 120 | 0.049 | 0 | 2.625 | 2.576 | 2.576 | opened
137 | SS 35/10 Snagost | 2 х 4,0 | 1.26 | 0.05 | 10 | 1.21 | 0 | 4.2 | 2.99 | 2.99 | opened | 137 | SS 35/10 Snagost | 2 х 4,0 | 0.037 | 1.297 | 0.05 | 10 | 1.247 | 0 | 4.2 | 2.953 | 2.953 | opened
138 | SS 35/10 SOM | 1,6 + 4,0 | 1.56 | 0.08 | 10 | 1.48 | 0 | 1.68 | 0.2 | 0.2 | opened | 138 | SS 35/10 SOM | 1,6 + 4,0 | 0.068 | 1.628 | 0.08 | 10 | 1.548 | 0 | 1.68 | 0.132 | 0.132 | opened
139 | SS 35/10 Sosnovy Bor | 3,2 + 4,0 | 0.69 | 0.69 | 120 | 0 | 0 | 3.36 | 3.36 | 3.36 | opened | 139 | SS 35/10 Sosnovy Bor | 3,2 + 4,0 | 0.049 | 0.739 | 0.69 | 120 | 0.049 | 0 | 3.36 | 3.311 | 3.311 | opened
140 | SS 35/10 Stakanovo | 2 х 2,5 | 1.23 | 0.58 | 80 | 0.65 | 0 | 2.625 | 1.975 | 1.975 | opened | 140 | SS 35/10 Stakanovo | 2 х 2,5 | 0.051 | 1.281 | 0.58 | 80 | 0.701 | 0 | 2.625 | 1.924 | 1.924 | opened
141 | SS 35/10 Starkovo | 2 х 1,6 | 0.45 | 0.2 | 80 | 0.25 | 0 | 1.68 | 1.43 | 1.43 | opened | 141 | SS 35/10 Starkovo | 2 х 1,6 | 0.009 | 0.459 | 0.2 | 80 | 0.259 | 0 | 1.68 | 1.421 | 1.421 | opened
142 | CC 35/10 Starshee | 2 х 1,6 | 0.31 | 0.2 | 120 | 0.11 | 0 | 1.68 | 1.57 | 1.57 | opened | 142 | CC 35/10 Starshee | 2 х 1,6 | 0.014 | 0.324 | 0.2 | 120 | 0.124 | 0 | 1.68 | 1.556 | 1.556 | opened
143 | SS 35/10 Teplitsy | 2 х 4,0 | 2.25 | 1.08 | 45 | 1.17 | 0 | 4.2 | 3.03 | 3.03 | opened | 143 | SS 35/10 Teplitsy | 2 х 4,0 | 0.08 | 2.33 | 1.08 | 45 | 1.25 | 0 | 4.2 | 2.95 | 2.95 | opened
144 | SS 35/10 Turovka | 2 х 2,5 | 0.8 | 0.6 | 120 | 0.2 | 0 | 2.625 | 2.425 | 2.425 | opened | 144 | SS 35/10 Turovka | 2 х 2,5 | 0.055 | 0.855 | 0.6 | 120 | 0.255 | 0 | 2.625 | 2.37 | 2.37 | opened
145 | SS 35/10 Uspenka | 2 х 2,5 | 1.19 | 1 | 80 | 0.19 | 0 | 2.625 | 2.435 | 2.435 | opened | 145 | SS 35/10 Uspenka | 2 х 2,5 | 0.035 | 1.225 | 1 | 80 | 0.225 | 0 | 2.625 | 2.4 | 2.4 | opened
146 | SS 35/6 Tsentralnaya | 2 х 25,0 | 24.9 | 5 |  | 19.9 | 0 | 26.25 | 6.35 | 6.35 | opened | 146 | SS 35/6 Tsentralnaya | 2 х 25,0 | 0.005 | 24.905 | 5 |  | 19.905 | 0 | 26.25 | 6.345 | 6.345 | opened
147 | SS 35/10 Chermoshnoe | 2 х 2,5 | 0.45 | 0.5 | 120 | -0.05 | 0 | 2.625 | 2.675 | 2.675 | opened | 147 | SS 35/10 Chermoshnoe | 2 х 2,5 |  | 0.45 | 0.5 | 120 | -0.05 | 0 | 2.625 | 2.675 | 2.675 | opened
148 | SS 35/10 Shatalovka | 2,5 + 4,0 | 0.31 | 0.21 | 80 | 0.1 | 0 | 2.625 | 2.525 | 2.525 | opened | 148 | SS 35/10 Shatalovka | 2,5 + 4,0 | 0.035 | 0.345 | 0.21 | 80 | 0.135 | 0 | 2.625 | 2.49 | 2.49 | opened
149 | SS 35/10 Shipy | 2 х 2,5 | 0.2 | 0.3 | 120 | -0.1 | 0 | 2.625 | 2.725 | 2.725 | opened | 149 | SS 35/10 Shipy | 2 х 2,5 | 0.012 | 0.212 | 0.3 | 120 | -0.088 | 0 | 2.625 | 2.713 | 2.713 | opened
150 | SS 35/10 Elevator | 4,0 + 6,3 | 2.21 | 0.6 | 120 | 1.61 | 0 | 4.2 | 2.59 | 2.59 | opened | 150 | SS 35/10 Elevator | 4,0 + 6,3 | 0.015 | 2.225 | 0.6 | 120 | 1.625 | 0 | 4.2 | 2.575 | 2.575 | opened
151 | SS 35/10 Yugo-Zapadnaya | 2 х 10,0 | 9.28 | 4.7 | 80 | 4.58 | 0 | 10.5 | 5.92 | 5.92 | opened | 151 | SS 35/10 Yugo-Zapadnaya | 1 х 10,0 |  | 9.28 | 4.7 | 80 | 4.58 | 0 | 10.5 | 5.92 | 5.92 | opened
152 | SS 35/10 Plant of reinforced-concrete products | 2 х 2,5 | 1.97 | 3.9 | 120 | -1.93 | 0 | 2.625 | 4.555 | 4.555 | opened | 152 | SS 35/10 Plant of reinforced-concrete products | 2 х 2,5 |  | 1.97 | 3.9 | 120 | -1.93 | 0 | 2.625 | 4.555 | 4.555 | opened
| TOTAL: | 3206.8 | 784.983 | 777.63 | [5 empty] | 1201.837 |  | 2: TOTAL:; 3: 3206.8; 4: 81.9135; 5: 866.8965; МВА 6: 783.52; Мин. 12: 1149.266
| deficit | [8 empty] | -8.27 |  | 2: deficit; Мин. 12: -16.619
| proficit | [8 empty] | 1193.567 |  | 2: proficit; Мин. 12: 1132.6465
*Note: Capacity deficit over SS Vysokaya is grounded by transfer of loads from SS Tsentralnaya and will be removed after putting into operation
РУ-10 кВ на ПС Центральная.