## брянск
No. | Object of main substation, voltage class | Current deficit | [8 empty] | Note
|  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | Summary total capacity of Central Substation following the results of measurements of load maximum Sмах , MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit/proficit of Main Substation, MVA
|  |  |  | МVА | Мin.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | SS 110/10 kv Lopandino | 6.3 | 1.2 | 1.2 | 24 hours | 0 | 0 | 6.615 | 6.615 | 6.615 | opened
2 | SS 110/35/10 kv Nerussa | 16 | 3.8 | 3.4 | 24 hours | 0.4 | 0 | 16.8 | 16.4 | 15.1 | opened
| Nom. capacity MV, MVA | 16 | 1.7 | 1.5 | 24 hours | 0.2 | 0 | 16.8 | 15.1
| Nom. capacity LV, MVA | 16 | 2.1 | 1.9 | 24 hours | 0.2 | 0 | 16.8 | 16.6
3 | SS 110/6 kv Svenskaya | 6.3 | 1.602 | 1.5 | 24 hours | 0.102 | 0 | 6.615 | 6.513 | 6.513 | opened
4 | SS 110/10 kv Khmelevskaya | 6.3 | 0.361 | 0.361 | 24 hours | 0 | 0 | 6.615 | 6.615 | 6.615 | opened
5 | SS 110/6 kv Energoremont | 10 | 6.4 | 6.4 | 24 hours | 0 | 0 | 10.5 | 10.5 | 10.5 | opened
1 | SS 110/6 kv Naytopovichi 8NA | 10 | 0.671 | 0.671 | 24 hours | 0 | 0 | 10.5 | 10.5 | 10.5 | opened
2 | SS 110/10 kv Glybochka | 2.5 | 1.225 | 1.225 | 24 hours | 0 | 0 | 2.625 | 2.625 | 2.625 | opened
3 | SS 110/10 kv Desyatukha | 6.3 | 1.191 | 1.187 | 24 hours | 0.004 | 0 | 6.615 | 6.611 | 6.611 | opened
4 | SS 110/35/10 kv Ivaytenki | 6.3 | 1.6 | 1.6 | 24 hours | 0 | 0 | 6.615 | 6.615 | 5.915 | opened
| Nom. capacity MV, MVA | 6.3 | 0.7 | 0.9 | 24 hours | 0 | 0 | 6.615 | 5.915
| Nom. capacity LV, MVA | 6.3 | 0.9 | 0.7 | 24 hours | 0.2 | 0 | 6.615 | 6.415
5 | SS 110/35/10 kv Lugovaya | 16 | 5.4 | 4.7 | 24 hours | 0.7 | 0 | 16.8 | 16.1 | 12.1 | opened
| Nom. capacity MV, MVA | 16 | 4.7 | 3.8 | 24 hours | 0.9 | 0 | 16.8 | 12.1
| Nom. capacity LV, MVA | 16 | 0.7 | 0.9 | 24 hours | 0 | 0 | 16.8 | 16.8
6 | SS 110/35/10 kv Plyuskovo | 6.3 | 2.2 | 2.1 | 24 hours | 0.1 | 0 | 6.615 | 6.515 | 5.615 | opened
| Nom. capacity MV, MVA | 6.3 | 1 | 1.1 | 24 hours | 0 | 0 | 6.615 | 5.615
| Nom. capacity LV, MVA | 6.3 | 1.2 | 1 | 24 hours | 0.2 | 0 | 6.615 | 6.415
7 | SS 35/10 kv Aleshinskaya | 2.5 | 0.4 | 0.4 | 24 hours | 0.4 | 0 | 0.4 | 0 | 0 | opened
8 | SS 35/10 kv Altukhovskaya | 1.6 | 0.5 | 0.5 | 24 hours | 0.5 | 0 | 0.5 | 0 | 0 | opened
9 | SS 35/10 kv Domashovo | 2.5 | 0.522 | 0.522 | 24 hours | 0.522 | 0 | 0.522 | 0 | 0 | opened
10 | SS 35/6 kv Dronovskaya | 2.5 | 0.6 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0 | 0 | opened
11 | SS 35/10 kv Kokorevskaya | 4 | 0.9 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0 | 0 | opened
12 | SS 35/6 kv Malopolpinskaya | 4 | 0.447 | 0.447 | 24 hours | 0.447 | 0 | 0.447 | 0 | 0 | opened
13 | SS 35/10 kv Morachevskaya | 1.6 | 0.316 | 0.316 | 24 hours | 0.316 | 0 | 0.316 | 0 | 0 | opened
14 | SS 35/10 kv Saltanovskaya | 2.5 | 0.66 | 0.66 | 24 hours | 0.66 | 0 | 0.66 | 0 | 0 | opened
15 | SS 35/10 kv Svetovo | 2.5 | 0.375 | 0.375 | 24 hours | 0.375 | 0 | 0.375 | 0 | 0 | opened
16 | SS 35/10 kv Seshcha | 2.5 | 0.6 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0 | 0 | opened
17 | SS 35/10 kv Sovkhoznaya | 4 | 0.4 | 0.4 | 24 hours | 0.4 | 0 | 0.4 | 0 | 0 | opened
18 | SS 35/10 kv Strachevskaya | 2.5 | 0.6 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0 | 0 | opened
19 | SS 35/10 kv Strashevichi | 4 | 0.732 | 0.732 | 24 hours | 0.732 | 0 | 0.732 | 0 | 0 | opened
20 | SS 35/10 kv Usozhskaya | 2.5 | 0.886 | 0.886 | 24 hours | 0.886 | 0 | 0.886 | 0 | 0 | opened
21 | SS 35/10 kv Kharinovskaya | 1 | 0.1 | 0.1 | 24 hours | 0.1 | 0 | 0.1 | 0 | 0 | opened
22 | SS 35/10 kv Kharitonovskaya | 4 | 0.762 | 0.762 | 24 hours | 0.762 | 0 | 0.762 | 0 | 0 | opened
23 | SS 35/10 kv Divovka | 2.5 | 0.632 | 0.632 | 24 hours | 0.632 | 0 | 0.632 | 0 | 0 | opened
24 | SS 35/10 kv Molodkovo | 1 | 0.5 | 0.5 | 24 hours | 0.5 | 0 | 0.5 | 0 | 0 | opened
25 | SS 35/10 kv Papsuevskaya | 2.5 | 0.412 | 0.412 | 24 hours | 0.412 | 0 | 0.412 | 0 | 0 | opened
26 | SS 35/10 kv Radutinskaya | 1.6 | 0.539 | 0.539 | 24 hours | 0.539 | 0 | 0.539 | 0 | 0 | opened
27 | SS 35/6 kv Ushchepye | 1.6 | 0.625 | 0.625 | 24 hours | 0.625 | 0 | 0.625 | 0 | 0 | opened
28 | SS 35/10 kv Ushchepye | 1.6 | 0.141 | 0.141 | 24 hours | 0.141 | 0 | 0.141 | 0 | 0 | opened
29 | SS 35/10 kv Yakovskaya | 2.5 | 0.583 | 0.583 | 24 hours | 0.583 | 0 | 0.583 | 0 | 0 | opened
30 | SS 110/35/6 kv Aksinino | 40+40 | 21.1 | 0 | 0 | 21.1 | 0 | 42 | 20.9 | 20.9 | opened
| Nom. capacity MV, MVA | 40+40 | 3.5 | 0 | 0 | 3.5 | 0 | 42 | 38.5
| Nom. capacity LV, MVA | 40+40 | 17.6 | 0 | 0 | 17.6 | 0 | 42 | 24.4
31 | SS 110/10 kv Airport | 6,3+6,3 | 0.9 | 0 | 0 | 0.9 | 0 | 6.615 | 5.715 | 5.715 | opened
32 | SS 110/6 kv Bezhitskaya | 25+40 | 34.57 | 0 | 0 | 34.57 | 0 | 26.25 | -8.32 | -8.32 | closed
33 | SS 110/6 kv Water intake | 6,3+6,3 | 1.938 | 0 | 0 | 1.938 | 0 | 6.615 | 4.677 | 4.677 | opened
34 | SS 110/6 kv Gorodishchenskaya | 16+16 | 25.56 | 1.5 | 12 hours | 24.06 | 0 | 16.8 | -7.26 | -7.26 | closed
35 | SS 110/10 kv Dobrunskaya | 6,3+4 | 4.338 | 0 | 0 | 4.338 | 0 | 4.2 | -0.138 | -0.138 | closed
36 | SS 110/35/6 kv Dormashevskaya | 40+63 | 44.04 | 0 | 0 | 44.04 | 0 | 42 | -2.04 | -2.04 | closed
| Nom. capacity MV, MVA | 40+63 | 22.42 | 0 | 0 | 22.42 | 0 | 42 | 19.58
| Nom. capacity LV, MVA | 40+63 | 21.62 | 0 | 0 | 21.62 | 0 | 42 | 20.38
37 | SS 110/35/10 kv Dubrovskaya | 16+16 | 9.37 | 0 | 0 | 9.37 | 0 | 16.8 | 7.43 | 7.43 | opened
| Nom. capacity MV, MVA | 16+16 | 5.47 | 0 | 0 | 5.47 | 0 | 16.8 | 11.33
| Nom. capacity LV, MVA | 16+16 | 3.9 | 0 | 0 | 3.9 | 0 | 16.8 | 12.9
38 | SS 110/35/6 kv Dyadkovksya | 25+25 | 36.58 | 9.19 | 12 hours | 27.39 | 0 | 26.25 | -1.14 | -1.14 | closed
| Nom. capacity MV, MVA | 25+25 | 9.19 | 9.19 | 12 hours | 0 | 0 | 26.25 | 17.06
| Nom. capacity LV, MVA | 25+25 | 27.39 | 0 | 0 | 27.39 | 0 | 26.25 | -1.14
39 | SS 110/35/10 kv Zhukovskaya | 16+25 | 15.7 | 5.2 | 6 hours | 10.5 | 0 | 16.8 | 6.3 | 6.3 | открыт
| Nom. capacity MV, MVA | 16+25 | 7 | 5.2 | 6 hours | 1.8 | 0 | 16.8 | 9.8
| Nom. capacity LV, MVA | 16+25 | 8.7 | 0 | 0 | 8.7 | 0 | 16.8 | 8.1
40 | SS 110/6 kv Zarechnaya | 10+10 | 8.27 | 0 | 0 | 8.27 | 0 | 10.5 | 2.23 | 2.23 | opened
41 | SS 110/35/6 kv Ivotskaya | 25+25 | 9.98 | 2.68 | 6 houкs | 7.3 | 0 | 26.25 | 18.95 | 18.95 | opened
| Nom. capacity MV, MVA | 25+25 | 6.36 | 2.68 | 6 hours | 3.68 | 0 | 26.25 | 19.89
| Nom. capacity LV, MVA | 25+25 | 3.62 | 0 | 0 | 0 | 0 | 26.25 | 26.25
42 | SS 110/6 kv Kamvolnaya | 16+25 | 17.92 | 0 | 0 | 17.92 | 0 | 16.8 | -1.12 | -1.12 | closed
43 | SS 110/6 kv Karachevskaya | 16+25 | 10.9 | 0 | 0 | 10.9 | 0 | 16.8 | 5.9 | 5.9 | opened
44 | SS 110/6 kv Karachizhskaya | 10+10 | 18.28 | 0 | 0 | 18.28 | 0 | 10.5 | -7.78 | -7.78 | closed
45 | SS 110/35/10 kv Kletnyanskaya | 10+16 | 7.1 | 1.4 | 6 hours | 5.7 | 0 | 10.5 | 4.8 | 4.8 | opened
| Nom. capacity MV, MVA | 10+16 | 1.9 | 1.4 | 6 hours | 0.5 | 0 | 10.5 | 8.6
| Nom. capacity LV, MVA | 10+16 | 5.2 | 0 | 0 | 5.2 | 0 | 10.5 | 5.3
46 | SS 110/35/10 kv Komarichi | 16+16 | 11.6 | 3.7 | 6 hours | 7.9 | 0 | 16.8 | 8.9 | 8.9 | opened
| Nom. capacity MV, MVA | 16+16 | 6.7 | 3.7 | 6 hours | 3 | 0 | 16.8 | 10.1
| Nom. capacity LV, MVA | 16+16 | 4.9 | 0 | 0 | 4.9 | 0 | 16.8 | 11.9
47 | SS 110/10 kv Letoshniki | 6,3+2,5 | 1.015 | 0 | 0 | 1.015 | 0 | 2.625 | 1.61 | 1.61 | opened
48 | SS 110/6 kv Mamonovskaya | 10+16 | 15.29 | 0 | 0 | 15.29 | 0 | 10.5 | -4.79 | -4.79 | closed
49 | SS 110/35/10 kv Maritskaya | 10+16 | 5.5 | 4.5 | 6 hours | 1 | 0 | 10.5 | 9.5 | 6.1 | opened
| Nom. capacity MV, MVA | 10+16 | 4.4 | 4.5 | 6 hours | 0 | 0 | 10.5 | 6.1
| Nom. capacity LV, MVA | 10+16 | 1.1 | 0 | 0 | 1.1 | 0 | 10.5 | 9.4
50 | SS 110/6 kv Michurinskaya | 6,3+10 | 2.504 | 0 | 0 | 2.504 | 0 | 6.615 | 4.111 | 4.111 | opened
51 | SS 110/10 kv Molotinskaya | 6,3+6,3 | 2.567 | 0 | 0 | 2.567 | 0 | 6.615 | 4.048 | 4.048 | opened
52 | SS 110/10 kv Polpinskaya | 16+16 | 4.7 | 0 | 0 | 4.7 | 0 | 16.8 | 12.1 | 12.1 | opened
53 | SS 110/6 kv Sovetskaya | 16+16+25+40 | 36.96 | 0 | 0 | 36.96 | 0 | 59.85 | 22.89 | 22.89 | opened
54 | SS 110/6 kv Staleliteynaya | 40+31,5+40 | 42.4 | 0 | 0 | 42.4 | 0 | 75.075 | 32.675 | 32.675 | opened
55 | SS 110/10 kv Teplichnaya | 10+10 | 4.9 | 0 | 0 | 4.9 | 0 | 10.5 | 5.6 | 5.6 | opened
56 | SS 110/6 kv Uritskaya | 20+20 | 14.38 | 0 | 0 | 14.38 | 0 | 21 | 6.62 | 6.62 | opened
57 | SS 110/35/10 kv Tsentralnaya | 16+16 | 14.06 | 4.8 | 6 hours | 9.26 | 0 | 16.8 | 7.54 | 7.54 | opened
| Nom. capacity MV, MVA | 16+16 | 4.82 | 4.8 | 6 hours | 0.02 | 0 | 16.8 | 11.98
| Nom. capacity LV, MVA | 16+16 | 9.24 | 0 | 0 | 9.24 | 0 | 16.8 | 7.56
58 | SS 110/6 kv Yuzhnaya | 16+25 | 19.43 | 0 | 0 | 19.43 | 0 | 16.8 | -2.63 | -2.63 | closed
59 | SS 110/10 kv Bobovichi | 6,3+2,5 | 1.497 | 0 | 0 | 1.497 | 0 | 2.625 | 1.128 | 1.128 | opened
60 | SS 110/6 kv Belaya Berezka | 16+25 | 4.469 | 0 | 0 | 4.469 | 0 | 16.8 | 12.331 | 12.331 | opened
61 | SS 110/10 kv Valuets | 4+6,3 | 1.208 | 0 | 0 | 1.208 | 0 | 4.2 | 2.992 | 2.992 | opened
62 | SS 110/35/6 kv Vodoochistnaya | 10+6,3 | 2.1 | 0.54 | 3 hours | 1.56 | 0 | 42 | 40.44 | 40.1 | opened
| Nom. capacity MV, MVA | 10+6,3 | 0.2 | 0.54 | 3 hours | 0 | 0 | 42 | 41.8
| Nom. capacity LV, MVA | 10+6,3 | 1.9 | 0 | 0 | 1.9 | 0 | 42 | 40.1
63 | SS 110/6 kv Vysokoe | 40+40 | 31.467 | 0 | 0 | 31.467 | 0 | 42 | 10.533 | 10.533 | opened
64 | SS 110/10 kv Zalineynaya | 10+6,3 | 3.931 | 0 | 0 | 3.931 | 0 | 6.615 | 2.684 | 2.684 | opened
65 | SS 110/6 kv Zapadnaya | 10+10 | 10.5 | 0 | 0 | 10.5 | 0 | 10.5 | 0 | 0 | opened
66 | SS 110/35/10 kv Klimovo | 16+16 | 10.2 | 1.64 | 6 hours | 8.56 | 0 | 42 | 33.44 | 33.44 | opened
| Nom. capacity MV, MVA | 16+16 | 3.1 | 1.64 | 6 hours | 1.46 | 0 | 42 | 38.9
| Nom. capacity LV, MVA | 16+16 | 7.1 | 0 | 0 | 7.1 | 0 | 42 | 34.9
67 | SS 110/35/6 kv Kozhany | 10+10 | 3.864 | 3.12 | 6 hours | 0.744 | 0 | 42 | 41.256 | 38.884 | opened
| Nom. capacity MV, MVA | 10+10 | 3.116 | 3.12 | 6 hours | -0.004 | 0 | 42 | 38.884
| Nom. capacity LV, MVA | 10+10 | 0.748 | 0 | 0 | 0.748 | 0 | 42 | 41.252
68 | SS 110/10 kv Krasny Rog | 2,5+2,5 | 1.265 | 0 | 0 | 1.265 | 0 | 2.625 | 1.36 | 1.36 | opened
69 | SS 110/35/10 kv Pogar | 16+16+16 | 10.552 | 1.8 | 6 hours | 8.752 | 0 | 42 | 33.248 | 33.248 | opened
| Nom. capacity MV, MVA | 16+16 | 1.803 | 1.8 | 6 hours | 0.003 | 0 | 42 | 40.197
| Nom. capacity LV, MVA | 16+16 | 8.749 | 0 | 0 | 8.749 | 0 | 42 | 33.251
70 | SS 110/35/10 kv Pochepskaya | 16+25 | 12.995 | 2.21 | 3 hours | 10.785 | 0 | 42 | 31.215 | 31.213 | opened
| Nom. capacity MV, MVA | 16+25 | 2.208 | 2.21 | 3 hours | -0.002 | 0 | 42 | 39.792
| Nom. capacity LV, MVA | 16+25 | 10.787 | 0 | 0 | 10.787 | 0 | 42 | 31.213
71 | SS 110/10 kv Semyachki | 2,5+2,5 | 0.539 | 0 | 0 | 0.539 | 0 | 2.625 | 2.086 | 2.086 | opened
72 | SS 110/35/10 kv Starodub | 16+16 | 12.564 | 7.34 | 6 hours | 5.224 | 0 | 42 | 36.776 | 34.665 | opened
| Nom. capacity MV, MVA | 16+16 | 7.335 | 7.34 | 6 hours | -0.005 | 0 | 42 | 34.665
| Nom. capacity LV, MVA | 16+16 | 5.229 | 0 | 0 | 5.229 | 0 | 42 | 36.771
73 | SS 110/10 kv Staroselye | 6,3+6,3 | 0.976 | 0 | 0 | 0.976 | 0 | 6.615 | 5.639 | 5.639 | opened
74 | SS 110/35/6 kv Surazh | 16+16 | 18.6 | 3.04 | 6 hours | 15.56 | 0 | 42 | 26.44 | 26.4 | opened
| Nom. capacity MV, MVA | 16+16 | 3 | 3.04 | 6 hours | -0.04 | 0 | 42 | 39
| Nom. capacity LV, MVA | 16+16 | 15.6 | 0 | 0 | 15.6 | 0 | 42 | 26.4
75 | SS 110/10 kv Trubchevsk | 16+10 | 7.871 | 0 | 0 | 7.871 | 0 | 10.5 | 2.629 | 2.629 | opened
76 | SS 110/10 kv Shelomy | 6,3+6,3 | 1.005 | 0 | 0 | 1.005 | 0 | 6.615 | 5.61 | 5.61 | opened
77 | SS 110/35/6 kv Yubileynaya | 16+16 | 14.3 | 6.45 | 3 hours | 7.85 | 0 | 42 | 34.15 | 34 | opened
| Nom. capacity MV, MVA | 16+16 | 6.3 | 6.45 | 3 hours | 0 | 0 | 42 | 35.7
| Nom. capacity LV, MVA | 16+16 | 8 | 0 | 0 | 8 | 0 | 42 | 34
78 | SS 35/6 kv Beloberezhskaya | 6,3+6,3 | 3 | 0 | 0 | 3 | 0 | 6.615 | 3.615 | 3.615 | opened
79 | SS 35/10 kv Brasovskaya | 6,3+6,3 | 3.828 | 0 | 0 | 3.828 | 0 | 6.615 | 2.787 | 2.787 | opened
80 | SS 35/10 kv Bulshevskaya | 1,6+1,6 | 0.6 | 0 | 0 | 0.6 | 0 | 1.68 | 1.08 | 1.08 | opened
81 | SS 35/6 kv Bytosh | 3,2+6,3 | 2.708 | 0 | 0 | 2.708 | 0 | 3.36 | 0.652 | 0.652 | opened
82 | SS 35/6 kv Velyaminovskaya | 4+4 | 2.021 | 0 | 0 | 2.021 | 0 | 4.2 | 2.179 | 2.179 | opened
83 | SS 35/6 kv Vetma | 2,5+2,5 | 0.21 | 0 | 0 | 0.21 | 0 | 2.625 | 2.415 | 2.415 | opened
84 | SS 35/6 kv Volodarskaya | 10+6,3 | 11.35 | 0 | 0 | 11.35 | 0 | 6.615 | -4.735 | -4.735 | closed
85 | SS 35/10 kv Glodnevskaya | 4+2,5 | 1.353 | 0 | 0 | 1.353 | 0 | 2.625 | 1.272 | 1.272 | opened
86 | SS 35/6 kv Gorodskaya | 10+10 | 12.14 | 0 | 0 | 12.14 | 0 | 10.5 | -1.64 | -1.64 | closed
87 | SS 35/10 kv Grishina Sloboda | 4+4 | 0.6 | 0 | 0 | 0.6 | 0 | 4.2 | 3.6 | 3.6 | opened
88 | SS 35/10 kv Dobrovodye | 1,6+1,6 | 0.316 | 0 | 0 | 0.316 | 0 | 1.68 | 1.364 | 1.364 | opened
89 | SS 35/10 kv Zhiryatinskaya | 4+4 | 1.7 | 0 | 0 | 1.7 | 0 | 4.2 | 2.5 | 2.5 | opened
90 | SS 35/10 kv Igritskaya | 4+6,3 | 2.084 | 0 | 0 | 2.084 | 0 | 4.2 | 2.116 | 2.116 | opened
91 | SS 35/10 kv Kasilovskaya | 2,5+1 | 0.141 | 0 | 0 | 0.141 | 0 | 1.05 | 0.909 | 0.909 | opened
92 | SS 35/10 kv Kositskaya | 2,5+2,5 | 0.3 | 0 | 0 | 0.3 | 0 | 2.625 | 2.325 | 2.325 | opened
93 | SS 35/10 kv Krupets | 2,5+2,5 | 0.825 | 0 | 0 | 0.825 | 0 | 2.625 | 1.8 | 1.8 | opened
94 | SS 35/10 kv Luna | 1,6+1,6 | 1.105 | 0 | 0 | 1.105 | 0 | 1.68 | 0.575 | 0.575 | opened
95 | SS 35/6 kv Lyubokhna | 6,3+6,3 | 6.18 | 0 | 0 | 6.18 | 0 | 6.615 | 0.435 | 0.435 | opened
96 | SS 35/10 kv Mareevskaya | 1,6+1,6 | 0.8 | 0 | 0 | 0.8 | 0 | 1.68 | 0.88 | 0.88 | opened
97 | SS 35/10 kv Nevdolsk | 1,6+1,6 | 0.212 | 0 | 0 | 0.212 | 0 | 1.68 | 1.468 | 1.468 | opened
98 | SS 35/10 kv Norinskaya | 4+4 | 0.6 | 0 | 0 | 0.6 | 0 | 4.2 | 3.6 | 3.6 | opened
99 | SS 35/6 kv Paltso | 4+2,5 | 0.447 | 0 | 0 | 0.447 | 0 | 2.625 | 2.178 | 2.178 | opened
100 | SS 35/6 kv Pobeda | 4+4 | 3.67 | 0 | 0 | 3.67 | 0 | 4.2 | 0.53 | 0.53 | opened
101 | SS 35/10 kv Pogreby | 4+4 | 1 | 0 | 0 | 1 | 0 | 4.2 | 3.2 | 3.2 | opened
102 | SS 35/10 kv Privolskaya | 2,5+1,6 | 1 | 0 | 0 | 1 | 0 | 1.68 | 0.68 | 0.68 | opened
103 | SS 35/10 kv Rzhanitskaya | 2,5+2,5 | 0.7 | 0 | 0 | 0.7 | 0 | 2.625 | 1.925 | 1.925 | opened
104 | SS 35/10 kv Rognedinskaya | 4+6,3 | 1.6 | 0 | 0 | 1.6 | 0 | 4.2 | 2.6 | 2.6 | opened
105 | SS 35/10,5 kv Ruzhnenskaya | 4+4 | 0.86 | 0 | 0 | 0.86 | 0 | 4.2 | 3.34 | 3.34 | opened
106 | SS 35/10 kv Sevskaya | 6,3+6,3 | 3.8 | 0 | 0 | 3.8 | 0 | 6.615 | 2.815 | 2.815 | opened
107 | SS 35/6 kc Seshcha | 1,6+4 | 2 | 0 | 0 | 2 | 0 | 1.68 | -0.32 | -0.32 | closed
108 | SS 35/6 kv Star | 10+10 | 3.84 | 0 | 0 | 3.84 | 0 | 10.5 | 6.66 | 6.66 | opened
109 | SS 35/10 kv Teplovskaya | 2,5+2,5 | 0.721 | 0 | 0 | 0.721 | 0 | 2.625 | 1.904 | 1.904 | opened
110 | SS 35/10 kv Fedorovskaya | 1,6+1,8 | 0.584 | 0 | 0 | 0.584 | 0 | 1.68 | 1.096 | 1.096 | opened
111 | SS 35/6 kv Fokinskaya | 16+16+16 | 22.62 | 0 | 0 | 22.62 | 0 | 33.6 | 10.98 | 10.98 | opened
112 | SS 35/6 kv Fosforitnaya | 6,3+5,6+16 | 8.3 | 0 | 0 | 8.3 | 0 | 12.495 | 4.195 | 4.195 | opened
113 | SS 35/10 kv Khvoshchevskaya | 2,5+2,5 | 0.93 | 0 | 0 | 0.93 | 0 | 2.625 | 1.695 | 1.695 | opened
114 | SS 35/10 kv Abarinskaya | 4+4 | 0.835 | 0 | 0 | 0.835 | 0 | 4.2 | 3.365 | 3.365 | opened
115 | SS 35/10 kv Andreykovichi | 2,5+2,5 | 0.93 | 0 | 0 | 0.93 | 0 | 2.625 | 1.695 | 1.695 | opened
116 | SS 35/10 kv Borshchevo | 1,6+1,6 | 1.08 | 0 | 0 | 1.08 | 0 | 1.68 | 0.6 | 0.6 | opened
117 | SS 35/10 kv Vlazovichi | 2,5+1,6 | 0.5 | 0 | 0 | 0.5 | 0 | 1.68 | 1.18 | 1.18 | opened
118 | SS 35/6 kv Water intake | 2,5+2,5 | 0.36 | 0 | 0 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | opened
119 | SS 35/10 kv Voronok | 2,5+3,2 | 1.47 | 0 | 0 | 1.47 | 0 | 2.625 | 1.155 | 1.155 | opened
120 | SS 35/10 kv Gordeevka | 4+4 | 2.3 | 0 | 0 | 2.3 | 0 | 4.2 | 1.9 | 1.9 | opened
121 | SS 35/10 kv Gridenki | 2,5+3,2 | 1.533 | 0 | 0 | 1.533 | 0 | 2.625 | 1.092 | 1.092 | opened
122 | SS 35/10 kv Zavodskaya | 4+2,5 | 1.12 | 0 | 0 | 1.12 | 0 | 2.625 | 1.505 | 1.505 | opened
123 | SS 35/10 kv Istopki | 1,6+1,6 | 1.106 | 0 | 0 | 1.106 | 0 | 1.68 | 0.574 | 0.574 | opened
124 | SS 35/10 kv Katashin | 1,6+1,6 | 0.899 | 0 | 0 | 0.899 | 0 | 1.68 | 0.781 | 0.781 | opened
125 | SS 35/10 kv Kivay | 2,5+2,5 | 1.931 | 0 | 0 | 1.931 | 0 | 2.625 | 0.694 | 0.694 | opened
126 | SS 35/10 kv Krutoyar | 2,5+1,6 | 0.762 | 0 | 0 | 0.762 | 0 | 1.68 | 0.918 | 0.918 | opened
127 | SS 35/10 kv Logovatoe | 2,5+1,6 | 1.329 | 0 | 0 | 1.329 | 0 | 1.68 | 0.351 | 0.351 | opened
128 | SS 35/10 kv Lopazna | 2,5+2,5 | 0.36 | 0 | 0 | 0.36 | 0 | 2.625 | 2.265 | 2.265 | opened
129 | SS 35/10 kv Mglinskaya | 4+4 | 3.899 | 0 | 0 | 3.899 | 0 | 4.2 | 0.301 | 0.301 | opened
130 | SS 35/10 kv Mishkovka | 2,5+1,6 | 0.632 | 0 | 0 | 0.632 | 0 | 1.68 | 1.048 | 1.048 | opened
131 | SS 35/10 kv Novo-Drokov | 2,5+2,5 | 0.58 | 0 | 0 | 0.58 | 0 | 2.625 | 2.045 | 2.045 | opened
132 | SS 35/10 kv Putevaya | 6,3+6,3 | 5.767 | 0 | 0 | 5.767 | 0 | 6.615 | 0.848 | 0.848 | opened
133 | SS 35/10 kv Selishchanskaya | 2,5+2,5 | 1.369 | 0 | 0 | 1.369 | 0 | 2.625 | 1.256 | 1.256 | opened
134 | SS 35/10 kv Slava | 2,5+1,6 | 1.325 | 0 | 0 | 1.325 | 0 | 1.68 | 0.355 | 0.355 | opened
135 | SS 35/10 kv Smolevichi | 6,3+6,3 | 3.22 | 0 | 0 | 3.22 | 0 | 6.615 | 3.395 | 3.395 | opened
136 | SS 35/10 kv Solovyevka | 1,6+1,6 | 0.45 | 0 | 0 | 0.45 | 0 | 1.68 | 1.23 | 1.23 | opened
137 | SS 35/10 kv Sytaya Buda | 2,5+2,5 | 0.447 | 0 | 0 | 0.447 | 0 | 2.625 | 2.178 | 2.178 | opened
138 | SS 35/6 kv Tembr | 4+4+3,2 | 6.93 | 0 | 0 | 6.93 | 0 | 7.56 | 0.63 | 0.63 | opened
139 | SS 35/10 kv Churovichi | 2,5+4 | 0.978 | 0 | 0 | 0.978 | 0 | 2.625 | 1.647 | 1.647 | opened
140 | SS 35/10 kv Shcherbinichi | 2,5+2,5 | 1.03 | 0 | 0 | 1.03 | 0 | 2.625 | 1.595 | 1.595 | opened
| Total: | 2274.8 | 776.924
| deficit | [8 empty] | -41.913
| proficit | [8 empty] | 673.5