## Костромаэнерго
No. | Object of main substation, voltage class | Current deficit | [8 empty] | Note
|  | Installed power capacity of transformers Sуst. Including their number, pcs/ MVA | Summary total capacity of central substation following the results of measurements of load maximal Sмах , MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transmission capacity, MVA | Deficit /proficit of main substation, MVA
|  |  |  | MVA | Min.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
One-transformer substations
1 | Sandogora 35/6 kv | 1 | 0.47 | 0.55 | 120 | 0.55 | 0 | 0.55 | 0.08 | 0.08 | opened
2 | Gridino 35/10 kv | 1.8 | 0.73 | 1.2 | 120 | 1.2 | 0 | 1.2 | 0.47 | 0.47 | opened
3 | Novinki 35/10 kv | 1.8 | 0.13 | 1.44 | 120 | 1.44 | 0 | 1.44 | 1.31 | 1.31 | opened
4 | Priskokovo 35/10kv | 2.5 | 1.5 | 1.5 | 120 | 1.5 | 0 | 1.5 | 0 | 0 | opened
5 | Grigortsevo 110/10 kv | 2.5 | 0.25 | 1.5 | 120 | 1.5 | 0 | 1.5 | 1.25 | 1.25 | opened
6 | Klementyevo 110/10 kv | 6.3 | 0.38 | 3.7 | 120 | 3.7 | 0 | 3.7 | 3.32 | 3.32 | opened
7 | Rudino 35/10 kv | 2.5 | 0.25 | 1.5 | 120 | 1.5 | 0 | 1.5 | 1.25 | 1.25 | opened
8 | Stoyankovo 35/10 kv | 1.6 | 0.14 | 0.72 | 120 | 0.72 | 0 | 0.72 | 0.58 | 0.58 | opened
9 | Adishchevo 35/10 kv | 4 | 1.35 | 2.6 | 120 | 2.6 | 0 | 2.6 | 1.25 | 1.25 | opened
10 | Stolbovo 110/10 kv | 10 | 0.27 | 4.6 | 120 | 4.6 | 0 | 4.6 | 4.33 | 4.33 | opened
11 | Raslovo 35/10 kv | 2.5 | 0.54 | 1.38 | 120 | 1.38 | 0 | 1.38 | 0.84 | 0.84 | opened
12 | Andreevskoe 35/10 kv | 1.6 | 0.18 | 0.93 | 120 | 0.93 | 0 | 0.93 | 0.75 | 0.75 | opened
13 | Popadyino 35/10 kv | 1.6 | 0.22 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.66 | 0.66 | opened
14 | Elegino 110/10 kv | 2.5 | 0.13 | 0.98 | 120 | 0.98 | 0 | 0.98 | 0.85 | 0.85 | opened
15 | Krenyovo 35/10 kv | 2.5 | 0.47 | 2.5 | 24 hours | 2.5 | 0 | 2.5 | 2.03 | 2.03 | opened
16 | Semyonovskoe 35/10 kv | 1.6 | 0.09 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 1.51 | 1.51 | opened
17 | Khimik 35/10 kv | 3.2 | 0.1 | 1.44 | 120 | 1.44 | 0 | 1.44 | 1.34 | 1.34 | opened
18 | N. Beryozovets 35/10 kv | 2.5 | 0.33 | 0.43 | 120 | 0.43 | 0 | 0.43 | 0.1 | 0.1 | opened
19 | Stepanovo 35/10 kv | 4 | 0.32 | 2.32 | 120 | 2.32 | 0 | 2.32 | 2 | 2 | opened
20 | Gorbachevo 35/10 kv | 1 | 0.11 | 0.78 | 120 | 0.78 | 0 | 0.78 | 0.67 | 0.67 | opened
21 | Kalinino 35/10 kv | 1 | 0.11 | 0.56 | 120 | 0.56 | 0 | 0.56 | 0.45 | 0.45 | opened
22 | Kuzemino 35/10 kv | 1.6 | 0.23 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 1.37 | 1.37 | opened
23 | Sovega 35/10 kv | 1 | 0.09 | 0.65 | 120 | 0.65 | 0 | 0.65 | 0.56 | 0.56 | opened
24 | Lukovtsino 110/10 kv | 2.5 | 0.19 | 1.38 | 120 | 1.38 | 0 | 1.38 | 1.19 | 1.19 | opened
25 | Fyodorovskoe 110/10 kv | 2.5 | 0.15 | 1.5 | 120 | 1.5 | 0 | 1.5 | 1.35 | 1.35 | opened
26 | Pankratovo 35/10 kv | 1 | 0.06 | 0.39 | 120 | 0.39 | 0 | 0.39 | 0.33 | 0.33 | opened
27 | Petrovskoe 35/10 kv | 1.6 | 0.32 | 0.77 | 120 | 0.77 | 0 | 0.77 | 0.45 | 0.45 | opened
28 | Kotelnikovo 35/10 kv | 1 | 0.11 | 0.26 | 120 | 0.26 | 0 | 0.26 | 0.15 | 0.15 | opened
29 | Legitovo 35/10 kv | 2.5 | 0.31 | 1.1 | 120 | 1.1 | 0 | 1.1 | 0.79 | 0.79 | opened
30 | Sloboda 35/10 kv | 2.5 | 0.05 | 0.85 | 120 | 0.85 | 0 | 0.85 | 0.8 | 0.8 | opened
31 | Zavrazhye 35/10 kv | 1.6 | 0.29 | 0.74 | 120 | 0.74 | 0 | 0.74 | 0.45 | 0.45 | opened
32 | Okulovo 35/10 kv | 1.6 | 0.16 | 0.9 | 120 | 0.9 | 0 | 0.9 | 0.74 | 0.74 | opened
33 | Chernyshevo 35/10 kv | 4 | 0.57 | 1.8 | 120 | 1.8 | 0 | 1.8 | 1.23 | 1.23 | opened
34 | Yakovlevo 110/35/10 kv | 10 | 0.06 | 5.3 | 120 | 5.3 | 0 | 5.3 | 5.24 | 5.24 | opened
| Nom. Capacity MV, MVA | 10 | 0 | 0 | 120 | 0 | 0 | 0 | 0
| Nom. Capacity LV, MVA | 10 | 0.06 | 5.3 | 120 | 5.3 | 0 | 5.3 | 5.24
35 | Chermenino 35/10 kv | 1.6 | 0.07 | 0.86 | 120 | 0.86 | 0 | 0.86 | 0.79 | 0.79 | opened
36 | Nezhitino 35/10 kv | 1 | 0.08 | 0.54 | 120 | 0.54 | 0 | 0.54 | 0.46 | 0.46 | opened
37 | Nikolo-Makarovo 35/10 kv | 1.6 | 0.45 | 0.99 | 120 | 0.99 | 0 | 0.99 | 0.54 | 0.54 | opened
38 | Gusevo 110/10 kv | 2.5 | 0.29 | 1.63 | 120 | 1.63 | 0 | 1.63 | 1.34 | 1.34 | opened
39 | Medveditsa 35/10 kv | 2.5 | 0.53 | 1.3 | 120 | 1.3 | 0 | 1.3 | 0.77 | 0.77 | opened
40 | Novinskoe 110/10 kv | 2.5 | 0.03 | 1.23 | 120 | 1.23 | 0 | 1.23 | 1.2 | 1.2 | opened
41 | Filino 35/10 kv | 1.6 | 0.25 | 0.96 | 120 | 0.96 | 0 | 0.96 | 0.71 | 0.71 | opened
42 | Dyakonovo 110/10 kv | 2.5 | 0.28 | 1.13 | 120 | 1.13 | 0 | 1.13 | 0.85 | 0.85 | opened
43 | Oktyabrskaya 110/10 kv | 2.5 | 0.76 | 2.5 | 24 hours | 2.5 | 0 | 2.5 | 1.74 | 1.74 | opened
44 | Kuzhbal 35/10 kv | 2.5 | 0.4 | 1.48 | 120 | 1.48 | 0 | 1.48 | 1.08 | 1.08 | opened
45 | Nikolo-Poloma 110/10 kv | 2.5 | 1.04 | 1.13 | 120 | 1.13 | 0 | 1.13 | 0.09 | 0.09 | opened
46 | Nikola 110/35/10 kv | 6.3 | 0.28 | 3.15 | 120 | 3.15 | 0 | 3.15 | 2.87 | 2.87 | opened
| Nom. Capacity MV, MVA | 6.3 | 0 | 0 | 120 | 0 | 0 | 0 | 0
| Nom. Capacity LV, MVA | 6.3 | 0.28 | 3.15 | 120 | 3.15 | 0 | 3.15 | 2.87
47 | Zavetluzhye 35/10 kv | 1.6 | 0.11 | 0.67 | 120 | 0.67 | 0 | 0.67 | 0.56 | 0.56 | opened
48 | Talitsa 35/10 kv | 1.6 | 0.26 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 1.34 | 1.34 | opened
49 | Khoroshaya 35/10 kv | 2.5 | 0.06 | 1.95 | 120 | 1.95 | 0 | 1.95 | 1.89 | 1.89 | opened
50 | Zabegaevo 35/10 kv | 1.6 | 0.09 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.79 | 0.79 | opened
51 | Ilyinskoe 35/10 kv | 1.6 | 0.04 | 0.9 | 120 | 0.9 | 0 | 0.9 | 0.86 | 0.86 | opened
52 | Luptyug 35/10 kv | 2.5 | 0.11 | 1.35 | 120 | 1.35 | 0 | 1.35 | 1.24 | 1.24 | opened
53 | Solovetskoe 35/10 kv | 1.6 | 0.09 | 0.72 | 120 | 0.72 | 0 | 0.72 | 0.63 | 0.63 | opened
54 | Gudkovo 110/10 kv | 2.5 | 0.05 | 1.38 | 120 | 1.38 | 0 | 1.38 | 1.33 | 1.33 | opened
55 | Shortyug 110/10 kv | 6.3 | 0.52 | 3.47 | 120 | 3.47 | 0 | 3.47 | 2.95 | 2.95 | opened
56 | Yakshanga 110/10 kv | 6.3 | 1.41 | 3.47 | 120 | 3.47 | 0 | 3.47 | 2.06 | 2.06 | opened
57 | Katunino 35/10 kv | 2.5 | 0.17 | 1.33 | 120 | 1.33 | 0 | 1.33 | 1.16 | 1.16 | opened
58 | Konyovo 35/10 kv | 1.6 | 0.21 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.67 | 0.67 | opened
59 | Shekshema 110/10 kv | 6.3 | 0.58 | 2.5 | 24 hours | 2.5 | 0 | 2.5 | 1.92 | 1.92 | opened
60 | Golovino 35/10 kv | 1 | 0.06 | 0.12 | 120 | 0.12 | 0 | 0.12 | 0.06 | 0.06 | opened
61 | Pishchyovka 35/10 kv | 1 | 0.16 | 0.45 | 120 | 0.45 | 0 | 0.45 | 0.29 | 0.29 | opened
Two- and more transformer substations
62 | Vasilyovo 110/35/10 kv | 10+10 | 2.13 | 0.86 | 120 | 1.27 | 0 | 10.5 | 9.23 | 9.23 | opened
| Nom. Capacity MV, MVA | 10+10 | 0.59 | 0 | 120 | 0.59 | 0 | 10.5 | 9.91
| Nom. Capacity LV, MVA | 10+10 | 1.54 | 0.86 | 120 | 0.68 | 0 | 10.5 | 9.82
63 | Kalinki 110/35/10/6 kv | 10+10+1,6 | 6.12 | 1.15 | 120 | 4.97 | 0 | 12.18 | 7.21 | 7.21 | opened
| Nom. Capacity MV, MVA | 10+10+1,6 | 4.59 | 0 | 120 | 4.59 | 0 | 12.18 | 7.59
| Nom. Capacity LV, MVA | 10+10+1,6 | 1.53 | 1.15 | 120 | 0.38 | 0 | 12.18 | 11.8
64 | Apraksino 35/10 kv | 2,5+2,5 | 1.73 | 0.425 | 120 | 1.305 | 0 | 2.625 | 1.32 | 1.32 | opened
65 | Borshchino 35/10 kv | 4+4 | 0.56 | 0.62 | 120 | -0.06 | 0 | 4.2 | 4.26 | 4.26 | opened
66 | Gorkovskaya 35/10 kv | 1,6+1,6 | 0.2 | 0.11 | 120 | 0.09 | 0 | 1.68 | 1.59 | 1.59 | opened
67 | Ilyinskoe 35/10 kv | 2,5+2,5 | 2.33 | 0.55 | 120 | 1.78 | 0 | 2.625 | 0.845 | 0.845 | opened
68 | Kuznetsovo 35/10 kv | 2,5+2,5 | 1.1 | 0.4 | 120 | 0.7 | 0 | 2.625 | 1.925 | 1.925 | opened
69 | Kuzmishchi 35/10 kv | 1,6+1,6 | 0.72 | 0.29 | 120 | 0.43 | 0 | 1.68 | 1.25 | 1.25 | opened
70 | Minskoe 35/10 kv | 2,5+2,5 | 1.3 | 0.43 | 120 | 0.87 | 0 | 2.625 | 1.755 | 1.755 | opened
71 | Miskovo 35/6 kv | 1,8+1,8 | 0.35 | 0.2 | 120 | 0.15 | 0 | 1.89 | 1.74 | 1.74 | opened
72 | Nikolskoe 35/6 kv | 4+4 | 2.5 | 0.92 | 120 | 1.58 | 0 | 4.2 | 2.62 | 2.62 | opened
73 | Samet 35/6 kv | 1,6+4 | 1.43 | 0 | 0 | 1.43 | 0 | 1.68 | 0.25 | 0.25 | opened
74 | Sukhonogovo 35/10 kv | 3,2+4 | 2.71 | 0 | 0 | 2.71 | 0 | 3.36 | 0.65 | 0.65 | opened
75 | Sushchevo 35/10 kv | 4+4 | 3.68 | 0.76 | 120 | 2.92 | 0 | 4.2 | 1.28 | 1.28 | opened
76 | EMZ 35/6 kv | 1+1 | 0.76 | 0 | 0 | 0.76 | 0 | 1.05 | 0.29 | 0.29 | opened
77 | Krasnoe 110/35/10 kv | 16+16 | 12.41 | 0 | 0 | 12.41 | 0 | 16.8 | 4.39 | 4.39 | opened
| Nom. Capacity MV, MVA | 16+16 | 0.77 | 0 | 0 | 0.77 | 0 | 16.8 | 16.03
| Nom. Capacity LV, MVA | 16+16 | 11.64 | 0 | 0 | 11.64 | 0 | 16.8 | 5.16
78 | Isaevo 35/10 kv | 4+4 | 0.77 | 1.03 | 120 | -0.26 | 0 | 4.2 | 4.46 | 4.46 | opened
79 | Chapaevo 35/10 kv | 2,5+2,5 | 1.27 | 0.43 | 120 | 0.84 | 0 | 2.625 | 1.785 | 1.785 | opened
80 | Chernevo 35/10 kv | 1,8+1,8 | 0.37 | 0.43 | 120 | -0.06 | 0 | 1.89 | 1.95 | 1.95 | opened
81 | Nerekhta-1 110/35/10 kv | 25+25 | 18.51 | 2.75 | 120 | 15.76 | 0 | 26.25 | 10.49 | 10.49 | opened
| Nom. Capacity MV, MVA | 25+25 | 6.52 | 0 | 120 | 6.52 | 0 | 26.25 | 19.73
| Nom. Capacity LV, MVA | 25+25 | 11.99 | 2.75 | 120 | 9.24 | 0 | 26.25 | 17.01
| Nerekhta-1 110/10 kv | 16+16 | 2.41 | 2.2 | 120 | 0.21 | 0 | 16.8 | 16.59
82 | Nerekhta-2 110/10/6 kv | 5,6+10 | 0.93 | 1.55 | 120 | -0.62 | 0 | 5.88 | 6.5 | 6.5 | opened
83 | Vladychnoe 35/10 kv | 1,6+1,6 | 0.57 | 0.41 | 120 | 0.16 | 0 | 1.68 | 1.52 | 1.52 | opened
84 | Tatarskoe 35/10 kv | 1,6+1,6 | 0.36 | 0.23 | 120 | 0.13 | 0 | 6.615 | 6.485 | 6.485 | opened
85 | Aleksandrovo 110/35/10 kv | 6,3+6,3 | 3.89 | 0.76 | 120 | 3.13 | 0 | 6.615 | 3.485 | 3.305 | opened
| Nom. Capacity MV, MVA | 6,3+6,3 | 3.31 | 0 | 120 | 3.31 | 0 | 6.615 | 3.305
| Nom. Capacity LV, MVA | 6,3+6,3 | 0.58 | 0.76 | 120 | -0.18 | 0 | 6.615 | 6.795
86 | Krasnaya Polyana 110/35/10 kv | 10+10 | 3.91 | 1.28 | 120 | 2.63 | 0 | 10.5 | 7.87 | 7.87 | opened
| Nom. Capacity MV, MVA | 10+10 | 0.72 | 0 | 120 | 0.72 | 0 | 10.5 | 9.78
| Nom. Capacity LV, MVA | 10+10 | 3.19 | 1.28 | 120 | 1.91 | 0 | 10.5 | 8.59
87 | Igodovo 35/10 kv | 1,6+1,6 | 0.37 | 0.25 | 120 | 0.12 | 0 | 1.68 | 1.56 | 1.56 | opened
88 | Klevantsovo 35/10 kv | 1,6+1,6 | 0.8 | 0.56 | 120 | 0.24 | 0 | 1.68 | 1.44 | 1.44 | opened
89 | Ostrovskoe 35/10 kv | 2,5+2,5 | 1.32 | 0.52 | 120 | 0.8 | 0 | 2.625 | 1.825 | 1.825 | opened
90 | Sudislavl 110/10 kv | 10+10 | 8.14 | 1.8 | 120 | 6.34 | 0 | 10.5 | 4.16 | 4.16 | opened
91 | Voronye 35/10 kv | 1,8+1,8 | 0.49 | 0.4 | 120 | 0.09 | 0 | 1.89 | 1.8 | 1.8 | opened
92 | Susanino 110/35/10 kv | 10+10 | 3.93 | 1.89 | 120 | 2.04 | 0 | 10.5 | 8.46 | 8.46 | opened
| Nom. Capacity MV, MVA | 10+10 | 0.38 | 0 | 120 | 0.38 | 0 | 10.5 | 10.12
| Nom. Capacity LV, MVA | 10+10 | 3.55 | 1.89 | 120 | 1.66 | 0 | 10.5 | 8.84
93 | Kaliniskaya 35/10 kv | 2,5+2,5 | 0.2 | 0.07 | 120 | 0.13 | 0 | 2.625 | 2.495 | 2.495 | opened
94 | Airport 110/35/6 kv | 16+16 | 4.17 | 2.88 | 120 | 1.29 | 0 | 16.8 | 15.51 | 15.51 | opened
| Nom. Capacity MV, MVA | 16+16 | 0 | 0 | 120 | 0 | 0 | 16.8 | 16.8
| Nom. Capacity LV, MVA | 16+16 | 4.17 | 2.88 | 120 | 1.29 | 0 | 16.8 | 15.51
95 | Vostochnaya-2 110/35/10 kv | 25+25 | 23.04 | 0.02 | 120 | 23.02 | 0 | 26.25 | 3.23 | 3.23 | opened
| Nom. Capacity MV, MVA | 25+25 | 19.24 | 0 | 120 | 19.24 | 0 | 26.25 | 7.01
| Nom. Capacity LV, MVA | 25+25 | 3.8 | 0.02 | 120 | 3.78 | 0 | 26.25 | 22.47
96 | Kostroma-3 110/35/10 kv | 10+16 | 11.49 | 0 | 120 | 11.49 | 0 | 10.5 | -0.99 | -0.99 | closed
| Nom. Capacity MV, MVA | 10+16 | 2.68 | 0 | 120 | 2.68 | 0 | 10.5 | 7.82
| Nom. Capacity LV, MVA | 10+16 | 8.81 | 0 | 120 | 8.81 | 0 | 10.5 | 1.69
97 | Yuzhnaya 110/35/10 kv | 25+25 | 10.9 | 0 | 120 | 10.9 | 0 | 26.25 | 15.35 | 15.35 | opened
| Nom. Capacity MV, MVA | 25+25 | 5.45 | 0 | 120 | 5.45 | 0 | 26.25 | 20.8
| Nom. Capacity LV, MVA | 25+25 | 5.45 | 0 | 120 | 5.45 | 0 | 26.25 | 20.8
98 | Davydovskaya 110/10 kv | 25+25 | 8.91 | 0.02 | 120 | 8.89 | 0 | 26.25 | 17.36 | 17.36 | opened
99 | Kostroma-1 110/6 kv | 10+10 | 10.38 | 0 | 0 | 10.38 | 0 | 10.5 | 0.12 | 0.12 | opened
100 | Severnaya 110/6 kv | 20+25 | 19.24 | 0 | 0 | 19.24 | 0 | 21 | 1.76 | 1.76 | opened
101 | Strommashina 110/6 kv | 40+40 | 9.03 | 0 | 0 | 9.03 | 0 | 42 | 32.97 | 32.97 | opened
102 | Tsentralnaya 110/10/6 kv | 25+25 | 16.44 | 0 | 0 | 16.44 | 0 | 26.25 | 9.81 | 9.81 | opened
103 | Baydarka 35/6 kv | 6,3+6,3 | 1.99 | 1.2 | 120 | 0.79 | 0 | 6.615 | 5.825 | 5.825 | opened
104 | Volzhskaya 35/6 kv | 4+4 | 1.29 | 0.76 | 120 | 0.53 | 0 | 4.2 | 3.67 | 3.67 | opened
105 | Vostochnaya-1 35/6 kv | 10+10+6,3 | 22.36 | 0 | 0 | 22.36 | 0 | 17.115 | -5.245 | -5.245 | closed
106 | Karavaevo 35/10 kv | 6,3+6,3 | 3.46 | 0 | 0 | 3.46 | 0 | 6.615 | 3.155 | 3.155 | opened
107 | Korkino 35/10 kv | 2,5+2,5 | 1.67 | 0.85 | 120 | 0.82 | 0 | 2.625 | 1.805 | 1.805 | opened
108 | KPD 110/35/10 kv | 16+16 | 7.54 | 1.44 | 120 | 6.1 | 0 | 16.8 | 10.7 | 10.7 | opened
| Nom. Capacity MV, MVA | 16+16 | 0.62 | 0 | 120 | 0.62 | 0 | 16.8 | 16.18
| Nom. Capacity LV, MVA | 16+16 | 6.92 | 1.44 | 120 | 5.48 | 0 | 16.8 | 11.32
109 | SM State district power station 110/35/6 kv | 10+16 | 6.48 | 0 | 0 | 6.48 | 0 | 10.5 | 4.02 | 4.02 | opened
| Nom. Capacity MV, MVA | 10+16 | 0.62 | 0 | 0 | 0.62 | 0 | 10.5 | 9.88
| Nom. Capacity LV, MVA | 10+16 | 5.86 | 0 | 0 | 5.86 | 0 | 10.5 | 4.64
110 | Sidorovskoe 35/6 kv | 2,5+4 | 0.76 | 0.82 | 120 | -0.06 | 0 | 2.625 | 2.685 | 2.685 | opened
111 | Buy (r) 110/35/10 kv | 4+10 | 1.87 | 0 | 0 | 1.87 | 0 | 4.2 | 2.33 | 2.33 | opened
| Nom. Capacity MV, MVA | 4+10 | 1.87 | 0 | 0 | 1.87 | 0 | 4.2 | 2.33
| Nom. Capacity LV, MVA | 4+10 | 0 | 0 | 0 | 0 | 0 | 4.2 | 4.2
112 | Buy (agriculture) 110/10 kv | 6,3+6,3 | 6.25 | 1.2 | 120 | 5.05 | 0 | 6.615 | 1.565 | 1.565 | opened
113 | Zapadnaya 110/10 kv | 10+10 | 5.08 | 2.63 | 120 | 2.45 | 0 | 10.5 | 8.05 | 8.05 | opened
114 | Dor 35/10 kv | 1,6+1,6 | 0.46 | 0.06 | 120 | 0.4 | 0 | 1.68 | 1.28 | 1.28 | opened
115 | Dyakonovo 35/10 kv | 1+1 | 0.23 | 0.26 | 120 | -0.03 | 0 | 1.05 | 1.08 | 1.08 | opened
116 | Likurga 35/10 kv | 1,8+1,6 | 0.2 | 0.12 | 120 | 0.08 | 0 | 1.68 | 1.6 | 1.6 | opened
117 | Shushkodom 35/10 kv | 1+1 | 0.29 | 0.06 | 120 | 0.23 | 0 | 1.05 | 0.82 | 0.82 | opened
118 | Novaya 110/35/10 kv | 6,3+6,3 | 2.93 | 0.64 | 120 | 2.29 | 0 | 6.615 | 4.325 | 4.325 | opened
| Nom. Capacity MV, MVA | 6,3+6,3 | 1.83 | 0 | 120 | 1.83 | 0 | 6.615 | 4.785
| Nom. Capacity LV, MVA | 6,3+6,3 | 1.1 | 0.64 | 120 | 0.46 | 0 | 6.615 | 6.155
119 | Orekhovo 110/35/10 kv | 6,3+6,3 | 1.36 | 0 | 120 | 1.36 | 0 | 6.615 | 5.255 | 5.255 | opened
| Nom. Capacity MV, MVA | 6,3+6,3 | 0.53 | 0 | 120 | 0.53 | 0 | 6.615 | 6.085
| Nom. Capacity LV, MVA | 6,3+6,3 | 0.83 | 0 | 120 | 0.83 | 0 | 6.615 | 5.785
120 | Loparevo 110/10 kv | 2,5+2,5 | 0.36 | 0.55 | 120 | -0.19 | 0 | 2.625 | 2.815 | 2.815 | opened
121 | Poultry farm 35/10 kv | 4+4 | 1.73 | 1.28 | 120 | 0.45 | 0 | 4.2 | 3.75 | 3.75 | opened
122 | Kabanovo 35/10 kv | 2,5+2,5 | 0.28 | 0.22 | 120 | 0.06 | 0 | 2.625 | 2.565 | 2.565 | opened
123 | Levkovo 35/10 kv | 1,6+1,6 | 0.22 | 0.74 | 120 | -0.52 | 0 | 1.68 | 2.2 | 2.2 | opened
124 | Pronino 35/10 kv | 4+2,5 | 0.38 | 0.2 | 120 | 0.18 | 0 | 2.625 | 2.445 | 2.445 | opened
125 | Toltunovo 35/10 kv | 2,5+2,5 | 0.2 | 0.13 | 120 | 0.07 | 0 | 2.625 | 2.555 | 2.555 | opened
126 | Soligalich 110/35/10 kv | 10+10 | 5.27 | 1.7 | 120 | 3.57 | 0 | 10.5 | 6.93 | 6.93 | opened
| Nom. Capacity MV, MVA | 10+10 | 0.94 | 0 | 120 | 0.94 | 0 | 10.5 | 9.56
| Nom. Capacity LV, MVA | 10+10 | 4.33 | 1.7 | 120 | 2.63 | 0 | 10.5 | 7.87
127 | Pochinok 35/10 kv | 1,6+2,5 | 0.53 | 0.34 | 120 | 0.19 | 0 | 1.68 | 1.49 | 1.49 | opened
128 | Chukhloma 110/35/10 kv | 6,3+6,3 | 3.97 | 2.06 | 120 | 1.91 | 0 | 6.615 | 4.705 | 4.705 | opened
| Nom. Capacity MV, MVA | 6,3+6,3 | 1.12 | 0 | 120 | 1.12 | 0 | 6.615 | 5.495
| Nom. Capacity LV, MVA | 6,3+6,3 | 2.85 | 2.06 | 120 | 0.79 | 0 | 6.615 | 5.825
129 | Suday 35/10 kv | 1,6+1,6 | 1.01 | 0.49 | 120 | 0.52 | 0 | 1.68 | 1.16 | 1.16 | opened
130 | Antropovo (r) 110/35/10 kv | 6,3+16 | 6.09 | 0.38 | 120 | 5.71 | 0 | 6.615 | 0.905 | 0.905 | opened
| Nom. Capacity MV, MVA | 6,3+16 | 3.53 | 0 | 120 | 3.53 | 0 | 6.615 | 3.085
| Nom. Capacity LV, MVA | 6,3+16 | 2.56 | 0.38 | 120 | 2.18 | 0 | 6.615 | 4.435
131 | Palkino 35/10 kv | 2,5+4 | 0.7 | 0.45 | 120 | 0.25 | 0 | 2.625 | 2.375 | 2.375 | opened
132 | Slovinka 35/10 kv | 1,6+1,6 | 0.11 | 0.1 | 120 | 0.01 | 0 | 1.68 | 1.67 | 1.67 | opened
133 | Kady 110/35/10 kv | 10+10 | 3.48 | 0.69 | 120 | 2.79 | 0 | 10.5 | 7.71 | 7.71 | opened
| Nom. Capacity MV, MVA | 10+10 | 1.23 | 0 | 120 | 1.23 | 0 | 10.5 | 9.27
| Nom. Capacity LV, MVA | 10+10 | 2.25 | 0.69 | 120 | 1.56 | 0 | 10.5 | 8.94
134 | Ekaterinkino 35/10 kv | 1,6+1,6 | 0.09 | 0.1 | 120 | -0.01 | 0 | 1.68 | 1.69 | 1.69 | opened
135 | Ilyinskoe 110/35/10 kv | 10+10 | 5.36 | 0.04 | 120 | 5.32 | 0 | 10.5 | 5.18 | 5.18 | opened
| Nom. Capacity MV, MVA | 10+10 | 5.25 | 0 | 120 | 5.25 | 0 | 10.5 | 5.25
| Nom. Capacity LV, MVA | 10+10 | 0.11 | 0.04 | 120 | 0.07 | 0 | 10.5 | 10.43
136 | Kologriv 35/10 kv | 4+4 | 2.12 | 1.42 | 120 | 0.7 | 0 | 4.2 | 3.5 | 3.5 | opened
137 | Ovsyannikovo 35/10 kv | 1,6+1,6 | 0.23 | 0.08 | 120 | 0.15 | 0 | 1.68 | 1.53 | 1.53 | opened
138 | Makaryev-1 110/35/10 kv | 10+10 | 7.54 | 0.8 | 120 | 6.74 | 0 | 10.5 | 3.76 | 3.76 | opened
| Nom. Capacity MV, MVA | 10+10 | 5.36 | 0 | 120 | 5.36 | 0 | 10.5 | 5.14
| Nom. Capacity MV, MVA | 10+10 | 2.18 | 0.8 | 120 | 1.38 | 0 | 10.5 | 9.12
139 | Gorchukha 35/10 kv | 2,5+2,5 | 1.19 | 0 | 0 | 1.19 | 0 | 2.625 | 1.435 | 1.435 | opened
140 | Makaryev-2 35/10 kv | 4+4 | 3 | 1.58 | 120 | 1.42 | 0 | 4.2 | 2.78 | 2.78 | opened
141 | Timoshino 35/10 kv | 1+1 | 0.18 | 0 | 0 | 0.18 | 0 | 1.05 | 0.87 | 0.87 | opened
142 | Unzha 35/10 kv | 1+1,6 | 0.81 | 0.1 | 120 | 0.71 | 0 | 1.05 | 0.34 | 0.34 | opened
143 | Yakimovo 35/10 kv | 1,6+2,5 | 0.12 | 0.32 | 120 | -0.2 | 0 | 1.68 | 1.88 | 1.88 | opened
144 | BKhZ 110/6 kv | 25+25 | 2.58 | 0 | 0 | 2.58 | 0 | 26.25 | 23.67 | 23.67 | opened
145 | Sosnovka 35/10 kv | 2,5+1,6 | 0.44 | 0.15 | 120 | 0.29 | 0 | 1.68 | 1.39 | 1.39 | opened
146 | Georgievskoe 35/10 kv | 2,5+2,5 | 2.15 | 1.23 | 120 | 0.92 | 0 | 2.625 | 1.705 | 1.705 | opened
147 | Neya 110/35/27,5/10 kv | 40+40+6,3 | 16.05 | 3.6 | 120 | 12.45 | 0 | 48.615 | 36.165 | 36.165 | opened
| Nom. Capacity MV, MVA | 40+40+6,3 | 8.53 | 0 | 120 | 8.53 | 0 | 48.615 | 40.085
| Nom. Capacity LV, MVA | 40+40+6,3 | 7.52 | 3.6 | 120 | 3.92 | 0 | 48.615 | 44.695
148 | Vozherovo 35/10 kv | 1,6+1,6 | 0.15 | 0.12 | 120 | 0.03 | 0 | 1.68 | 1.65 | 1.65 | opened
149 | Matveevo 35/10 kv | 1,8+4 | 0.51 | 0.42 | 120 | 0.09 | 0 | 1.89 | 1.8 | 1.8 | opened
150 | Parfenyevo 35/10 kv | 4+4 | 2.32 | 1.89 | 120 | 0.43 | 0 | 4.2 | 3.77 | 3.77 | opened
151 | Vokhma 110/35/10 kv | 6,3+16 | 5.42 | 0 | 0 | 5.42 | 0 | 6.615 | 1.195 | 1.195 | opened
| Nom. Capacity MV, MVA | 6,3+8 | 1.53 | 0 | 0 | 1.53 | 0 | 6.615 | 5.085
| Nom. Capacity LV, MVA | 6,3+8 | 3.89 | 0 | 0 | 3.89 | 0 | 6.615 | 2.725
152 | Lapshino 35/10 kv | 2,5+2,5 | 0.36 | 0.05 | 120 | 0.31 | 0 | 2.625 | 2.315 | 2.315 | opened
153 | Spass 35/10 kv | 1,6+2,5 | 0.35 | 0.35 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened
154 | Bogovarovo 35/10 kv | 2,5+4 | 1.59 | 1 | 120 | 0.59 | 0 | 2.625 | 2.035 | 2.035 | opened
155 | Pavino 110/35/10 kv | 10+6,3 | 1.69 | 0 | 0 | 1.69 | 0 | 6.615 | 4.925 | 4.925 | opened
| Nom. Capacity MV, MVA | 10+6,3 | 0.18 | 0 | 0 | 0.18 | 0 | 6.615 | 6.435
| Nom. Capacity LV, MVA | 10+6,3 | 1.51 | 0 | 0 | 1.51 | 0 | 6.615 | 5.105
156 | Ledengskaya 35/10 kv | 1,6+4 | 0.07 | 0.07 | 120 | 0 | 0 | 1.68 | 1.68 | 1.68 | opened
157 | Pyshchug 110/35/10 kv | 6,3+6,3 | 2.42 | 0 | 0 | 2.42 | 0 | 6.615 | 4.195 | 4.195 | opened
| Nom. Capacity MV, MVA | 6,3+6,3 | 0.12 | 0 | 0 | 0.12 | 0 | 6.615 | 6.495
| Nom. Capacity LV, MVA | 6,3+6,3 | 2.3 | 0 | 0 | 2.3 | 0 | 6.615 | 4.315
158 | Rozhdestvenskoe 110/35/10 kv | 10+4 | 1.77 | 0.75 | 120 | 1.02 | 0 | 4.2 | 3.18 | 3.18 | opened
| Nom. Capacity MV, MVA | 10+4 | 0.69 | 0 | 120 | 0.69 | 0 | 4.2 | 3.51
| Nom. Capacity LV, MVA | 10+4 | 1.08 | 0.75 | 120 | 0.33 | 0 | 4.2 | 3.87
159 | Odoevskoe 35/10 kv | 1,6+1,6 | 0.25 | 0.27 | 120 | -0.02 | 0 | 1.68 | 1.7 | 1.7 | opened
160 | Sharya (r) 110/35/6 kv | 20+25 | 19.02 | 2 | 120 | 17.02 | 0 | 21 | 3.98 | 3.98 | opened
| Nom. Capacity MV, MVA | 20+25 | 12.2 | 0 | 120 | 12.2 | 0 | 21 | 8.8
| Nom. Capacity LV, MVA | 20+25 | 6.82 | 2 | 120 | 4.82 | 0 | 21 | 16.18
161 | Industrial hub 110/6/6 kv | 25+25 | 3.32 | 2.5 | 120 | 0.82 | 0 | 26.25 | 25.43 | 25.43 | opened
162 | Krivyachka 35/10 kv | 1,6+1 | 0.82 | 0.57 | 120 | 0.25 | 0 | 1.05 | 0.8 | 0.8 | opened
163 | Nikolo-Shanga 35/10 kv | 1,6+1,6 | 0.78 | 0 | 0 | 0.78 | 0 | 1.68 | 0.9 | 0.9 | opened
164 | Tsentralnaya 35/6 kv | 10+10 | 8.96 | 3 | 120 | 5.96 | 0 | 10.5 | 4.54 | 4.54 | opened
| Total over Kostromaenergo | 1705 | 401.12
| deficit | [8 empty] | -6.235
| proficit | [8 empty] | 525.81