## апрель2010
No. | Object of main substation, voltage class | Current deficit | [8 empty] | note
|  | Installed power capacity of transformers Sуst. Including their number, pcs/ MVA | Summary total capacity of central substation following the results of measurements of load maximal Sмах , MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Deficit /proficit of main substation, MVA
|  |  |  | MVA | Min.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
One-transformer substations
1 | SS 110/35/10 Artyukhovka | 1*6,3 | 1.64 | 6.3 | 24 hours | 6.3 | 0 | 6.3 | 4.66 | 1.2 | opened
| Nom. capacity MV, MVA | 6.3 | 1.1 | 2.3 | 24 hours | 2.3 | 0 | 2.3 | 1.2
| Nom. capacity MV, MVA | 6.3 | 0.54 | 4 | 24 hours | 4 | 0 | 4 | 3.46
2 | SS 110/10 Beketovo | 1*6,3 | 0.39 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.76 | 1.76 | opened
3 | SS 110/35/10 Besedino | 1*6,3 | 2.84 | 6.7 | 24 hours | 6.7 | 0 | 6.7 | 3.86 | 0.16 | opened
| Nom. capacity MV, MVA | 6.3 | 0.5 | 4.2 | 24 hours | 4.2 | 0 | 4.2 | 3.7
| Nom. capacity LV, MVA | 6.3 | 2.34 | 2.5 | 24 hours | 2.5 | 0 | 2.5 | 0.16
4 | SS 110/10 Voskhod | 1*10 | 0.8 | 2.5 | 24 hours | 2.5 | 0 | 2.5 | 1.7 | 1.7 | opened
5 | SS 110/35/10 Zhuryatino | 1*6,3 | 0.82 | 6 | 24 hours | 6 | 0 | 6 | 5.18 | 1.48 | opened
| Nom. capacity MV, MVA | 6.3 | 0 | 3.7 | 24 hours | 3.7 | 0 | 3.7 | 3.7
| Nom. capacity LV, MVA | 6.3 | 0.82 | 2.3 | 24 hours | 2.3 | 0 | 2.3 | 1.48
6 | SS 110/35/10 Zhukovka | 1*10 | 1.1 | 5.16 | 120 | 5.16 | 0 | 5.16 | 4.06 | 0.49 | opened
| Nom. capacity MV, MVA | 10 | 0.93 | 4.5 | 24 hours | 4.5 | 0 | 4.5 | 3.57
| Nom. capacity LV, MVA | 10 | 0.17 | 0.66 | 120 | 0.66 | 0 | 0.66 | 0.49
7 | SS 110/10 Zabelye | 1*2,5 | 0.31 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.84 | 1.84 | opened
8 | SS 110/10 Ivnitsa | 1*6,3 | 0.4 | 0.45 | 24 hours | 0.45 | 0 | 0.45 | 0.05 | 0.05 | opened
9 | SS 110/35/10 Lachinovo | 1*10 | 1.28 | 5.13 | 24 hours | 5.13 | 0 | 5.13 | 3.85 | 1 | opened
| Nom. capacity MV, MVA | 10 | 0.75 | 3.6 | 24 hours | 3.6 | 0 | 3.6 | 2.85
| Nom. capacity LV, MVA | 10 | 0.53 | 1.53 | 24 hours | 1.53 | 0 | 1.53 | 1
10 | SS 110/10 Malaya Loknya | 1*10 | 1.2 | 1.21 | 24 hours | 1.21 | 0 | 1.21 | 0.01 | 0.01 | opened
11 | SS 110/35/10 Maritsa | 1*2,5 | 0.99 | 1.92 | 24 hours | 1.92 | 0 | 1.92 | 0.93 | 0.93 | opened
12 | SS 110/35/10 Raskhovets | 1*6,3 | 0.56 | 5.89 | 24 hours | 5.89 | 0 | 5.89 | 5.33 | 1.97 | opened
| Nom. capacity MV, MVA | 6.3 | 0.38 | 3.74 | 24 hours | 3.74 | 0 | 3.74 | 3.36
| Nom. capacity LV, MVA | 6.3 | 0.18 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.97
13 | SS 110/10 Semyonovskaya | 1*2,5 | 0.4 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1 | 1 | opened
14 | SS 110/6 Teplichnaya | 1*16 | 4.1 | 6.64 | 24 hours | 6.64 | 0 | 6.64 | 2.54 | 2.54 | opened
15 | SS 110/35/10 Troitskaya | 1*10 | 3.01 | 7.5 | 24 hours | 7.5 | 0 | 7.5 | 4.49 | 0.79 | opened
| Nom. capacity MV, MVA | 10 | 2.7 | 6.4 | 24 hours | 6.4 | 0 | 6.4 | 3.7
| Nom. capacity LV, MVA | 10 | 0.31 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.79
16 | SS 35/10 Avtodor | 1*2,5 | 0.46 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.34 | 0.34 | opened
17 | SS 35/10 Agronom | 1*1,8 | 0.7 | 0.96 | 24 hours | 0.96 | 0 | 0.96 | 0.26 | 0.26 | opened
18 | SS 35/10 Akimovka | 1*2,5 | 0.25 | 0.68 | 24 hours | 0.68 | 0 | 0.68 | 0.43 | 0.43 | opened
19 | SS 35/10 Alekseevka | 1*2,5 | 0.28 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.15 | 1.15 | opened
20 | SS 35/10 Afanasyevka (WPS) | 1*4 | 0.55 | 1.34 | 24 hours | 1.34 | 0 | 1.34 | 0.79 | 0.79 | opened
21 | SS 35/10 B. Gneushevo | 1*2,5 | 0.77 | 0.96 | 24 hours | 0.96 | 0 | 0.96 | 0.19 | 0.19 | opened
22 | SS 35/10 B.Soldatskoe1 | 1*3,2 | 0.78 | 2.83 | 24 hours | 2.83 | 0 | 2.83 | 2.05 | 2.05 | opened
23 | SS 35/10 Banishchi | 1*1,6 | 0.22 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.42 | 0.42 | opened
24 | SS 35/10 Baranovo | 1*4 | 0.46 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 0.97 | 0.97 | opened
25 | SS 35/10 Belgorodka | 1*2,5 | 0.27 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.88 | 1.88 | opened
26 | SS 35/10 Belitsa | 1*4 | 0.6 | 1.76 | 24 hours | 1.76 | 0 | 1.76 | 1.16 | 1.16 | opened
27 | SS 35/10 Biryukovka | 1*1,6 | 0.6 | 0.67 | 24 hours | 0.67 | 0 | 0.67 | 0.07 | 0.07 | opened
28 | SS 35/10 Bobrovka | 1*1,6 | 0.24 | 0.67 | 24 hours | 0.67 | 0 | 0.67 | 0.43 | 0.43 | opened
29 | SS 35/10 Bobrovo | 1*2,5 | 0.42 | 0.76 | 24 hours | 0.76 | 0 | 0.76 | 0.34 | 0.34 | opened
30 | SS 35/10 Budki | 1*1 | 0.09 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.55 | 0.55 | opened
31 | SS 35/10 Bukreevka (CPS) | 1*1,8 | 0.59 | 1.6 | 50 | 1.6 | 0 | 1.6 | 1.01 | 1.01 | opened
32 | SS 35/10 Bukreevka (WPS) | 1*1,6 | 0.21 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.43 | 0.43 | opened
33 | SS 35/10 Burtsevka | 1*1,6 | 0.18 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.25 | 1.25 | opened
34 | SS 35/10 Bykovo | 1*4 | 0.89 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 0.54 | 0.54 | opened
35 | SS 35/10 V. Shchigor | 1*2,5 | 0.12 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 2.03 | 2.03 | opened
36 | SS 35/10 Vanino | 1*2,5 | 0.36 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.44 | 0.44 | opened
37 | SS 35/10 Vasilyevka | 1*2,5 | 0.64 | 1.05 | 24 hours | 1.05 | 0 | 1.05 | 0.41 | 0.41 | opened
38 | SS 35/10 Water storage | 1*4 | 1.58 | 2.72 | 24 hours | 2.72 | 0 | 2.72 | 1.14 | 1.14 | opened
39 | SS 35/10 Volokonsk | 1*2,5 | 0.3 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.8 | 0.8 | opened
40 | SS 35/10 Vorobyovka | 1*2,5 | 0.65 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.25 | 0.25 | opened
41 | SS 35/10 Voronok | 1*4 | 0.86 | 2.1 | 24 hours | 2.1 | 0 | 2.1 | 1.24 | 1.24 | opened
42 | SS 35/10 Vyazovoe | 1*2,5 | 0.66 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.49 | 1.49 | opened
43 | SS 35/10 Gakhovo | 1*2,5 | 0.21 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1.59 | 1.59 | opened
44 | SS 35/10 Generalshino | 1*2,5 | 0.25 | 1.5 | 24 hours | 1.5 | 0 | 1.5 | 1.25 | 1.25 | opened
45 | SS 35/10 Glazovo | 1*2,5 | 0.94 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 0.46 | 0.46 | opened
46 | SS 35/10 Glebovo | 1*2,5 | 0.49 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 0.91 | 0.91 | opened
47 | SS 35/10 Gordeevka | 1*1,6 | 0.12 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.58 | 0.58 | opened
48 | SS 35/10 Gorodensk | 1*1,6 | 0.59 | 0.76 | 24 hours | 0.76 | 0 | 0.76 | 0.17 | 0.17 | opened
49 | SS 35/10 Goryainovo | 1*2,5 | 0.5 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.6 | 0.6 | opened
50 | SS 35/10 12th State stud farm | 1*2,5 | 0.53 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 0.9 | 0.9 | opened
51 | SS 35/10 Grayvoronka | 1*2,5 | 0.5 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 0.93 | 0.93 | opened
52 | SS 35/10 Grinyovka | 1*2,5 | 0.28 | 2.85 | 24 hours | 2.85 | 0 | 2.85 | 2.57 | 2.57 | opened
53 | SS 35/10 Gustomoy | 1*1,6 | 0.21 | 0.94 | 24 hours | 0.94 | 0 | 0.94 | 0.73 | 0.73 | opened
54 | SS 35/10 Daryino | 1*2,5 | 0.4 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1.4 | 1.4 | opened
55 | SS 35/10 Demyakino | 1*2,5 | 0.43 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.37 | 0.37 | opened
56 | SS 35/10 Efrosimovka | 1*1,8 | 0.38 | 1.07 | 24 hours | 1.07 | 0 | 1.07 | 0.69 | 0.69 | opened
57 | SS 35/10 Zhdanovo | 1*2,5 | 0.38 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.47 | 0.47 | opened
58 | SS 35/10 Zashchitnoe | 1*1,6 | 0.32 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.83 | 1.83 | opened
59 | SS 35/10 Zvannoe | 1*2,5 | 0.6 | 0.84 | 24 hours | 0.84 | 0 | 0.84 | 0.24 | 0.24 | opened
60 | SS 35/10 Znamenka | 1*1,8 | 1.01 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.14 | 1.14 | opened
61 | SS 35/10 Iskra | 1*2,5 | 0.16 | 0.58 | 24 hours | 0.58 | 0 | 0.58 | 0.42 | 0.42 | opened
62 | SS 35/10 Kazanka | 1*4 | 0.33 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.47 | 0.47 | opened
63 | SS 35/10 Kalinovka (new) | 1*2,5 | 0.17 | 1.8 | 24 hours | 1.8 | 0 | 1.8 | 1.63 | 1.63 | opened
64 | SS 35/10 Karyzh | 1*1,6 | 0.18 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.46 | 0.46 | opened
65 | SS 35/10 Kitaevka | 1*1,6 | 0.26 | 0.74 | 24 hours | 0.74 | 0 | 0.74 | 0.48 | 0.48 | opened
66 | SS 35/10 Kobylki | 1*2,5 | 0.68 | 1.53 | 24 hours | 1.53 | 0 | 1.53 | 0.85 | 0.85 | opened
67 | SS 35/10 Kolontaevka | 1*2,5 | 0.26 | 0.84 | 24 hours | 0.84 | 0 | 0.84 | 0.58 | 0.58 | opened
68 | SS 35/10 Kondratovka | 1*1,8 | 0.55 | 1.42 | 24 hours | 1.42 | 0 | 1.42 | 0.87 | 0.87 | opened
69 | SS 35/10 Korovyakovka | 1*1,6 | 0.21 | 0.76 | 24 hours | 0.76 | 0 | 0.76 | 0.55 | 0.55 | opened
70 | SS 35/10 Lezhenki | 1*2,5 | 0.09 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.34 | 1.34 | opened
71 | SS 35/10 Leninskaya | 1*1,8 | 0.67 | 0.73 | 24 hours | 0.73 | 0 | 0.73 | 0.06 | 0.06 | opened
72 | SS 35/10 Lobazovka | 1*2,5 | 0.86 | 1.09 | 24 hours | 1.09 | 0 | 1.09 | 0.23 | 0.23 | opened
73 | SS 35/10 Lugovka | 1*1,6 | 0.54 | 1.29 | 24 hours | 1.29 | 0 | 1.29 | 0.75 | 0.75 | opened
74 | SS 35/10 Lyubava | 1*6,3 | 0.31 | 1.15 | 24 hours | 1.15 | 0 | 1.15 | 0.84 | 0.84 | opened
75 | SS 35/10 Lyubimovka-1 | 1*3,2 | 0 | 0.96 | 24 hours | 0.96 | 0 | 0.96 | 0.96 | 0.96 | opened
76 | SS 35/10 M. Kamenets | 1*1,6 | 0.6 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.5 | 0.5 | opened
77 | SS 35/10 М. Gneushevo | 1*4 | 0.7 | 1.28 | 24 hours | 1.28 | 0 | 1.28 | 0.58 | 0.58 | opened
78 | SS 35/10 М. Kryuki | 1*2,5 | 0.4 | 1.19 | 24 hours | 1.19 | 0 | 1.19 | 0.79 | 0.79 | opened
79 | SS 35/10 Markovo | 1*2,5 | 0.65 | 0.8 | 24 hours | 0.8 | 0 | 0.8 | 0.15 | 0.15 | opened
80 | SS 35/10 Marmyzhi | 1*2,5 | 0.21 | 1.33 | 24 hours | 1.33 | 0 | 1.33 | 1.12 | 1.12 | opened
81 | SS 35/10 Melovoe | 1*4 | 0.99 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.16 | 1.16 | opened
82 | SS 35/10 Mokva | 1*4 | 0.5 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.65 | 1.65 | opened
83 | SS 35/10 Mokrusheno | 1*1,6 | 0.6 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.5 | 0.5 | opened
84 | SS 35/10 Molotychi | 1*2,5 | 0.4 | 0.9 | 24 hours | 0.9 | 0 | 0.9 | 0.5 | 0.5 | opened
85 | SS 35/10 Mochaki | 1*2,5 | 0.03 | 1.07 | 24 hours | 1.07 | 0 | 1.07 | 1.04 | 1.04 | opened
86 | SS 35/10 N. Vladimirovka | 1*2,5 | 0.08 | 4.3 | 24 hours | 4.3 | 0 | 4.3 | 4.22 | 4.22 | opened
87 | SS 35/10 N. Gurovo | 1*4,0 | 0.73 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.42 | 1.42 | opened
88 | SS 35/10 Nadeyka | 1*2,5 | 0.16 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.24 | 1.24 | opened
89 | SS 35/10 Niva | 1*2,5 | 0.4 | 1.56 | 24 hours | 1.56 | 0 | 1.56 | 1.16 | 1.16 | opened
90 | SS 35/10 Olgovka | 1*2,5 | 0.41 | 0.97 | 24 hours | 0.97 | 0 | 0.97 | 0.56 | 0.56 | opened
91 | SS 35/10 Olkhovatka | 1*4 | 0.38 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.26 | 0.26 | opened
92 | SS 35/10 Orositelnaya | 1*4 | 0.93 | 2.97 | 24 hours | 2.97 | 0 | 2.97 | 2.04 | 2.04 | opened
93 | SS 35/10 Peny-2 | 1*2,5 | 0.6 | 2.32 | 24 hours | 2.32 | 0 | 2.32 | 1.72 | 1.72 | opened
94 | SS 35/10 Perestuplino (old) | 1*2,5 | 0.16 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.24 | 1.24 | opened
95 | SS 35/10 Perestuplino (new) | 1*2,5 | 0.36 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.04 | 1.04 | opened
96 | SS 35/10 Petrovo | 1*6,3 | 1 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.15 | 1.15 | opened
97 | SS 35/10 Petrovskaya | 1*2,5 | 0.03 | 0.74 | 24 hours | 0.74 | 0 | 0.74 | 0.71 | 0.71 | opened
98 | SS 35/10 Pokrovskoe | 1*2,5 | 0.27 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.88 | 1.88 | opened
99 | SS 35/10 Prilepy | 1*1,6 | 0.53 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.62 | 1.62 | opened
100 | SS 35/10 Pristen | 1*4 | 2.3 | 3.3 | 24 hours | 3.3 | 0 | 3.3 | 1 | 1 | opened
101 | SS 35/10 R. Budy 35/10 | 1*4 | 0 | 0.74 | 24 hours | 0.74 | 0 | 0.74 | 0.74 | 0.74 | opened
102 | SS 35/10 Reut | 1*2,5 | 0.16 | 0.86 | 0 | 0.86 | 0 | 0.86 | 0.7 | 0.7 | opened
103 | SS 35/10 Rovenka | 1*1,6 | 0.16 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.27 | 1.27 | opened
104 | SS 35/10 Rodina (NPC) | 1*2,5 | 0.17 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.53 | 0.53 | opened
105 | SS 35/10 Rodina (EPS) | 1*4 | 0.5 | 2.3 | 24 hours | 2.3 | 0 | 2.3 | 1.8 | 1.8 | opened
106 | SS 35/10 Rubanshchina | 1*2,5 | 0.4 | 1.31 | 24 hours | 1.31 | 0 | 1.31 | 0.91 | 0.91 | opened
107 | SS 35/10 Rusanovo | 1*1,8 | 0.39 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.04 | 1.04 | opened
108 | SS 35/10 Ryshkovo | 1*2,5 | 0.56 | 0.94 | 24 hours | 0.94 | 0 | 0.94 | 0.38 | 0.38 | opened
109 | SS 35/10 Ryazanovo | 1*1,6 | 0.58 | 1.15 | 24 hours | 1.15 | 0 | 1.15 | 0.57 | 0.57 | opened
110 | SS 35/10 Sazanovka | 1*2,5 | 0.3 | 1.25 | 24 hours | 1.25 | 0 | 1.25 | 0.95 | 0.95 | opened
111 | SS 35/10 Sergievka | 1*2,5 | 0.4 | 2.7 | 24 hours | 2.7 | 0 | 2.7 | 2.3 | 2.3 | opened
112 | SS 35/10 Sokolye | 1*2,5 | 0.3 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.13 | 1.13 | opened
113 | SS 35/10 Solntsevo | 1*2,5 | 0.9 | 1.76 | 24 hours | 1.76 | 0 | 1.76 | 0.86 | 0.86 | opened
114 | SS 35/10 Spasskoe | 1*1,6 | 0.22 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.88 | 0.88 | opened
115 | SS 35/10 Sr. Olshanka | 1*2,5 | 0.3 | 1.4 | 24 hours | 1.4 | 0 | 1.4 | 1.1 | 1.1 | opened
116 | SS 35/10 Streletskaya | 1*2,5 | 0.35 | 1.3 | 24 hours | 1.3 | 0 | 1.3 | 0.95 | 0.95 | opened
117 | SS 35/10 Subbotino | 1*2,5 | 0.6 | 1.34 | 24 hours | 1.34 | 0 | 1.34 | 0.74 | 0.74 | opened
118 | SS 35/10 Sukhaya | 1*1,6 | 0.44 | 0.71 | 24 hours | 0.71 | 0 | 0.71 | 0.27 | 0.27 | opened
119 | SS 35/10 Telmana | 1*2,5 | 0.3 | 1.15 | 24 hours | 1.15 | 0 | 1.15 | 0.85 | 0.85 | opened
120 | SS 35/10 Terebuzh | 1*2,5 | 0.46 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 0.97 | 0.97 | opened
121 | SS 35/10 Fateevka | 1*2,5 | 0.08 | 0.7 | 24 hours | 0.7 | 0 | 0.7 | 0.62 | 0.62 | opened
122 | SS 35/10 Fentisovo | 1*1,6 | 0.17 | 1.72 | 24 hours | 1.72 | 0 | 1.72 | 1.55 | 1.55 | opened
123 | SS 35/10 Chapaevskaya | 1*2,5 | 0.2 | 1.1 | 24 hours | 1.1 | 0 | 1.1 | 0.9 | 0.9 | opened
124 | SS 35/10 Chemerki | 1*1,6 | 0.06 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.79 | 0.79 | opened
125 | SS 35/10 Chizhovka | 1*1,6 | 0.35 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.08 | 1.08 | opened
126 | SS 35/10 Shatilovka | 1*2,5 | 0.16 | 1.43 | 24 hours | 1.43 | 0 | 1.43 | 1.27 | 1.27 | opened
127 | SS 35/10 Sheptukhovka | 1*2,5 | 0.75 | 1.47 | 24 hours | 1.47 | 0 | 1.47 | 0.72 | 0.72 | opened
128 | SS 35/10 Shuklino | 1*2,5 | 0.25 | 0.85 | 24 hours | 0.85 | 0 | 0.85 | 0.6 | 0.6 | opened
129 | SS 35/10 Elevator | 1*6,3 | 0.31 | 0.6 | 24 hours | 0.6 | 0 | 0.6 | 0.29 | 0.29 | opened
130 | SS 35/10 Yankovo | 1*1,6 | 0.25 | 0.64 | 24 hours | 0.64 | 0 | 0.64 | 0.39 | 0.39 | opened
131 | SS 35/10 Yasenki | 1*2,5 | 0.48 | 2.15 | 24 hours | 2.15 | 0 | 2.15 | 1.67 | 1.67 | opened
Two- and more transformer substations
1 | SS 110/6 Akkumulyatornaya | 2*25 | 10.47 | 0 | 0 | 10.47 | 0 | 26.25 | 15.78 | 15.78 | opened
2 | SS 110/10 ARZ | 6,3+10 | 2.62 | 0.9 | 45 | 1.72 | 0 | 6.62 | 4.9 | 4.9 | opened
3 | SS 110/35/10 Atomgrad | 2*25 | 13.07 | 20.2 | 120 | -7.13 | 0 | 26.25 | 33.38 | 26.02 | opened
| Nom. capacity MV, MVA | 25 | 3.24 | 10.6 | 120 | -7.36 | 0 | 26.25 | 33.61
| Nom. capacity lV, MVA | 25 | 9.83 | 9.6 | 120 | 0.23 | 0 | 26.25 | 26.02
4 | SS 110/10 B. Zhirovo | 2*6,3 | 0.36 | 0.6 | 120 | -0.24 | 0 | 6.62 | 6.86 | 6.86 | opened
5 | SS 110/35/10 Basovo | 5,6+10 | 1.19 | 6.19 | 15 | -5 | 0 | 5.88 | 10.88 | 5.38 | opened
| Nom. capacity MV, MVA | 5,6+10 | 0.5 | 6 |  | -5.5 | 0 | 5.88 | 11.38
| Nom. capacity LV, MVA | 5,6+10 | 0.69 | 0.19 | 120 | 0.5 | 0 | 5.88 | 5.38
6 | SS 110/35/10 Belaya | 2*16 | 8.4 | 12 | 120 | -3.6 | 0 | 16.8 | 20.4 | 13.4 | opened
| Nom. capacity MV, MVA | 16 | 3.4 | 0 |  | 3.4 | 0 | 16.8 | 13.4
| Nom. capacity LV, MVA | 16 | 5 | 12 | 120 | -7 | 0 | 16.8 | 23.8
7 | SS 110/35/10 Bobryshovo | 2*6,3 | 1.2 | 1.3 | 120 | -0.1 | 0 | 6.62 | 6.72 | 6.02 | opened
| Nom. capacity MV, MVA | 6.3 | 0.6 |  |  | 0.6 | 0 | 6.62 | 6.02
| Nom. capacity LV, MVA | 6.3 | 0.6 | 1.3 | 120 | -0.7 | 0 | 6.62 | 7.32
8 | SS 110/10 Vinnikovo | 2,5+6,3 | 2.31 | 1.17 | 45 | 1.14 | 0 | 2.63 | 1.49 | 1.49 | opened
9 | SS 110/35/6 Volokno | 40+2*40,5 | 37.58 | 16.8 | 0 | 20.78 | 0 | 84.53 | 63.75 | 61.28 | opened
| Nom. capacity MV, MVA | 40+2*40,5 | 14.33 | 16.8 | 0 | -2.47 | 0 | 84.53 | 87
| Nom. capacity MV, MVA | 40+2*40,5 | 23.25 | 0 | 0 | 23.25 | 0 | 84.53 | 61.28
10 | SS 110/10 Vysokaya* | 2*16 | 28.27 | 3.2 | 15 | 25.07 | 0 | 16.8 | -8.27 | -8.27 | closed*
11 | SS 110/35/10 Glushkovo | 2*10 | 8.7 | 8.04 | 120 | 0.66 | 0 | 10.5 | 9.84 | 8.44 | opened
| Nom. capacity MV, MVA | 10 | 5.2 | 6.6 | 120 | -1.4 | 0 | 10.5 | 11.9
| Nom. capacity LV, MVA | 10 | 3.5 | 1.44 | 80 | 2.06 | 0 | 10.5 | 8.44
12 | SS 110/10 Gorodskaya | 2*25 | 10.4 | 0 | 0 | 10.4 | 0 | 26.25 | 15.85 | 15.85 | opened
13 | SS 110/35/10 Gorshechnoe | 10+16 | 9.41 | 6.52 | 120 | 2.89 | 0 | 10.5 | 7.61 | 7.61 | opened
| Nom. capacity MV, MVA | 10+16 | 6.13 | 6.06 |  | 0.07 | 0 | 10.5 | 10.43
| Nom. capacity LV, MVA | 10+16 | 3.28 | 0.46 | 120 | 2.82 | 0 | 10.5 | 7.68
14 | SS 110/35/10 Dmitriev | 2*10 | 7.09 | 10.4 | 120 | -3.31 | 0 | 10.5 | 13.81 | 8.43 | opened
| Nom. capacity MV, MVA | 10 | 2.02 | 7.4 |  | -5.38 | 0 | 10.5 | 15.88
| Nom. capacity LV, MVA | 10 | 5.07 | 3 | 80 | 2.07 | 0 | 10.5 | 8.43
15 | SS 110/6 Dolgie Budy | 2*10 | 0.8 | 0.5 | 120 | 0.3 | 0 | 10.5 | 10.2 | 10.2 | opened
16 | SS 110/35/10 Zolotukhino | 2*25 | 6.76 | 23.57 | 80 | -16.81 | 0 | 26.25 | 43.06 | 25.59 | opened
| Nom. capacity MV, MVA | 25 | 2.8 | 18.8 |  | -16 | 0 | 26.25 | 42.25
| Nom. capacity LV, MVA | 25 | 3.96 | 3.3 | 120 | 0.66 | 0 | 26.25 | 25.59
17 | SS 110/35/10 Kamyshi | 2*6,3 | 8.59 | 5.45 | 20 | 3.14 | 0 | 6.62 | 3.48 | 3.07 | opened
| Nom. capacity MV, MVA | 6.3 | 7 | 3.45 |  | 3.55 | 0 | 6.62 | 3.07
| Nom. capacity LV, MVA | 6.3 | 1.59 | 2 | 20 | -0.41 | 0 | 6.62 | 7.03
18 | SS 110/35/10 Kastornoe | 15+16 | 14.13 | 6.97 | 120 | 7.16 | 0 | 15.75 | 8.59 | 8.59 | opened
| Nom. capacity MV, MVA | 15+16 | 10.63 | 6.6 |  | 4.03 | 0 | 15.75 | 11.72
| Nom. capacity LV, MVA | 15+16 | 3.5 | 0.37 | 120 | 3.13 | 0 | 15.75 | 12.62
19 | SS 110/35/10 Kilikino | 2*16 | 2.53 | 6.9 | 120 | -4.37 | 0 | 16.8 | 21.17 | 18.51 | opened
| Nom. capacity MV, MVA | 16 | 2.34 | 5 |  | -2.66 | 0 | 16.8 | 19.46
| Nom. capacity LV, MVA | 16 | 0.19 | 1.9 | 120 | -1.71 | 0 | 16.8 | 18.51
20 | SS 110/35/6 Kirovskaya | 2*40 | 53.66 | 16.36 | 120 | 37.3 | 0 | 42 | 4.7 | 4.7 | opened
| Nom. capacity MV, MVA | 40 | 26.67 | 13.06 | 120 | 13.61 | 0 | 42 | 28.39
| Nom. capacity LV, MVA | 40 | 26.99 | 3.3 | 120 | 23.69 | 0 | 42 | 18.31
21 | SS 110/35/10 Klyukva | 2*16 | 3.28 | 1.2 | 120 | 2.08 | 0 | 16.8 | 14.72 | 14.72 | opened
| Nom. capacity MV, MVA | 16 | 0 |  |  | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, MVA | 16 | 3.28 | 1.2 | 120 | 2.08 | 0 | 16.8 | 14.72
22 | SS 110/10 Kompressornaya | 2*40 | 1.11 | 0 | 0 | 1.11 | 0 | 42 | 40.89 | 40.89 | opened
23 | SS 110/35/10 Konyshevka | 10+16 | 9.06 | 8 | 120 | 1.06 | 0 | 10.5 | 9.44 | 9.44 | opened
| Nom. capacity MV, MVA | 10+16 | 6.94 | 5.9 |  | 1.04 | 0 | 10.5 | 9.46
| Nom. capacity LV, MVA | 10+16 | 2.12 | 2.1 |  | 0.02 | 0 | 10.5 | 10.48
24 | SS 110/10 Kotelnaya | 10+25 | 7.8 | 2.1 | 0 | 5.7 | 0 | 10.5 | 4.8 | 4.8 | opened
25 | SS 110/35/10 Kshen | 2*10 | 8.73 | 6.63 | 10 | 2.1 | 0 | 10.5 | 8.4 | 6.59 | opened
| Nom. capacity MV, MVA | 10 | 4.25 | 6.06 |  | -1.81 | 0 | 10.5 | 12.31
| Nom. capacity LV, MVA | 10 | 4.48 | 0.57 | 120 | 3.91 | 0 | 10.5 | 6.59
26 | SS 110/6 Lesnaya | 2*40 | 2.37 | 0 | 0 | 2.37 | 0 | 42 | 39.63 | 39.63 | opened
27 | SS 110/35/10 Lgov | 2*25 | 13.14 | 4 | 120 | 9.14 | 0 | 26.25 | 17.11 | 3.02 | opened
| Nom. capacity MV, MVA | 25 | 1.66 |  |  | 1.66 | 0 | 10.5 | 8.84
| Nom. capacity LV, MVA | 25 | 11.48 | 4 | 120 | 7.48 | 0 | 10.5 | 3.02
28 | SS 110/35/10 Lukashevka | 2*16 | 8.27 | 10.6 | 120 | -2.33 | 0 | 16.8 | 19.13 | 17.03 | opened
| Nom. capacity MV, MVA | 16 | 5.07 | 5.3 |  | -0.23 | 0 | 16.8 | 17.03
| Nom. capacity LV, MVA | 16 | 3.2 | 5.3 | 120 | -2.1 | 0 | 16.8 | 18.9
29 | SS 110/35/10 Lyubostan | 6,3+10 | 5.6 | 13.1 | 120 | -7.5 | 0 | 6.62 | 14.12 | 7.32 | opened
| Nom. capacity MV, MVA | 6,3+10 | 5 | 11.8 |  | -6.8 | 0 | 6.62 | 13.42
| Nom. capacity LV, MVA | 6,3+10 | 0.6 | 1.3 |  | -0.7 | 0 | 6.62 | 7.32
30 | SS 110/35/6 Manturovo | 2*16 | 6.58 | 9.35 | 10 | -2.77 | 0 | 16.8 | 19.57 | 16.86 | opened
| Nom. capacity MV, MVA | 16 | 6.38 | 9.09 |  | -2.71 | 0 | 16.8 | 19.51
| Nom. capacity LV, MVA | 16 | 0.2 | 0.26 | 120 | -0.06 | 0 | 16.8 | 16.86
31 | SS 110/35/10 8th Marta | 6,3+10 | 7.07 | 9.6 | 120 | -2.53 | 0 | 6.62 | 9.15 | 7.41 | opened
| Nom. capacity MV, MVA | 6,3+10 | 5.81 | 6.6 | 120 | -0.79 | 0 | 6.62 | 7.41
| Nom. capacity LV, MVA | 6,3+10 | 1.26 | 3 | 45 | -1.74 | 0 | 6.62 | 8.36
32 | SS 110/10 Martovskaya | 2*6,3 | 0.74 | 0.55 | 120 | 0.19 | 0 | 6.62 | 6.43 | 6.43 | opened
33 | SS 110/35/10 Maryino | 10+25 | 6.15 | 8.11 | 120 | -1.96 | 0 | 10.5 | 12.46 | 11.27 | opened
| Nom. capacity MV, MVA | 10+25 | 3.71 | 4.9 |  | -1.19 | 0 | 10.5 | 11.69
| Nom. capacity LV, MVA | 10+25 | 2.44 | 3.21 |  | -0.77 | 0 | 10.5 | 11.27
34 | SS 110/35/10 Medvenka | 2*10 | 5.95 | 19.22 | 120 | -13.27 | 0 | 10.5 | 23.77 | 8.74 | opened
| Nom. capacity MV, MVA | 10 | 2.07 | 17.1 |  | -15.03 | 0 | 10.5 | 25.53
| Nom. capacity LV, MVA | 10 | 3.88 | 2.12 | 120 | 1.76 | 0 | 10.5 | 8.74
35 | SS 110/6 Neftyanaya | 2*10 | 0.28 |  |  | 0.28 | 0 | 10.5 | 10.22 | 10.22 | opened
36 | SS 110/35/10 Oboyan | 16 + 25 | 16.1 | 26.86 | 120 | -10.76 | 0 | 16.8 | 27.56 | 12.16 | opened
| Nom. capacity MV, MVA | 16 + 25 | 2 | 17.4 | 0 | -15.4 | 0 | 16.8 | 32.2
| Nom. capacity LV, MVA | 16 + 25 | 14.1 | 9.46 |  | 4.64 | 0 | 16.8 | 12.16
37 | SS 110/35/10 Oktyabrskaya | 2*16 | 8.62 | 15.5 | 120 | -6.88 | 0 | 16.8 | 23.68 | 14.72 | opened
| Nom. capacity MV, MVA | 16 | 5.54 | 14.5 |  | -8.96 | 0 | 16.8 | 25.76
| Nom. capacity LV, MVA | 16 | 3.08 | 1 | 120 | 2.08 | 0 | 16.8 | 14.72
38 | SS 110/35/10 Olkhovka | 2*6,3 | 1.92 | 6.31 | 120 | -4.39 | 0 | 6.62 | 11.01 | 7.71 | opened
| Nom. capacity MV, MVA | 6.3 | 1.7 | 5 | 120 | -3.3 | 0 | 6.62 | 9.92
| Nom. capacity LV, MVA | 6.3 | 0.22 | 1.31 | 120 | -1.09 | 0 | 6.62 | 7.71
39 | SS 110/10 Paniki | 2*2,5 | 0.79 | 0.1 | 120 | 0.69 | 0 | 2.63 | 1.94 | 1.94 | opened
40 | SS 110/35/10 Peny | 2*16,0 | 9.63 | 6.9 | 120 | 2.73 | 0 | 16.8 | 14.07 | 14.07 | opened
| Nom. capacity MV, MVA | 16 | 4.37 | 3.5 |  | 0.87 | 0 | 16.8 | 15.93
| Nom. capacity LV, MVA | 16 | 5.26 | 3.4 | 120 | 1.86 | 0 | 16.8 | 14.94
41 | SS 110/35/10 Pribor | 2*25 | 32.12 | 6.5 | 0 | 25.62 | 0 | 26.25 | 0.63 | 0.63 | opened
| Nom. capacity MV, MVA | 25 | 0 |  |  | 0 | 0 | 26.25 | 26.25
| Nom. capacity LV, MVA | 25 | 32.12 | 6.5 | 0 | 25.62 | 0 | 26.25 | 0.63
42 | SS 110/10 Progress | 2*63 | 23.2 | 0 | 0 | 23.2 | 0 | 66.2 | 43 | 43 | opened
43 | SS 110/10 Poultry plant | 6,3+10 | 5.92 | 0 | 0 | 5.92 | 0 | 6.62 | 0.7 | 0.7 | opened
44 | SS 110/35/10 R. Budy | 2*10,0 | 3.4 | 15.7 | 120 | -12.3 | 0 | 10.5 | 22.8 | 15.5 | opened
| Nom. capacity MV, MVA | 10 | 2 | 9.3 |  | -7.3 | 0 | 10.5 | 17.8
| Nom. capacity LV, MVA | 10 | 1.4 | 6.4 |  | -5 | 0 | 10.5 | 15.5
45 | SS 110/35/10 Razinkovo | 6,3+10 | 2.9 | 21.4 | 45 | -18.5 | 0 | 6.62 | 25.12 | 9.27 | opened
| Nom. capacity MV, MVA | 6,3+10 | 1.95 | 17.8 |  | -15.85 | 0 | 6.62 | 22.47
| Nom. capacity LV, MVA | 6,3+10 | 0.95 | 3.6 | 45 | -2.65 | 0 | 6.62 | 9.27
46 | SS 110/35/10 Rudnaya | 2*31,5 | 20.09 | 3.25 | 10 | 16.84 | 0 | 33.1 | 16.26 | 16.26 | opened
| Nom. capacity MV, MVA | 31.5 | 14.23 | 1.7 |  | 12.53 | 0 | 33.1 | 20.57
| Nom. capacity LV, MVA | 31.5 | 5.86 | 1.55 | 120 | 4.31 | 0 | 33.1 | 28.79
47 | SS 110/35/10 Rylsk | 16+25 | 18.95 | 11 | 120 | 7.95 | 0 | 16.8 | 8.85 | 8.85 | opened
| Nom. capacity MV, MVA | 16+25 | 12.9 | 7 |  | 5.9 | 0 | 16.8 | 10.9
| Nom. capacity LV, MVA | 16+25 | 6.05 | 4 | 120 | 2.05 | 0 | 16.8 | 14.75
48 | SS 110/10 Solovyinaya | 2*25 | 6.91 | 0 | 0 | 6.91 | 0 | 26.25 | 19.34 | 19.34 | opened
49 | SS 110/10 STK | 2*10 | 1.91 | 0 | 0 | 1.91 | 0 | 10.5 | 8.59 | 8.59 | opened
50 | SS 110/10 Studenok | 2*6,3 | 3.62 | 0.7 | 120 | 2.92 | 0 | 6.62 | 3.7 | 3.7 | opened
51 | SS 110/35/10 Sudzha | 2*25 | 16.5 | 29 | 120 | -12.5 | 0 | 26.25 | 38.75 | 28.05 | opened
| Nom. capacity MV, MVA | 25 | 6.4 | 17.1 |  | -10.7 | 0 | 26.25 | 36.95
| Nom. capacity LV, MVA | 25 | 10.1 | 11.9 |  | -1.8 | 0 | 26.25 | 28.05
52 | SS 110/35/10 Schyotmash | 2*25 | 13.6 | 0 | 0 | 13.6 | 0 | 26.25 | 12.65 | 12.65 | opened
| Nom. capacity MV, MVA | 25 | 3.9 |  |  | 3.9 | 0 | 26.25 | 22.35
| Nom. capacity LV, MVA | 25 | 9.7 | 0 | 0 | 9.7 | 0 | 26.25 | 16.55
53 | SS 110/35/10 Tyotkino | 2*10 | 5.51 | 3.44 | 120 | 2.07 | 0 | 10.5 | 8.43 | 7.63 | opened
| Nom. capacity MV, MVA | 10 | 1.2 | 2 |  | -0.8 | 0 | 10.5 | 11.3
| Nom. capacity LV, MVA | 10 | 4.31 | 1.44 |  | 2.87 | 0 | 10.5 | 7.63
54 | SS 110/35/10 Tim | 6,3+16 | 5.7 | 9.59 | 120 | -3.89 | 0 | 6.62 | 10.51 | 5.02 | opened
| Nom. capacity MV, MVA | 6,3+16 | 3.6 | 9.09 |  | -5.49 | 0 | 6.62 | 12.11
| Nom. capacity LV, MVA | 6,3+16 | 2.1 | 0.5 | 120 | 1.6 | 0 | 6.62 | 5.02
55 | SS 110/35/10 Uyutnoe | 10+16 | 1.01 | 0.5 | 120 | 0.51 | 0 | 10.5 | 9.99 | 9.83 | opened
| Nom. capacity MV, MVA | 10+16 | 0.67 |  |  | 0.67 | 0 | 10.5 | 9.83
| Nom. capacity LV, MVA | 10+16 | 0.34 | 0.5 | 120 | -0.16 | 0 | 10.5 | 10.66
56 | SS 110/35/10 Fatezh | 2*16 | 6.32 | 17.4 | 120 | -11.08 | 0 | 16.8 | 27.88 | 17.08 | opened
| Nom. capacity MV, MVA | 16 | 2 | 12.8 |  | -10.8 | 0 | 16.8 | 27.6
| Nom. capacity LV, MVA | 16 | 4.32 | 4.6 | 120 | -0.28 | 0 | 16.8 | 17.08
57 | SS 110/35/10 Fosforitnaya | 2*25 | 5.44 | 12.34 | 120 | -6.9 | 0 | 26.25 | 33.15 | 24.41 | opened
| Nom. capacity MV, MVA | 25 | 3.38 | 12.12 |  | -8.74 | 0 | 26.25 | 34.99
| Nom. capacity LV, MVA | 25 | 2.06 | 0.22 | 10 | 1.84 | 0 | 26.25 | 24.41
58 | SS 110/35/10 Khomutovka | 7,5+10 | 5.69 | 6.3 | 80 | -0.61 | 0 | 7.88 | 8.49 | 5.32 | opened
| Nom. capacity MV, MVA | 7,5+10 | 0.73 | 3.9 |  | -3.17 | 0 | 7.88 | 11.05
| Nom. capacity LV, MVA | 7,5+10 | 4.96 | 2.4 | 80 | 2.56 | 0 | 7.88 | 5.32
59 | SS 110/35/10 Cheremisinovo | 2*16 | 6.15 | 9.38 | 10 | -3.23 | 0 | 16.8 | 20.03 | 15.06 | opened
| Nom. capacity MV, MVA | 16 | 4.12 | 9.09 |  | -4.97 | 0 | 16.8 | 21.77
| Nom. capacity LV, MVA | 16 | 2.03 | 0.29 | 120 | 1.74 | 0 | 16.8 | 15.06
60 | SS 110/35/10 Cheremoshki | 2*6,3 | 3.34 | 8.25 | 120 | -4.91 | 0 | 6.62 | 11.53 | 7.09 | opened
| Nom. capacity MV, MVA | 6.3 | 2.56 | 7 |  | -4.44 | 0 | 6.62 | 11.06
| Nom. capacity LV, MVA | 6.3 | 0.78 | 1.25 | 129 | -0.47 | 0 | 6.62 | 7.09
61 | SS 110/35/10 Shumakovo | 2*10 | 4.4 | 13.73 | 120 | -9.33 | 0 | 10.5 | 19.83 | 12.03 | opened
| Nom. capacity MV, MVA | 10 | 3.4 | 11.2 |  | -7.8 | 0 | 10.5 | 18.3
| Nom. capacity LV, MVA | 10 | 1 | 2.53 | 120 | -1.53 | 0 | 10.5 | 12.03
62 | SS 110/35/10 Shchigry | 2*25 | 11.28 | 12.9 | 120 | -1.62 | 0 | 26.5 | 28.12 | 21.55 | opened
| Nom. capacity MV, MVA | 25 | 5.55 | 12.12 |  | -6.57 | 0 | 26.5 | 33.07
| Nom. capacity LV, MVA | 25 | 5.73 | 0.78 | 120 | 4.95 | 0 | 26.5 | 21.55
63 | SS 110/35/10 Yastrebovka | 7,5+10 | 2.56 | 6.31 | 10 | -3.75 | 0 | 7.88 | 11.63 | 6.95 | opened
| Nom. capacity MV, MVA | 7,5+10 | 1.38 | 6.06 |  | -4.68 | 0 | 7.88 | 12.56
| Nom. capacity LV, MVA | 7,5+10 | 1.18 | 0.25 | 10 | 0.93 | 0 | 7.88 | 6.95
64 | SS 35/10 Amosovka | 2*2,5 | 0.31 | 0.2 | 120 | 0.11 | 0 | 2.63 | 2.52 | 2.52 | opened
65 | SS 35/10 Afanasyevka (SPS) | 1,6+2,5 | 0.5 | 0.37 | 120 | 0.13 | 0 | 1.68 | 1.55 | 1.55 | opened
66 | SS 35/10 B.Soldatskoe 2 | 2*4 | 1.4 | 1.1 | 80 | 0.3 | 0 | 4.2 | 3.9 | 3.9 | opened
67 | SS 35/10 B.Zmeinets | 2*1,6 | 0.23 | 1.43 | 120 | -1.2 | 0 | 1.68 | 2.88 | 2.88 | opened
68 | SS 35/10 Bezlesnaya | 2*4 | 1.19 | 6.1 | 0 | -4.91 | 0 | 4.2 | 9.11 | 9.11 | opened
69 | SS 35/10 Bereza | 1,0+2,5 | 0.49 | 0.15 | 120 | 0.34 | 0 | 1.05 | 0.71 | 0.71 | opened
70 | SS 35/10 Blagodat | 2,5+4 | 0.99 | 0.29 | 120 | 0.7 | 0 | 2.63 | 1.93 | 1.93 | opened
71 | SS 35/10 Bykanovo | 2*2,5 | 0.5 | 0.41 | 120 | 0.09 | 0 | 2.63 | 2.54 | 2.54 | opened
72 | SS 35/10 V. Lyubazh | 4+10 | 1.17 | 0.4 | 120 | 0.77 | 0 | 4.2 | 3.43 | 3.43 | opened
73 | SS 35/10 Vesyoloe | 2*1,6 | 0.8 | 0.22 | 120 | 0.58 | 0 | 1.68 | 1.1 | 1.1 | opened
74 | SS 35/10 Volobuevka | 2,5+4 | 0.57 | 0.46 | 120 | 0.11 | 0 | 2.63 | 2.52 | 2.52 | opened
75 | SS 35/10 Voropaevo | 2*4 | 0.87 | 0 | 0 | 0.87 | 0 | 4.2 | 3.33 | 3.33 | opened
76 | SS 35/10 Vostochnaya | 2*6,3 | 4.13 | 0.46 | 120 | 3.67 | 0 | 6.62 | 2.95 | 2.95 | opened
77 | SS 35/10 Vygornoe | 2*2,5 | 1.22 | 0.51 | 120 | 0.71 | 0 | 2.63 | 1.92 | 1.92 | opened
78 | SS 35/10 Gastomlya | 2*1,6 | 0.3 | 0.17 | 120 | 0.13 | 0 | 1.68 | 1.55 | 1.55 | opened
79 | SS 35/10 Gorodok | 2*4 | 1.6 | 0.7 | 45 | 0.9 | 0 | 4.2 | 3.3 | 3.3 | opened
80 | SS 35/10 Guevo | 2*2,5 | 1.2 | 1.69 | 20 | -0.49 | 0 | 2.63 | 3.12 | 3.12 | opened
81 | SS 35/10 Dolzhenkovo | 2*1,6 | 0.4 | 0.38 | 120 | 0.02 | 0 | 1.68 | 1.66 | 1.66 | opened
82 | SS 35/6 Dukhovets | 2,5+4 | 3.33 | 3.5 | 0 | -0.17 | 0 | 2.63 | 2.8 | 2.8 | opened
83 | SS 35/10 Zhernovets | 2*2,5 | 0.4 | 0.26 | 120 | 0.14 | 0 | 2.63 | 2.49 | 2.49 | opened
84 | SS 35/6 Zapadnaya | 2*10 | 12.57 | 2.5 | 0 | 10.07 | 0 | 10.5 | 0.43 | 0.43 | opened
85 | SS 35/10 Zolotukhinskaya KRS | 2*4 | 1.1 | 1.67 | 0 | -0.57 | 0 | 4.2 | 4.77 | 4.77 | opened
86 | SS 35/10 Zuevka | 1,6+2,5 | 0.9 | 0.93 | 45 | -0.03 | 0 | 1.68 | 1.71 | 1.71 | opened
87 | SS 35/10 Ivanino | 2*6,3 | 2.19 | 2.69 | 80 | -0.5 | 0 | 6.62 | 7.12 | 7.12 | opened
88 | SS 35/10 Kalinovka | 1,8+2,5 | 0.68 | 0.5 | 120 | 0.18 | 0 | 1.89 | 1.71 | 1.71 | opened
89 | SS 35/10 Kirilovka | 2*1,6 | 0.29 | 0.52 | 120 | -0.23 | 0 | 1.68 | 1.91 | 1.91 | opened
90 | SS 35/6 Kislinskaya | 2*10 | 16.7 | 6.25 | 20 | 10.45 | 0 | 10.5 | 0.05 | 0.05 | opened
91 | SS 35/10 Fodder plant | 4+6,3 | 0.29 | 0 | 0 | 0.29 | 0 | 4.2 | 3.91 | 3.91 | opened
92 | SS 35/10 Mixed fodder plant | 2*6,3 | 3.31 | 0.21 | 120 | 3.1 | 0 | 6.62 | 3.52 | 3.52 | opened
93 | SS 35/10 Kommunalnaya | 3,2+4 | 2.66 | 1.14 | 80 | 1.52 | 0 | 3.36 | 1.84 | 1.84 | opened
94 | SS 35/10 Korenevo | 4+6,3 | 3.45 | 2.7 | 80 | 0.75 | 0 | 4.2 | 3.45 | 3.45 | opened
95 | SS 35/10 Kremyanoe | 2,5+4 | 0.41 | 0.24 | 120 | 0.17 | 0 | 2.63 | 2.46 | 2.46 | opened
96 | SS 35/10 Krupets | 1,8+2,5 | 1.6 | 0.42 | 120 | 1.18 | 0 | 1.89 | 0.71 | 0.71 | opened
97 | SS 35/10 Kulbaki | 2*2,5 | 0.88 | 0.6 | 120 | 0.28 | 0 | 2.63 | 2.35 | 2.35 | opened
98 | SS 35/10 Kultprosvet | 2*2,5 | 0.18 | 0.17 | 120 | 0.01 | 0 | 2.63 | 2.62 | 2.62 | opened
99 | SS 35/10 Kurchatov | 2*10 | 4.85 | 4.5 | 80 | 0.35 | 0 | 10.5 | 10.15 | 10.15 | opened
100 | SS 35/10 Kutok | 2*2,5 | 0.17 | 0.05 | 120 | 0.12 | 0 | 2.63 | 2.51 | 2.51 | opened
101 | SS 35/10 Linets | 2*2,5 | 0.67 | 0.25 | 120 | 0.42 | 0 | 2.63 | 2.21 | 2.21 | opened
102 | SS 35/10 Luch | 2*6,3 | 2.83 | 0.23 | 120 | 2.6 | 0 | 6.62 | 4.02 | 4.02 | opened
103 | SS 35/10 Lyubimovka-2 | 2*4 | 0.75 | 1.59 | 80 | -0.84 | 0 | 4.2 | 5.04 | 5.04 | opened
104 | SS 35/10 Matveevka | 2*2,5 | 0.67 | 0.08 | 120 | 0.59 | 0 | 2.63 | 2.04 | 2.04 | opened
105 | SS 35/10 Mayak | 2*2,5 | 0.41 | 0.3 | 120 | 0.11 | 0 | 2.63 | 2.52 | 2.52 | opened
106 | SS 35/10 Mikhailovka | 4+6,3 | 2.15 | 1.7 | 80 | 0.45 | 0 | 4.2 | 3.75 | 3.75 | opened
107 | SS 35/10 Murynovka | 2*4 | 0.63 | 0.3 | 120 | 0.33 | 0 | 4.2 | 3.87 | 3.87 | opened
108 | SS 35/10 N. Borki | 2*2,5 | 0.5 | 0.63 | 120 | -0.13 | 0 | 2.63 | 2.76 | 2.76 | opened
109 | SS 35/10 Nikolskaya | 1,6+1,8 | 0.36 | 0.03 | 80 | 0.33 | 0 | 1.68 | 1.35 | 1.35 | opened
110 | SS 35/10 Novaya | 2*2,5 | 1.08 | 0.4 | 120 | 0.68 | 0 | 2.63 | 1.95 | 1.95 | opened
111 | SS 35/10 Orekhovo | 2*2,5 | 0.73 | 0.19 | 120 | 0.54 | 0 | 2.63 | 2.09 | 2.09 | opened
112 | SS 35/10 Orlovka | 2*2,5 | 0.17 | 0.52 | 120 | -0.35 | 0 | 2.63 | 2.98 | 2.98 | opened
113 | SS 35/10 Osotskoe | 2*2,5 | 0.19 | 0.2 | 120 | -0.01 | 0 | 2.63 | 2.64 | 2.64 | opened
114 | SS 35/10 Okhochevka | 4+6,3 | 1.27 | 0.74 | 120 | 0.53 | 0 | 4.2 | 3.67 | 3.67 | opened
115 | SS 35/10 Panino | 2*2,5 | 0.26 | 0.11 | 80 | 0.15 | 0 | 2.63 | 2.48 | 2.48 | opened
116 | SS 35/10 Pervoavgustovka | 2,5+3,2 | 0.74 | 0.52 | 120 | 0.22 | 0 | 2.63 | 2.41 | 2.41 | opened
117 | SS 35/10 Petrinka | 2,5+4 | 1.1 | 0.3 | 120 | 0.8 | 0 | 2.63 | 1.83 | 1.83 | opened
118 | SS 35/10 Platava | 2*2,5 | 1.07 | 0.26 | 120 | 0.81 | 0 | 2.63 | 1.82 | 1.82 | opened
119 | SS 35/10 Pogozhee | 2*1,6 | 0.23 | 0.46 | 120 | -0.23 | 0 | 1.68 | 1.91 | 1.91 | opened
120 | SS 35/10 Porechnoe | 2*4 | 0.5 | 1.16 | 120 | -0.66 | 0 | 4.2 | 4.86 | 4.86 | opened
121 | SS 35/10 Pochepnoe | 2*6,3 | 0.13 | 0.08 | 120 | 0.05 | 0 | 6.62 | 6.57 | 6.57 | opened
122 | SS 35/10 Prigorodnoe | 2*2,5 | 0.52 | 0.3 | 80 | 0.22 | 0 | 2.63 | 2.41 | 2.41 | opened
123 | SS 35/10 Pselets | 2*1,6 | 0.2 | 0.24 | 120 | -0.04 | 0 | 1.68 | 1.72 | 1.72 | opened
124 | SS 35/10 Puzachi | 1,6+4 | 0.4 | 0.43 | 120 | -0.03 | 0 | 1.68 | 1.71 | 1.71 | opened
125 | SS 35/10 Pushkarnoe | 2*2,5 | 0.8 | 0.32 | 120 | 0.48 | 0 | 2.625 | 2.145 | 2.145 | opened
126 | SS 35/10 R.Kolodets | 2*2,5 | 0.6 | 0.44 | 120 | 0.16 | 0 | 2.625 | 2.465 | 2.465 | opened
127 | SS 35/10 Razvetye | 2*4 | 2.38 | 1.03 | 120 | 1.35 | 0 | 4.2 | 2.85 | 2.85 | opened
128 | SS 35/10 V. Reutets | 2*4 | 0.28 | 0.11 | 120 | 0.17 | 0 | 4.2 | 4.03 | 4.03 | opened
129 | SS 35/10 Rozhdestvenka | 2*1,6 | 0.3 | 0.29 | 120 | 0.01 | 0 | 1.68 | 1.67 | 1.67 | opened
130 | SS 35/10 Rubilnik | 2*2,5 | 0.78 | 1.18 | 80 | -0.4 | 0 | 2.625 | 3.025 | 3.025 | opened
131 | SS 35/10 Ryzhkovo | 2*1,6 | 0.23 | 0.08 | 20 | 0.15 | 0 | 1.68 | 1.53 | 1.53 | opened
132 | SS 35/10 Sapogovo | 2*2,5 | 1.57 | 0.6 | 20 | 0.97 | 0 | 2.63 | 1.66 | 1.66 | opened
133 | SS 35/10 Svoboda-selskaya | 2*6,3 | 4.01 | 2.25 | 80 | 1.76 | 0 | 6.615 | 4.855 | 4.855 | opened
134 | SS 35/10 Selektsionnaya | 2*4 | 1.56 | 1.4 | 45 | 0.16 | 0 | 4.2 | 4.04 | 4.04 | opened
135 | SS 35/10 Semyonovka | 2*2,5 | 0.5 | 0 | - | 0.5 | 0 | 2.625 | 2.125 | 2.125 | opened
136 | SS 35/10 Seed plant | 2*2,5 | 0.6 | 0.6 | 120 | 0 | 0 | 2.63 | 2.63 | 2.63 | opened
137 | SS 35/10 Snagost | 2*4 | 1.26 | 0.05 | 10 | 1.21 | 0 | 4.2 | 2.99 | 2.99 | opened
138 | SS 35/10 SOM | 1,6+4 | 1.56 | 0.08 | 10 | 1.48 | 0 | 1.68 | 0.2 | 0.2 | opened
139 | SS 35/10 Sosnovy Bor | 3,2+4 | 0.69 | 0.69 | 120 | 0 | 0 | 3.36 | 3.36 | 3.36 | opened
140 | SS 35/10 Stakanovo | 2*2,5 | 1.23 | 0.58 | 80 | 0.65 | 0 | 2.625 | 1.975 | 1.975 | opened
141 | SS 35/10 Starkovo | 2*1,6 | 0.43 | 0.2 | 80 | 0.23 | 0 | 1.68 | 1.45 | 1.45 | opened
142 | SS 35/10 Starshee | 2*1,6 | 0.31 | 0.2 | 120 | 0.11 | 0 | 1.68 | 1.57 | 1.57 | opened
143 | SS 35/10 Teplitsy | 2*4 | 2.25 | 1.08 | 45 | 1.17 | 0 | 4.2 | 3.03 | 3.03 | opened
144 | SS 35/10 Turovka | 2*2,5 | 0.8 | 0.6 | 120 | 0.2 | 0 | 2.63 | 2.43 | 2.43 | opened
145 | SS 35/10 Uspenka | 2*2,5 | 1.19 | 1 | 80 | 0.19 | 0 | 2.63 | 2.44 | 2.44 | opened
146 | SS 35/6 Tsentralnaya | 2*25 | 24.9 | 5 | 10 | 19.9 | 0 | 26.25 | 6.35 | 6.35 | opened
147 | SS 35/10 Chermoshnoe | 2*2,5 | 0.4 | 0.5 | 120 | -0.1 | 0 | 4.2 | 4.3 | 4.3 | opened
148 | SS 35/10 Shatalovka | 2,5+4 | 0.31 | 0.21 | 80 | 0.1 | 0 | 2.625 | 2.525 | 2.525 | opened
149 | SS 35/10 Shipy | 2*2,5 | 0.2 | 0.3 | 120 | -0.1 | 0 | 2.625 | 2.725 | 2.725 | opened
150 | SS 35/10 Elevator | 4+6,3 | 2.21 | 0.6 | 120 | 1.61 | 0 | 4.2 | 2.59 | 2.59 | opened
151 | SS 35/10 Yugo-Zapadnaya | 2*10 | 9.28 | 4.7 | 80 | 4.58 | 0 | 10.5 | 5.92 | 5.92 | opened
152 | SS 35/10 Plant of reinforced-concrete products | 2*2,5 | 1.97 | 3.9 | 120 | -1.93 | 0 | 2.625 | 4.555 | 4.555 | opened
| TOTAL: | 3185.9 | 763.705 | 777.41 | [5 empty] | 1191.575
| deficit | [8 empty] | -8.27
| proficit | [8 empty] | 1183.31
*Note: Capacity deficit over SS Vasokaya is grounded by transfer of loads from SS Tsebtralnaya and will be removed after putting into operation
of switschgear-10 kv at SS Tsentralnaya
Deputy Director for Technical Issues -
|  | Chief Engineer | [6 empty] | A.N. Rudnevsky