## Орел
No. | Object of main substation, voltage class | Current deficit | [8 empty] | Note
|  | Installed power capacity of transformers Sуst., including their number, pcs/ MVA | Summary total capacity of Central Substation following the results of measurements of load maximum Sмах , MVA | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Transmission capacity, MVA | Deficit/proficit of Main Substation, MVA
|  |  |  | МVА | Мin.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | SS 35/10 kv Almazovo | 2.5 | 0.38 | 0.83 | 30 | 0.83 | 0 | 0.83 | 0.45 | 0.45 | opened
2 | SS 35/10 kv Voronets | 2.5 | 0.31 | 0.91 | 90 | 0.91 | 0 | 0.91 | 0.6 | 0.6 | opened
3 | SS 35/10 kv Gostoml | 2.5 | 0.65 | 0.66 | 120 | 0.66 | 0 | 0.66 | 0.01 | 0.01 | opened
4 | SS 35/10 kv Gubkino | 3.2 | 0.47 | 1.56 | 30 | 1.56 | 0 | 1.56 | 1.09 | 1.09 | opened
5 | SS 35/10 kv Devyatino | 1.6 | 0.31 | 0.71 | 45 | 0.71 | 0 | 0.71 | 0.4 | 0.4 | opened
6 | SS 35/10 kv Kamenka | 2.5 | 0.76 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 0.84 | 0.84 | opened
7 | SS 35/10 kv Kozminskaya | 2.5 | 0.28 | 1.29 | 45 | 1.29 | 0 | 1.29 | 1.01 | 1.01 | opened
8 | SS 110/35/10 kv Maloarkhangelskaya | 10 | 5.93 | 6.14 | 60 | 0.21 | 0 | 6.14 | 0.21 | 0.21 | opened
| Nom. capacity MV, MVA | 10 | 2.66 | 1.94 | 60
| Nom. capacity LV, MVA | 10 | 3.3 | 4.2 | 60 | 0.9 | 0 | 4.2 | 0.9
9 | SS 110/35/10 kv Novopolevo | 16 | 2.74 | 3.71 | 30 | 3.71 | 0 | 3.71 | 0.97 | -0.27 | closed
| Nom. capacity MV, MVA | 16 | 1.38 | 2.6 | 30
| Nom. capacity LV, MVA | 16 | 1.38 | 1.11 | 30 | 1.11 | 0 | 1.11 | -0.27
10 | SS 35/10 kv Nikolskaya | 2.5 | 0.6 | 1.33 | 45 | 1.33 | 0 | 1.33 | 0.73 | 0.73 | opened
11 | SS 35/10 kv Paramonovo | 1.8 | 0.15 | 0.48 | 90 | 0.48 | 0 | 0.48 | 0.33 | 0.33 | opened
12 | SS 35/10 kv Senkovo | 1.6 | 0.31 | 1.29 | 30 | 1.29 | 0 | 1.29 | 0.98 | 0.98 | opened
13 | SS 35/10 kv Somovo | 2.5 | 0.34 | 0.96 | 60 | 0.96 | 0 | 0.96 | 0.62 | 0.62 | opened
14 | SS 110/35/10 kv Trosna | 16 | 2.53 | 4.16 | 45 | 4.16 | 0 | 4.16 | 1.63 | 0.72 | opened
| Nom. capacity MV, MVA | 16 | 1.46 | 2.36 | 45
| Nom. capacity LV, MVA | 16 | 1.08 | 1.8 | 45 | 1.8 | 0 | 1.8 | 0.72
15 | SS 35/10 kv Shablykino | 5.6 | 0.09 | 0.8 | 90 | 0.8 | 0 | 0.8 | 0.71 | 0.71 | opened
16 | SS 35/10 kv Yuryevo | 2.5 | 0.18 | 1.07 | 60 | 1.07 | 0 | 1.07 | 0.89 | 0.89 | opened
17 | SS 110/35/10 kv Region V | 10 | 3.77 | 5.4 | 120 | 5.4 | 0 | 5.4 | 1.63 | 1.56 | opened
| Nom. capacity MV, MVA | 10 | 0 | 0
| Nom. capacity LV, MVA | 10 | 3.84 | 5.4 | 120 | 5.4 | 0 | 5.4 | 1.56
18 | SS 110/10 kv Pishchevaya | 6.3 | 2.57 | 1.875 | 60 | 1.875 | 0 | 1.875 | -0.695 | -0.695 | closed
19 | SS 110/10 kv Telchye | 3.2 | 1.65 | 1.46 | 120 | 1.46 | 0 | 1.46 | -0.19 | -0.19 | closed
20 | SS 110/10 kv B.Chern | 2.5 | 0.31 | 1 | 120 | 1 | 0 | 1 | 0.69 | 0.69 | opened
21 | SS 35/10 kv Bashkatovo | 1.6 | 0.37 | 0.8 | 120 | 0.8 | 0 | 0.8 | 0.43 | 0.43 | opened
22 | SS 35/10 kv Vysokoe | 1.6 | 0.28 | 1.24 | 120 | 1.24 | 0 | 1.24 | 0.96 | 0.96 | opened
23 | SS 35/10 kv Gladkoe | 2.5 | 0.43 | 1.46 | 120 | 1.46 | 0 | 1.46 | 1.03 | 1.03 | opened
24 | SS 35/10 kv Lykovo | 2.5 | 0.82 | 1.24 | 120 | 1.24 | 0 | 1.24 | 0.42 | 0.42 | opened
25 | SS 35/6 kv Sugar mill | 4 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | opened
26 | SS 35/10 kv Gnezdilivo | 1.6 | 0.3 | 0.68 | 120 | 0.68 | 0 | 0.68 | 0.38 | 0.38 | opened
27 | SS 35/10 kv Koptevo | 2.5 | 0.28 | 0.44 | 120 | 0.44 | 0 | 0.44 | 0.16 | 0.16 | opened
28 | SS 110/35/10/6 kv Meat processing factory | 10 | 1.57 | 2.13 | 120 | 2.13 | 0 | 2.13 | 0.56 | 0.32 | opened
| Nom. capacity MV, MVA | 10 | 0 | 0 | 0
| Nom. capacity LV, MVA | 10 | 1.81 | 2.13 | 120 | 2.13 | 0 | 2.13 | 0.32
29 | SS 110/35/10 kv Shatilovo | 10 | 1.43 | 0.69 | 120 | 0.69 | 0 | 0.69 | -0.74 | -0.74 | closed
| Nom. capacity MV, MVA | 10 | 0.53 | 0.16 | 180 | 0.16 | 0 | 0.16 | -0.37
| Nom. capacity LV, MVA | 10 | 0.91 | 0.53 | 120 | 0.53 | 0 | 0.53 | -0.38
30 | SS 110/35/10 kv Sovkhoznaya | 10 | 6.46 | 8.96 | 120 | 8.96 | 0 | 8.96 | 2.5 | 1.23 | opened
| Nom. capacity MV, MVA | 10 | 5.39 | 6.62 | 120 | 6.62 | 0 | 6.62 | 1.23
| Nom. capacity LV, MVA | 10 | 1.1 | 2.34 | 120 | 2.34 | 0 | 2.34 | 1.24
31 | SS 35/10 kv Danilovskaya | 1.6 | 0.45 | 0.54 | 120 | 0.54 | 0 | 0.54 | 0.09 | 0.09 | opened
32 | SS 35/10 kv Korseevo | 1.8 | 0.02 | 0.88 | 120 | 0.88 | 0 | 0.88 | 0.86 | 0.86 | opened
33 | SS 35/10 kv Lipovets | 2.5 | 0.82 | 1.39 | 120 | 1.39 | 0 | 1.39 | 0.57 | 0.57 | opened
34 | SS 35/10 kv Misaylovo | 1.6 | 0.47 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 1.13 | 1.13 | opened
35 | SS 35/10 kv Mikhaylovka | 2.5 | 0.26 | 0.31 | 80 | 0.31 | 0 | 0.31 | 0.05 | 0.05 | opened
36 | SS 35/10 kv Pankovo | 1.8 | 0.53 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 1.07 | 1.07 | opened
37 | SS 35/10 kv Sudbishchi | 2.5 | 0.73 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 0.87 | 0.87 | opened
38 | SS 35/10 kv Tim | 1.6 | 0.71 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 0.89 | 0.89 | opened
39 | SS 35/10 kv Topki | 1 | 0.36 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 1.24 | 1.24 | opened
40 | SS 35/10 kv Yarishche | 2.5 | 0.4 | 1.6 | 24 hours | 1.6 | 0 | 1.6 | 1.2 | 1.2 | opened
41 | SS 110/10 kv Alshanskaya | 10+10 | 6.6 | 3.88 | 30 | 2.72 | 0 | 10.5 | 7.78 | 7.78 | opened
42 | SS 35/10 kv Arkhangelskaya | 2,5+2,5 | 0.4 | 0.93 | 90 | -0.53 | 0 | 2.625 | 3.155 | 3.155 | opened
43 | SS 35/10 kv Atyaevskaya | 1,6+2,5 | 0.56 | 0 | - | 0.56 | 0 | 1.68 | 1.12 | 1.12 | opened
44 | SS 110/35/10 kv Bogoroditskaya | 10+10 | 2.9 | 3.06 | 90 | -0.16 | 0 | 10.5 | 10.66 | 10.29 | opened
45 | Nom. capacity MV, MVA | 10+10 | 2.64 | 2.43 | 90 | 0.21 | 0 | 10.5 | 10.29
| Nom. capacity LV, MVA | 10+10 | 0.23 | 0.63 | 90 | -0.4 | 0 | 10.5 | 10.9
| SS 35/10 kv Baklanovo | 1,6+1,6 | 0.83 | 0.64 | 60 | 0.19 | 0 | 1.68 | 1.49 | 1.49 | opened
46 | SS 35/10 kv Biofactory | 6,3+6,3 | 2.88 | 2.05 | 90 | 0.83 | 0 | 6.615 | 5.785 | 5.785 | opened
47 | SS 110/10 kv Volodarskaya | 2,5+6,3 | 3.85 | 1.46 | 30 | 2.39 | 0 | 2.625 | 0.235 | 0.235 | opened
48 | SS 110/10 kv Vostochnaya | 15+15 | 14.87 | 5.87 | 120 | 9 | 0 | 15.75 | 6.75 | 6.75 | opened
49 | SS 110/35/10 kv Dmitrovskaya | 10+10 | 3.64 | 0.45 | 60 | 3.19 | 0 | 10.5 | 7.31 | 7.31 | opened
50 | Nom. capacity MV, MVA | 10+10 | 0.31 | 0 | 0 | 0.31 | 0 | 10.5 | 10.19
| Nom. capacity LV, MVA | 10+10 | 3.32 | 0.45 | 60 | 2.87 | 0 | 10.5 | 7.63
| SS 110/10 kv Zheleznodorozhnaya | 16+16 | 12.57 | 3.98 | 180 | 8.59 | 0 | 16.8 | 8.21 | 8.21 | opened
51 | SS 35/10 kv Zhilyaevskaya | 1,8+1,8 | 1.06 | 0.64 | 60 | 0.42 | 0 | 1.89 | 1.47 | 1.47 | opened
52 | SS 110/6 kv Zavodskaya | 40+25 | 16.07 | 4.39 | 150 | 11.68 | 0 | 26.25 | 14.57 | 14.57 | opened
53 | SS 110/6 kv Zapadnaya | 25+25 | 25.03 | 0 | 120 | 25.03 | 0 | 26.25 | 1.22 | 1.22 | opened
54 | SS 35/10 kv Zvyaginki | 2,5+2,5 | 2.08 | 1.48 | 60 | 0.6 | 0 | 2.625 | 2.025 | 2.025 | opened
55 | SS 35/10 kv Ilyinskaya | 3,2+1,6 | 1.16 | 1.18 | 30 | -0.02 | 0 | 1.68 | 1.7 | 1.7 | opened
56 | SS 110/35/10 kv Kulikovskaya | 10+10 | 5.28 | 1.44 | 90 | 3.84 | 0 | 10.5 | 6.66 | 6.66 | opened
57 | Nom. capacity MV, MVA | 10+10 | 1.49 | 1 | 90 | 0.49 | 0 | 10.5 | 10.01
| Nom. capacity LV, MVA | 10+10 | 3.82 | 0.44 | 90 | 3.38 | 0 | 10.5 | 7.12
| SS 110/35/10 kv Kromskaya | 16+16 | 8.63 | 6.83 | 45 | 1.8 | 0 | 16.8 | 15 | 14.42 | opened
58 | Nom. capacity MV, MVA | 16+16 | 5 | 5 | 45 | 0 | 0 | 16.8 | 16.8
| Nom. capacity LV, MVA | 16+16 | 4.21 | 1.83 | 45 | 2.38 | 0 | 16.8 | 14.42
| SS 35/10 kv Krasnoarmeyskaya | 2,5+2,5 | 1.16 | 0.95 | 30 | 0.21 | 0 | 2.625 | 2.415 | 2.415 | opened
59 | SS 35/10 kv Kurakinskaya | 1,6+1,8 | 0.83 | 0 | - | 0.83 | 0 | 1.68 | 0.85 | 0.85 | opened
60 | SS 35/10 kv Kutafino | 1,6+1,6 | 0.22 | 0.83 | 30 | -0.61 | 0 | 1.68 | 2.29 | 2.29 | opened
61 | SS 35/10 kv Lovchikovo | 2,5+2,5 | 0.55 | 1.59 | 30 | -1.04 | 0 | 2.625 | 3.665 | 3.665 | opened
62 | SS 35/10 kv Lubyanskaya | 1+1,6 | 0.43 | 0.47 | 60 | -0.04 | 0 | 1.05 | 1.09 | 1.09 | opened
63 | SS 35/10 kv Lukovets | 1,8+2,5 | 0.42 | 0.99 | 90 | -0.57 | 0 | 1.89 | 2.46 | 2.46 | opened
64 | SS 35/10 kv Malorkhangelskaya | 5,6+5,6 | 0.54 | 1.7 | 30 | -1.16 | 0 | 5.88 | 7.04 | 7.04 | opened
65 | SS 110/35/10 kv Naryshkinskaya | 10+10 | 7.38 | 1.41 | 90 | 5.97 | 0 | 10.5 | 4.53 | 4.53 | opened
66 | Nom. capacity MV, MVA | 10+10 | 1.3 | 0.86 | 90 | 0.44 | 0 | 10.5 | 10.06
| Nom. capacity LV, MVA | 10+10 | 6.09 | 0.55 | 90 | 5.54 | 0 | 10.5 | 4.96
| SS 35/10 kv Nizhnyaya Sloboda | 2,5+5,6 | 0.58 | 1.63 | 45 | -1.05 | 0 | 2.625 | 3.675 | 3.675 | opened
67 | SS 35/10 kv Novopetrovka | 2,5+1,6 | 0.45 | 0.73 | 60 | -0.28 | 0 | 1.68 | 1.96 | 1.96 | opened
68 | SS 35/10 kv Putimets | 2,5+2,5 | 0.82 | 1.53 | 90 | -0.71 | 0 | 2.625 | 3.335 | 3.335 | opened
69 | SS 110/10 kv Pishchevaya | 40+25 | 6.16 | 2.22 | 60 | 3.94 | 0 | 26.25 | 22.31 | 22.31 | opened
70 | SS 35/10 kv Ryzhkovo | 2,5+2,5 | 0.49 | 0.65 | 90 | -0.16 | 0 | 2.625 | 2.785 | 2.785 | opened
71 | SS 110/35/10 kv Sverdlovskaya | 10+10 | 3.17 | 1.98 | 45 | 1.19 | 0 | 10.5 | 9.31 | 9.21 | opened
72 | Nom. capacity MV, MVA | 10+10 | 1.32 | 1.41 | 45 | -0.09 | 0 | 10.5 | 10.59
| Nom. capacity LV, MVA | 10+10 | 1.86 | 0.57 | 45 | 1.29 | 0 | 10.5 | 9.21
| SS 35/10 kv Streletskaya | 4+4 | 2.24 | 0.91 | 90 | 1.33 | 0 | 4.2 | 2.87 | 2.87 | opened
73 | SS 110/35/10/6 kv Sovetskaya | 20+20+25+40 | 29.48 | 3.86 | 180 | 25.62 | 0 | 68.25 | 42.63 | 19 | opened
74 | Nom. capacity MV, MVA | 20+20 | 7.1 | 5.1 | 90 | 2 | 0 | 21 | 19
| Nom. capacity LV, MVA | 20+20+25+40 | 22.28 | 3.86 | 180 | 18.42 | 0 | 68.25 | 49.83
| SS 35/10 kv Soskovskaya | 4+3,2 | 1.49 | 0.64 | 90 | 0.85 | 0 | 3.36 | 2.51 | 2.51 | opened
75 | SS 35/10 kv Trosna | 5,6+3,2 | 0.81 | 1.76 | 30 | -0.95 | 0 | 3.36 | 4.31 | 4.31 | opened
76 | SS 110/10 kv Khimmash | 25+25 | 8.13 | 1.51 | 120 | 6.62 | 0 | 26.25 | 19.63 | 19.63 | opened
77 | SS 35/10kv Khleboprodukty | 5,6+6,3 | 1.12 | 0 | - | 1.12 | 0 | 5.88 | 4.76 | 4.76 | opened
78 | SS 35/10 kv Khotynetskaya | 4+2,5 | 2.47 | 1.49 | 80 | 0.98 | 0 | 2.625 | 1.645 | 1.645 | opened
79 | SS 35/10 kv Khotkovo | 1,6+1,6 | 0.53 | 1.03 | 80 | -0.5 | 0 | 1.68 | 2.18 | 2.18 | opened
80 | SS 110/10/6 kv Tsentralnaya | 25+25 | 13.82 | 3.46 | 135 | 10.36 | 0 | 26.25 | 15.89 | 15.89 | opened
81 | SS 110/35/10 kv Shablykino | 6,3+6,3 | 2.37 | 1.36 | 30 | 1.01 | 0 | 6.615 | 5.605 | 5.605 | opened
82 | Nom. capacity MV, MVA | 6,3+6,3 | 0.97 | 0.54 | 30 | 0.43 | 0 | 6.615 | 6.185
| Nom. capacity LV, MVA | 6,3+6,3 | 1.42 | 0.82 | 30 | 0.6 | 0 | 6.615 | 6.015
| SS 110/35/10 kv Shakhovo | 10+10 | 2.51 | 2.55 | 120 | -0.04 | 0 | 10.5 | 10.54 | 10.07 | opened
83 | Nom. capacity MV, MVA | 10+10 | 0.82 | 0.39 | 120 | 0.43 | 0 | 10.5 | 10.07
| Nom. capacity LV, MVA | 10+10 | 1.7 | 2.16 | 120 | -0.46 | 0 | 10.5 | 10.96
| SS 35/10 kv Shepino | 2,5+1,6 | 1.4 | 1.1 | 120 | 0.3 | 0 | 1.68 | 1.38 | 1.38 | opened
84 | SS 110/10/6 kv Yugo-Vostochnaya | 25+25 | 10.72 | 0.74 | 60 | 9.98 | 0 | 26.25 | 16.27 | 16.27 | opened
85 | SS 110/10 kv Yuzhnaya | 10+10 | 9.07 | 1.05 | 90 | 8.02 | 0 | 10.5 | 2.48 | 2.48 | opened
86 | SS 220/110/10 kv Mtsensk | 40+40 | 9.81 | 0 | - | 9.81 | 0 | 42 | 32.19 | 32.19 | opened
87 | SS 110/35/10 kv Kommash | 10+16 | 10.51 | 4.65 | 90 | 5.86 | 0 | 10.5 | 4.64 | 4.64 | opened
88 | Nom. capacity MV, MVA | 10+16 | 0 | 0 |  | 0 | 0 | 10.5 | 10.5
| Nom. capacity LV, MVA | 10+16 | 10.5 | 4.65 | 90 | 5.85 | 0 | 10.5 | 4.65
| SS 110/35/10 kv Novosergievka | 6,3+10 | 2.55 | 4.13 | 120 | -1.58 | 0 | 6.615 | 8.195 | 6.695 | opened
89 | Nom. capacity MV, MVA | 6,3+10 | 2.32 | 2.4 | 120 | -0.08 | 0 | 6.615 | 6.695
| Nom. capacity LV, MVA | 6,3+10 | 0.24 | 1.73 | 120 | -1.49 | 0 | 6.615 | 8.105
| SS 110/10 kv 1 Voin | 6,3+6,3 | 2.33 | 1.83 | 120 | 0.5 | 0 | 6.615 | 6.115 | 6.115 | opened
90 | SS 110/35/10 kv Zalegoshch | 10+16 | 5.94 | 3.95 | 120 | 1.99 | 0 | 10.5 | 8.51 | 8.51 | opened
91 | Nom. capacity MV, MVA | 10+16 | 2.48 | 2.39 | 120 | 0.09 | 0 | 10.5 | 10.41
| Nom. capacity LV, MVA | 10+16 | 3.43 | 1.56 | 120 | 1.87 | 0 | 10.5 | 8.63
| SS 110/10 kv Kochety | 2,5+2,5 | 0.34 | 0.66 | 120 | -0.32 | 0 | 2.625 | 2.945 | 2.945 | opened
92 | SS 110/35/10 kv Bolkhov | 10+10 | 8.61 | 4.1 | 120 | 4.51 | 0 | 10.5 | 5.99 | 5.99 | opened
93 | Nom. capacity MV, MVA | 10+10 | 3.01 | 2.45 | 120 | 0.56 | 0 | 10.5 | 9.94
| Nom. capacity LV, MVA | 10+10 | 5.6 | 1.65 | 120 | 3.95 | 0 | 10.5 | 6.55
| SS 110/35/10 kv Novosil | 10+10 | 4.69 | 2.98 | 120 | 1.71 | 0 | 10.5 | 8.79 | 8.79 | opened
94 | Nom. capacity MV, MVA | 10+10 | 2.4 | 1.46 | 120 | 0.94 | 0 | 10.5 | 9.56
| Nom. capacity LV, MVA | 10+10 | 2.29 | 1.52 | 120 | 0.77 | 0 | 10.5 | 9.73
| SS 110/35/10 kv Znamenskaya | 10+10 | 2.2 | 1.78 | 120 | 0.42 | 0 | 10.5 | 10.08 | 10.08 | opened
95 | Nom. capacity MV, MVA | 10+10 | 0.49 | 0.34 | 120 | 0.15 | 0 | 10.5 | 10.35
| Nom. capacity LV, MVA | 10+10 | 1.71 | 1.44 | 120 | 0.27 | 0 | 10.5 | 10.23
| SS 35/10 kv Apalkovo | 1,8+1,8 | 0.43 | 0.48 | 120 | -0.05 | 0 | 1.89 | 1.94 | 1.94 | opened
96 | SS 35/10 kv Podberyozovo | 4+1 | 0.26 | 0.59 | 120 | -0.33 | 0 | 1.05 | 1.38 | 1.38 | opened
97 | SS 35/10 kv Protasovo | 2,5+1,6 | 0.51 | 0 |  | 0.51 | 0 | 1.68 | 1.17 | 1.17 | opened
98 | SS 35/10 kv Alyoshnya | 1+1 | 0.34 | 0.24 | 120 | 0.1 | 0 | 1.05 | 0.95 | 0.95 | opened
99 | SS 35/10 kv Lomovoe | 2,5+2,5 | 1 | 0 | - | 1 | 0 | 2.625 | 1.625 | 1.625 | opened
100 | SS 35/10 kv Mokhovoe | 2,5+4 | 0.91 | 0.63 | 120 | 0.28 |  | 2.625 | 2.345 | 2.345 | opened
101 | SS 35/10 kv Mishkovo 2 | 1,6+1,6 | 0.23 | 0.47 | 120 | -0.24 | 0 | 1.68 | 1.92 | 1.92 | opened
102 | SS 35/10 kv Vyazovoe | 2,5+2,5 | 0.32 | 0 | - | 0.32 | 0 | 2.625 | 2.305 | 2.305 | opened
103 | SS 35/10 kv Krasnoznamenka | 2,5+2,5 | 1.1 | 0.67 | 120 | 0.43 | 0 | 2.625 | 2.195 | 2.195 | opened
104 | SS 35/10 kv Fatnevo | 1,6+1,6 | 0.5 | 0.37 | 120 | 0.13 | 0 | 1.68 | 1.55 | 1.55 | opened
105 | SS 35/10 kv Varvarinka | 2,5+2,5 | 0.63 | 0.69 | 120 | -0.06 | 0 | 2.625 | 2.685 | 2.685 | opened
106 | SS 35/10 kv Odinok | 1,6+1,6 | 0.38 | 0 | - | 0.38 | 0 | 1.68 | 1.3 | 1.3 | opened
107 | SS 35/10 kv Uzkoe | 1,6+1 | 0.21 | 0.25 | 120 | -0.04 | 0 | 1.05 | 1.09 | 1.09 | opened
108 | SS 35/10 kv Korsakovo | 2,5+4 | 0.76 | 0.69 | 120 | 0.07 | 0 | 2.625 | 2.555 | 2.555 | opened
109 | SS 35/10 kv Paramonovo | 4+2,5 | 0.88 | 0.76 | 120 | 0.12 | 0 | 2.625 | 2.505 | 2.505 | opened
110 | SS 35/10 kv Speshnevo | 1,6+1,6 | 0.22 | 0 | - | 0.22 | 0 | 1.68 | 1.46 | 1.46 | opened
111 | SS 110/35/10 kv Verkhovye I | 16+10 | 8.57 | 3.65 | 120 | 4.92 | 0 | 10.5 | 5.58 | 5.58 | opened
112 | Nom. capacity MV, MVA | 16+10 | 3.01 | 2.05 | 120 | 0.96 | 0 | 10.5 | 9.54
| Nom. capacity LV, MVA | 16+10 | 5.62 | 1.6 | 120 | 4.02 | 0 | 10.5 | 6.48
| SS 110/35/10 kv Verkhovye II | 40+40 | 16.92 | 0.3 | - | 16.62 | 0 | 42 | 25.38 | 25.38 | opened
113 | Nom. capacity MV, MVA | 40+40 | 0.47 | 0.3 | - | 0.17 | 0 | 42 | 41.83
| Nom. capacity LV, MVA | 40+40 | 16.48 | 0 | - | 16.48 | 0 | 42 | 25.52
| SS 110/35/10 kv Dolgoe | 16+10 | 7.02 | 3.38 | 120 | 3.64 | 0 | 10.5 | 6.86 | 6.86 | opened
114 | Nom. capacity MV, MVA | 16+10 | 2.67 | 2.38 | 120 | 0.29 | 0 | 10.5 | 10.21
| Nom. capacity LV, MVA | 16+10 | 4.36 | 1 | 120 | 3.36 | 0 | 10.5 | 7.14
| SS 110/35/10 kv Kolpny-110 | 10+16 | 5.8 | 2.79 | 120 | 3.01 | 0 | 10.5 | 7.49 | 7.49 | opened
115 | Nom. capacity MV, MVA | 10+16 | 3.92 | 2.46 | 120 | 1.46 | 0 | 10.5 | 9.04
| Nom. capacity LV, MVA | 10+16 | 1.86 | 0.33 | 120 | 1.53 | 0 | 10.5 | 8.97
| SS 110/35/10 kv Kr. Zarya | 10+10 | 5.24 | 1.54 | 120 | 3.7 | 0 | 10.5 | 6.8 | 6.8 | opened
116 | Nom. capacity MV, MVA | 10+10 | 1.69 | 1.29 | 120 | 0.4 | 0 | 10.5 | 10.1
| Nom. capacity LV, MVA | 10+10 | 3.56 | 0.25 | 120 | 3.31 | 0 | 10.5 | 7.19
| SS 110/35/10 kv Pokrovskaya | 10+10 | 5.84 | 2.84 | 120 | 3 | 0 | 10.5 | 7.5 | 7.5 | opened
117 | Nom. capacity MV, MVA | 10+10 | 2.41 | 2.12 | 120 | 0.29 | 0 | 10.5 | 10.21
| Nom. capacity LV, MVA | 10+10 | 3.45 | 0.72 | 120 | 2.73 | 0 | 10.5 | 7.77
| SS 110/35/6 kv Cherkasskaya | 40+25 | 29.08 | 13.39 | 120 | 15.69 | 0 | 26.25 | 10.56 | 10.56 | opened
118 | Nom. capacity MV, MVA | 40+25 | 13.36 | 10.84 | 120 | 2.52 | 0 | 26.25 | 23.73
| Nom. capacity LV, MVA | 40+25 | 15.87 | 2.55 | 120 | 13.32 | 0 | 26.25 | 12.93
| SS 110/6 kv Plastmass | 16+16 | 10.73 | 0 | - | 10.73 | 0 | 16.8 | 6.07 | 6.07 | opened
119 | SS 110/10 kv PM | 10+10 | 5.07 | 0 | - | 5.07 | 0 | 10.5 | 5.43 | 5.43 | opened
120 | SS 110/10 kv Rechitsa | 6,3+6,3 | 1.81 | 1.85 | 120 | -0.04 | 0 | 6.615 | 6.655 | 6.655 | opened
121 | SS 110/10 kv R.Brod | 5,6+10 | 1.69 | 0.29 | 120 | 1.4 | 0 | 5.88 | 4.48 | 4.48 | opened
122 | SS 35/10 kv Alekseevskaya | 1,6+1,6 | 0.61 | 0.13 | 120 | 0.48 | 0 | 1.68 | 1.2 | 1.2 | opened
123 | SS 35/10 kv V.Dubrava | 2,5+2,5 | 1.6 | 0.65 | 120 | 0.95 | 0 | 2.625 | 1.675 | 1.675 | opened
124 | SS 35/10 kv V.Olshanoe | 4+2,5 | 0.76 | 0.43 | 120 | 0.33 | 0 | 2.625 | 2.295 | 2.295 | opened
125 | SS 35/10 kv Vvedenskoe | 1,6+1,8 | 1.1 | 0.56 | 120 | 0.54 | 0 | 1.68 | 1.14 | 1.14 | opened
126 | SS 35/10 kv Droskovo | 4+2,5 | 1.34 | 0 | - | 1.34 | 0 | 2.625 | 1.285 | 1.285 | opened
127 | SS 35/10 kv Kolpny-35 | 6,3+6,3 | 2.44 | 0.39 | 120 | 2.05 | 0 | 6.615 | 4.565 | 4.565 | opened
128 | SS 35/10 kv Krutoe | 2,5+1,6 | 1.59 | 0.87 | 120 | 0.72 | 0 | 1.68 | 0.96 | 0.96 | opened
129 | SS 35/10 kv Mezentsevo | 4+6,3 | 3.15 | 1.11 | 80 | 2.04 | 0 | 4.2 | 2.16 | 2.16 | opened
130 | SS 35/10 kv N.Zhernovets | 1,6+1,6 | 0.12 | 0 | - | 0.12 | 0 | 1.68 | 1.56 | 1.56 | opened
131 | SS 35/10 kv Netrubezh | 2,5+2,5 | 0.44 | 0.39 | - | 0.05 | 0 | 2.625 | 2.575 | 2.575 | opened
132 | SS 35/10 kv Nikolskaya | 2,5+3,2 | 1.85 | 0.54 | 80 | 1.31 | 0 | 2.625 | 1.315 | 1.315 | opened
133 | SS 35/10 kv Pesochnaya | 3,2+3,2 | 0.47 | 1.67 | 120 | -1.2 | 0 | 3.36 | 4.56 | 4.56 | opened
134 | SS 35/6 kv Pushkarskaya | 4+4 | 5.27 | 0 |  | 5.27 | 0 | 4.2 | -1.07 | -1.07 | closed
135 | SS 35/10 kv Rakhmanovo | 2,5+2,5 | 0.68 | 0.25 | 120 | 0.43 | 0 | 2.625 | 2.195 | 2.195 | opened
136 | SS 35/10 kv Rosstani | 2,5+2,5 | 1.28 | 0.7 | 80 | 0.58 | 0 | 2.625 | 2.045 | 2.045 | opened
137 | SS 35/10 kv Sergievskaya | 4+2,5 | 1.4 | 1.5 | 120 | -0.1 | 0 | 2.625 | 2.725 | 2.725 | opened
138 | SS 35/10 kv Skorodnoe | 1,6+1,6 | 0.47 | 0.33 | 120 | 0.14 | 0 | 1.68 | 1.54 | 1.54 | opened
139 | SS 35/10 kv Spasskaya | 2,5+1,6 | 0.24 | 0 | 120 | 0.24 | 0 | 1.68 | 1.44 | 1.44 | opened
140 | SS 35/10 kv SSK | 1,6+1 | 0.11 | 0 |  | 0.11 | 0 | 1.05 | 0.94 | 0.94 | opened
141 | SS 35/10 kv Urynok | 1,6+1,6 | 1.23 | 0.52 | 20 | 0.71 | 0 | 1.68 | 0.97 | 0.97 | opened
142 | SS 35/10 kv Khomutovo | 4+4 | 2.54 | 0.31 | 80 | 2.23 | 0 | 4.2 | 1.97 | 1.97 | opened
Total:
| deficit | [8 empty] | -2.965
| proficit | [8 empty] | 541.995