## Ярославль
Пропускная способность Центров питания филиала ОАО "МРСК Центра" - "Ярэнерго" по итогам зимнего замера максимума нагрузки 2010 г.
[13 empty] | Table 1 | [13 empty] | Table 2
No. | Name of supply center, voltage class | Current deficit | [12 empty] | Note | No. | Name of supply center, voltage class | Expected deficit/proficit | [9 empty] | Note
|  | Installed power capacity of transformers Sinst. including their number, pcs/ MVA | Установленная мощность первого трансформатора. МВА | Установленная мощность второго трансформатора. МВА | Summary total capacity of supply centers following the results of measurements of load maximal Sмаx, MVA | ячейки скрыть |  | Total capacity redistributed according to operating rules, MVA for the time period |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Supply Center deficit/proficit, MVA |  |  |  |  | Installed power capacity of transformers Sinst. including their number, when performing retrofit at the TS or other activities to retrofit the Supply Center pcs./ MVA | Additional capacity according to provided technical specifications at TS, MVA | Expected load of Supply Center, MVA | Total redistributed power capacity of transformers Sinst. including their number, when performing retrofit at the TS or other activities |  | Total capacity including re-distribution, MVA | Limiting factors, MVA | Permissible load accounted in the n-1 mode, MVA | Supply Center deficit/proficit, MVA
[5 empty] | MVA |  |  | MVA | Min | [11 empty] | MVA | Min
1 | 2 | 3 |  |  | 4 | Т-1 | Т-2 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | SS 35/10 Matveevo | 1.6 | 1.6 |  | 0.26 | 0.26 |  | 0.779 | 1 day and night | 0.26 | 0 | 0.779 | 0.519 | 0.519 | open | 1 | SS 35/10 Matveevo | 1.6 | 0.02 | 0.28 | 0.779 | 1 day and night | 0.28 | 0 | 0.779 | 0.499 | 0.499 | open
2 | SS 35/10 Mikhailovskoe | 6.3 | 6.3 |  | 1.11 | 1.11 |  | 6.62 | 1 day and night | 1.11 | 0 | 6.62 | 5.51 | 5.51 | open | 2 | SS 35/10 Mikhailovskoe | 6.3 | 0.003 | 1.113 | 6.62 | 1 day and night | 1.113 | 0 | 6.62 | 5.507 | 5.507 | open
3 | SS 35/10 Shirinye | 2.5 | 2.5 |  | 2.15 |  | 2.15 | 1.68 | 1 day and night | 2.15 | 0 | 1.68 | -0.47 | -0.47 | closed | 3 | SS 35/10 Shirinye | 2.5 | 0.191 | 2.341 | 1.68 | 1 day and night | 2.341 | 0 | 1.68 | -0.661 | -0.661 | closed
4 | SS 110/10 Pokrov | 2.5 | 2.5 |  | 0.27 | 0.27 |  | 1.282 | 1 day and night | 0.27 | 0 | 1.282 | 1.012 | 1.012 | open | 4 | SS 110/10 Pokrov | 2.5 | 0.006 | 0.276 | 1.282 | 1 day and night | 0.276 | 0 | 1.282 | 1.006 | 1.006 | open
5 | SS 35/10 Obnora | 1.6 | 1.6 |  | 0.2 | 0.2 |  | 1.212 | 1 day and night | 0.2 | 0 | 1.212 | 1.012 | 1.012 | open | 5 | SS 35/10 Obnora | 1.6 | 0.058 | 0.258 | 1.212 | 1 day and night | 0.258 | 0 | 1.212 | 0.954 | 0.954 | open
6 | SS 110/35/10 Abbakumtsevo | 10+10 | 10 | 10 | 10.09 |  |  |  |  | 10.09 | 0 | 10.5 | 0.41 | 0.41 | open | 6 | SS 110/35/10 Abbakumtsevo | 10+10 |  | 20.8091 |  |  | 20.8091 | 0 | 10.5 | -10.3091 | -10.3091 | closed
| Nom. capacity MV, МVА | 10+10 |  |  | 8.12 | 2.26 | 5.86 |  |  | 8.12 | 0 | 10.5 | 2.38 |  |  |  | Nom. capacity MV, МVА | 10+10 |  | 16.8726 |  |  | 16.8726 | 0 | 10.5 | -6.3726
| Nom. capacity LV, МVА | 10+10 |  |  | 1.97 | 0.7 | 1.27 |  |  | 1.97 | 0 | 10.5 | 8.53 |  |  |  | Nom. capacity LV, МVА | 10+10 | 1.9665 | 3.9365 |  |  | 3.9365 | 0 | 10.5 | 6.5635
7 | SS 35/10 Ananyino | 1,6+1,6 | 1.6 | 1.6 | 1.31 | 0.82 | 0.49 |  |  | 1.31 | 0 | 1.68 | 0.37 | 0.37 | open | 7 | SS 35/10 Ananyino | 1,6+1,6 | 0.877 | 2.187 |  |  | 2.187 | 0 | 1.68 | -0.507 | -0.507 | closed
8 | SS 110/10/10 Bragino | 40+40 | 40 | 40 | 34.91 | 15.54 | 19.37 | 2.338 | 120 | 32.572 | 0 | 42 | 9.428 | 9.428 | open | 8 | SS 110/10/10 Bragino | 40+40 | 3.6838 | 38.5938 | 2.338 | 120 | 36.2558 | 0 | 42 | 5.7442 | 5.7442 | open
9 | SS 35/10 Burmakino-1 | 4,0+4,0 | 4 | 4 | 2.03 | 0.75 | 1.28 | 0.554 | 120 | 1.476 | 0 | 4.2 | 2.724 | 2.724 | open | 9 | SS 35/10 Burmakino-1 | 4,0+4,0 | 0.906 | 2.936 | 0.554 | 120 | 2.382 | 0 | 4.2 | 1.818 | 1.818 | open
10 | SS 35/10 Vatolino | 4,0+4,0 | 4 | 4 | 3.42 | 1.62 | 1.8 |  |  | 3.42 | 0 | 4.2 | 0.78 | 0.78 | open | 10 | SS 35/10 Vatolino | 4,0+4,0 | 3.759 | 7.179 |  |  | 7.179 | 0 | 4.2 | -2.979 | -2.979 | closed
11 | SS 35/6 Vederniki | 6,3+6,3 | 6.3 | 6.3 | 4.12 | 1.46 | 2.66 |  |  | 4.12 | 0 | 6.62 | 2.5 | 2.5 | open | 11 | SS 35/6 Vederniki | 6,3+6,3 | 0.10393 | 4.2239 |  |  | 4.2239 | 0 | 6.62 | 2.3961 | 2.3961 | open
12 | SS 35/10 Velikovskaya | 4,0+4,0 | 4 | 4 | 1.97 | 1.13 | 0.84 |  |  | 1.97 | 0 | 4.2 | 2.23 | 2.23 | open | 12 | SS 35/10 Velikovskaya | 4,0+4,0 | 0.089 | 2.059 |  |  | 2.059 | 0 | 4.2 | 2.141 | 2.141 | open
13 | SS 35/10 Velikoe Selo | 1,6+1,6 | 1.6 | 1.6 | 0.71 | 0.61 | 0.1 |  |  | 0.71 | 0 | 1.68 | 0.97 | 0.97 | open | 13 | SS 35/10 Velikoe Selo | 1,6+1,6 | 0.072 | 0.782 |  |  | 0.782 | 0 | 1.68 | 0.898 | 0.898 | open
14 | SS 35/10 Vozrozhdenie | 4,0+4,0 | 4 | 4 | 1.17 | 0.36 | 0.81 |  |  | 1.17 | 0 | 4.2 | 3.03 | 3.03 | open | 14 | SS 35/10 Vozrozhdenie | 4,0+4,0 | 3.2754 | 4.4454 |  |  | 4.4454 | 0 | 4.2 | -0.2454 | -0.2454 | open
15 | SS 35/10 Volna | 4,0+2,5 | 4 | 2.5 | 2.53 | 1.21 | 1.32 |  |  | 2.53 | 0 | 2.63 | 0.1 | 0.1 | open | 15 | SS 35/10 Volna | 4,0+2,5 | 0.066 | 2.596 |  |  | 2.596 | 0 | 2.63 | 0.034 | 0.034 | open
16 | SS 35/10 Vyatskoe | 2,5+2,5 | 2.5 | 2.5 | 2.21 | 1.04 | 1.17 | 0.139 | 120 | 2.071 | 0 | 2.63 | 0.559 | 0.559 | open | 16 | SS 35/10 Vyatskoe | 2,5+2,5 | 0.252 | 2.462 | 0.139 | 120 | 2.323 | 0 | 2.63 | 0.307 | 0.307 | open
17 | SS 35/10 Gorinskaya | 2,5+2,5 | 2.5 | 2.5 | 0.66 | 0.34 | 0.32 | 0.329 | 120 | 0.331 | 0 | 2.63 | 2.299 | 2.299 | open | 17 | SS 35/10 Gorinskaya | 2,5+2,5 | 0.079 | 0.739 | 0.329 | 120 | 0.41 | 0 | 2.63 | 2.22 | 2.22 | open
18 | SS 35/10 Grigoryevskoe | 4,0+4,0 | 4 | 4 | 2.61 | 1.11 | 1.5 | 0.312 | 120 | 2.298 | 0 | 4.2 | 1.902 | 1.902 | open | 18 | SS 35/10 Grigoryevskoe | 4,0+4,0 | 0.703 | 3.313 | 0.312 | 120 | 3.001 | 0 | 4.2 | 1.199 | 1.199 | open
19 | SS 35/10 Guzitsino | 4,0+4,0 | 4 | 4 | 2.87 | 1.2 | 1.67 | 0.866 | 120 | 2.004 | 0 | 4.2 | 2.196 | 2.196 | open | 19 | SS 35/10 Guzitsino | 4,0+4,0 | 5.4519 | 8.3219 | 0.866 | 120 | 7.4559 | 0 | 4.2 | -3.2559 | -3.2559 | closed
20 | SS 35/10 State Fire-Fighting Service Yaroslavl | 6,3+6,3 | 6.3 | 6.3 | 2.56 | 2.25 | 0.31 |  |  | 2.56 | 0 | 6.62 | 4.06 | 4.06 | open | 20 | SS 35/10 State Fire-Fighting Service Yaroslavl | 6,3+6,3 | 0 | 2.56 |  |  | 2.56 | 0 | 6.62 | 4.06 | 4.06 | open
21 | SS 110/6 Depo | 16+16 | 16 | 16 | 7.07 | 4.28 | 2.79 |  |  | 7.07 | 0 | 16.8 | 9.73 | 9.73 | open | 21 | SS 110/6 Depo | 16+16 | 2.8606 | 9.9306 |  |  | 9.9306 | 0 | 16.8 | 6.8694 | 6.8694 | open
22 | SS 35/10 Dorozhaevo | 1,6+1,6 | 1.6 | 1.6 | 1.59 | 0.56 | 1.03 | 1.039 | 120 | 0.551 | 0 | 1.68 | 1.129 | 1.129 | open | 22 | SS 35/10 Dorozhaevo | 1,6+1,6 | 0.86 | 2.45 | 1.039 | 120 | 1.411 | 0 | 1.68 | 0.269 | 0.269 | open
23 | SS 110/10 Druzhba | 16+16 | 16 | 16 | 5.51 | 1.77 | 3.74 | 1.932 | 120 | 3.578 | 0 | 16.8 | 13.222 | 13.222 | open | 23 | SS 110/10 Druzhba | 16+16 | 0.4513 | 5.9613 | 1.932 | 120 | 4.0293 | 0 | 16.8 | 12.7707 | 12.7707 | open
24 | SS 35/10 Dubki | 6,3+6,3 | 6.3 | 6.3 | 4.87 | 2.91 | 1.96 | 1.386 | 120 | 3.484 | 0 | 6.62 | 3.136 | 3.136 | open | 24 | SS 35/10 Dubki | 6,3+6,3 | 0.7465 | 5.6165 | 1.386 | 120 | 4.2305 | 0 | 6.62 | 2.3895 | 2.3895 | open
25 | SS 35/10 Dybino | 2,5+2,5 | 2.5 | 2.5 | 1.23 | 0.7 | 0.53 |  |  | 1.23 | 0 | 2.63 | 1.4 | 1.4 | open | 25 | SS 35/10 Dybino | 2,5+2,5 | 0.453 | 1.683 |  |  | 1.683 | 0 | 2.63 | 0.947 | 0.947 | open
26 | SS 35/6 Zavolzhskaya | 10+10 | 10 | 10 | 9.72 | 2.85 | 6.87 |  |  | 9.72 | 0 | 10.5 | 0.78 | 0.78 | open | 26 | SS 35/6 Zavolzhskaya | 10+10 | 1.0857 | 10.8057 |  |  | 10.8057 | 0 | 10.5 | -0.30575 | -0.30575 | closed
27 | SS 110/6/6 Institutskaya | 40+40 | 40 | 40 | 31.83 | 18.69 | 13.14 |  |  | 31.83 | 0 | 42 | 10.17 | 10.17 | open | 27 | SS 110/6/6 Institutskaya | 40+40 | 3.0371 | 34.8671 |  |  | 34.8671 | 0 | 42 | 7.1329 | 7.1329 | open
28 | SS 35/10 Koza | 1,6+1,6 | 1.6 | 1.6 | 0.3 | 0.07 | 0.23 | 0.052 | 120 | 0.248 | 0 | 1.68 | 1.432 | 1.432 | open | 28 | SS 35/10 Koza | 1,6+1,6 | 0.038 | 0.338 | 0.052 | 120 | 0.286 | 0 | 1.68 | 1.394 | 1.394 | open
29 | SS 110/35/6 Konstantinovo | 20+16 | 20 | 16 | 10.56 |  |  | 0.021 | 120 | 10.539 | 0 | 16.8 | 6.261 | 6.261 | open | 29 | SS 110/35/6 Konstantinovo | 20+16 |  | 12.8675 | 0.021 | 120 | 12.8465 | 0 | 16.8 | 3.9535 | 3.9535 | open
| Nom. capacity MV, МVА | 20+16 |  |  | 7.47 | 3.95 | 3.52 |  |  | 7.47 | 0 | 16.8 | 9.33 |  |  |  | Nom. capacity MV, МVА | 20+16 |  | 9.3815 |  |  | 9.3815 | 0 | 16.8 | 7.4185
| Nom. capacity LV, МVА | 20+16 |  |  | 3.09 | 2.1 | 0.99 | 0.021 | 120 | 3.069 | 0 | 16.8 | 13.731 |  |  |  | Nom. capacity LV, МVА | 20+16 | 0.396 | 3.486 | 0.021 | 120 | 3.465 | 0 | 16.8 | 13.335
30 | SS 35/10 Kurba | 2,5+2,5 | 2.5 | 2.5 | 2.48 | 0.68 | 1.8 | 0.242 | 120 | 2.238 | 0 | 2.63 | 0.392 | 0.392 | open | 30 | SS 35/10 Kurba | 2,5+2,5 | 0.421 | 2.901 | 0.242 | 120 | 2.659 | 0 | 2.63 | -0.029 | -0.029 | closed
31 | SS 35/10 Lesnye Polyany | 10+10 | 10 | 10 | 7.08 | 4.29 | 2.79 | 1.212 | 120 | 5.868 | 0 | 10.5 | 4.632 | 4.632 | open | 31 | SS 35/10 Lesnye Polyany | 10+10 | 1.121 | 8.201 | 1.212 | 120 | 6.989 | 0 | 10.5 | 3.511 | 3.511 | open
32 | SS 35/10 Modelovo-2 | 6,3+6,3 | 6.3 | 6.3 | 5.85 | 2.1 | 3.75 | 2.338 | 120 | 3.512 | 0 | 6.62 | 3.108 | 3.108 | open | 32 | SS 35/10 Modelovo-2 | 6,3+6,3 | 5.9007 | 11.7507 | 2.338 | 120 | 9.4127 | 0 | 6.62 | -2.7927 | -2.7927 | closed
33 | SS 35/10 Nekrasovo | 10+10 | 10 | 10 | 11.17 | 5.47 | 5.7 |  |  | 11.17 | 0 | 10.5 | -0.67 | -0.67 | closed | 33 | SS 35/10 Nekrasovo | 10+10 | 2.7094 | 13.8794 |  |  | 13.8794 | 0 | 10.5 | -3.3794 | -3.3794 | closed
34 | SS 35/10 Nikolskoe | 2,5+2,5 | 2.5 | 2.5 | 0.73 | 0.69 | 0.04 | 0.398 | 120 | 0.332 | 0 | 2.63 | 2.298 | 2.298 | open | 34 | SS 35/10 Nikolskoe | 2,5+2,5 | 0.068 | 0.798 | 0.398 | 120 | 0.4 | 0 | 2.63 | 2.23 | 2.23 | open
35 | SS 110/35/6 Oil refinary plant | 25+25 | 25 | 25 | 15.58 |  |  |  |  | 15.58 | 0 | 26.25 | 10.67 | 10.67 | open | 35 | SS 110/35/6 Oil refinary plant | 25+25 |  | 22.9839 |  |  | 22.9839 | 0 | 26.25 | 3.2661 | 3.2661 | open
| Nom. capacity MV, МVА | 25+25 |  |  | 8.31 | 4.92 | 3.39 |  |  | 8.31 | 0 | 26.25 | 17.94 |  |  |  | Nom. capacity MV, МVА | 25+25 |  | 8.4139 |  |  | 8.4139 | 0 | 26.25 | 17.8361
| Nom. capacity LV, МVА | 25+25 |  |  | 7.27 | 2.92 | 4.35 |  |  | 7.27 | 0 | 26.25 | 18.98 |  |  |  | Nom. capacity LV, МVА | 25+25 | 7.3 | 14.57 |  |  | 14.57 | 0 | 26.25 | 11.68
36 | SS 110/6/6 Orion | 40+40 | 40 | 40 | 14.71 | 8.56 | 6.15 |  |  | 14.71 | 0 | 42 | 27.29 | 27.29 | open | 36 | SS 110/6/6 Orion | 40+40 | 0.67533 | 15.3853 |  |  | 15.3853 | 0 | 42 | 26.6147 | 26.6147 | open
37 | SS 110/35/6 Pavlovskaya | 20+25 | 20 | 25 | 23.56 |  |  |  |  | 23.56 | 0 | 21 | -2.56 | -2.56 | closed | 37 | SS 110/35/6 Pavlovskaya | 20+25 |  | 23.9582 |  |  | 23.9582 | 0 | 21 | -2.9582 | -2.9582 | closed
| Nom. capacity MV, МVА | 20+25 |  |  | 5.71 | 0.93 | 4.78 |  |  | 5.71 | 0 | 21 | 15.29 |  |  |  | Nom. capacity MV, МVА | 20+25 |  | 6.0615 |  |  | 6.0615 | 0 | 21 | 14.9385
| Nom. capaity LV, МVА | 20+25 |  |  | 17.85 | 5.7 | 12.15 |  |  | 17.85 | 0 | 21 | 3.15 |  |  |  | Nom. capaity LV, МVА | 20+25 | 0.046702 | 17.8967 |  |  | 17.8967 | 0 | 21 | 3.1033
38 | SS 110/10 Pereval | 16+16 | 16 | 16 | 8.51 | 3.93 | 4.58 |  |  | 8.51 | 0 | 16.8 | 8.29 | 8.29 | open | 38 | SS 110/10 Pereval | 16+16 | 8.3719 | 16.8819 |  |  | 16.8819 | 0 | 16.8 | -0.081873 | -0.081873 | closed
39 | SS 110/6/6 Perekop | 25+25 | 25 | 25 | 10.33 | 6.29 | 4.04 |  |  | 10.33 | 0 | 26.25 | 15.92 | 15.92 | open | 39 | SS 110/6/6 Perekop | 25+25 | 0.37607 | 10.7061 |  |  | 10.7061 | 0 | 26.25 | 15.5439 | 15.5439 | open
40 | SS 110/6/6 Poligraf | 40+40 | 40 | 40 | 33.97 | 18.83 | 15.14 |  |  | 33.97 | 0 | 42 | 8.03 | 8.03 | open | 40 | SS 110/6/6 Poligraf | 40+40 | 2.8349 | 36.8049 |  |  | 36.8049 | 0 | 42 | 5.1951 | 5.1951 | open
41 | SS 110/35/10 Prechistoe | 10+10 | 10 | 10 | 3.82 |  |  | 0.52 | 120 | 3.3 | 0 | 10.5 | 7.2 | 7.2 | open | 41 | SS 110/35/10 Prechistoe | 10+10 |  | 4.2785 | 0.52 | 120 | 3.7585 | 0 | 10.5 | 6.7415 | 6.7415 | open
| Nom. capacity MV, МVА | 10+10 |  |  | 1 | 0.06 | 0.94 |  |  | 1 | 0 | 10.5 | 9.5 |  |  |  | Nom. capacity MV, МVА | 10+10 |  | 1.0895 |  |  | 1.0895 | 0 | 10.5 | 9.4105
| Nom. capacity LV, МVА | 10+10 |  |  | 2.82 | 1.36 | 1.46 | 0.52 | 120 | 2.3 | 0 | 10.5 | 8.2 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.369 | 3.189 | 0.52 | 120 | 2.669 | 0 | 10.5 | 7.831
42 | SS 35/10 Preventorium | 2,5+2,5 | 2.5 | 2.5 | 1.05 | 0.35 | 0.7 | 0.26 | 120 | 0.79 | 0 | 2.63 | 1.84 | 1.84 | open | 42 | SS 35/10 Preventorium | 2,5+2,5 | 2.7173 | 3.7673 | 0.26 | 120 | 3.5073 | 0 | 2.63 | -0.8773 | -0.8773 | closed
43 | SS 35/10 Rozhdestveno | 2,5+2,5 | 2.5 | 2.5 | 0.23 | 0.03 | 0.2 | 0.052 | 120 | 0.178 | 0 | 2.63 | 2.452 | 2.452 | open | 43 | SS 35/10 Rozhdestveno | 2,5+2,5 | 0.01 | 0.24 | 0.052 | 120 | 0.188 | 0 | 2.63 | 2.442 | 2.442 | open
44 | SS 110/6/6 Severnaya | 63+63 | 63 | 63 | 37.99 | 17.94 | 20.05 |  |  | 37.99 | 0 | 66.15 | 28.16 | 28.16 | open | 44 | SS 110/6/6 Severnaya | 63+63 | 4.8104 | 42.8004 |  |  | 42.8004 | 0 | 66.15 | 23.3496 | 23.3496 | open
45 | SS 35/10 Sereda | 2,5+2,5 | 2.5 | 2.5 | 1.34 | 0.48 | 0.86 | 0.987 | 120 | 0.353 | 0 | 2.63 | 2.277 | 2.277 | open | 45 | SS 35/10 Sereda | 2,5+2,5 | 0.627 | 1.967 | 0.987 | 120 | 0.98 | 0 | 2.63 | 1.65 | 1.65 | open
46 | SS 110/6 Tormoznaya | 16+16 | 16 | 16 | 14.508 | 9.098 | 5.41 |  |  | 14.508 | 0 | 16.8 | 2.292 | 2.292 | open | 46 | SS 110/6 Tormoznaya | 16+16 | 0.32124 | 14.8292 |  |  | 14.8292 | 0 | 16.8 | 1.9708 | 1.9708 | open
47 | SS 110/6 Petrol station pump | 16+16 | 16 | 16 | 4.59 | 2.47 | 2.12 |  |  | 4.59 | 0 | 16.8 | 12.21 | 12.21 | open | 47 | SS 110/6 Petrol station pump | 16+16 | 0 | 4.59 |  |  | 4.59 | 0 | 16.8 | 12.21 | 12.21 | open
48 | SS 35/10 Troitsa | 2,5+2,5 | 2.5 | 2.5 | 0.34 | 0.27 | 0.07 | 0.277 | 120 | 0.063 | 0 | 2.63 | 2.567 | 2.567 | open | 48 | SS 35/10 Troitsa | 2,5+2,5 | 0.007 | 0.347 | 0.277 | 120 | 0.07 | 0 | 2.63 | 2.56 | 2.56 | open
49 | SS 35/10 Tunoshna | 2,5+2,5 | 2.5 | 2.5 | 0.69 | 0.31 | 0.38 | 0.191 | 120 | 0.499 | 0 | 2.63 | 2.131 | 2.131 | open | 49 | SS 35/10 Tunoshna | 2,5+2,5 | 0.344 | 1.034 | 0.191 | 120 | 0.843 | 0 | 2.63 | 1.787 | 1.787 | open
50 | SS 35/10 Tutaev-35 | 6,3+6,3 | 6.3 | 6.3 | 7.26 | 3.54 | 3.72 |  |  | 7.26 | 0 | 6.62 | -0.64 | -0.64 | closed | 50 | SS 35/10 Tutaev-35 | 6,3+6,3 | 0.313 | 7.573 |  |  | 7.573 | 0 | 6.62 | -0.953 | -0.953 | closed
51 | SS 110/10 Tufanovo | 2,5+2,5 | 2.5 | 2.5 | 0.72 | 0.59 | 0.13 |  |  | 0.72 | 0 | 2.63 | 1.91 | 1.91 | open | 51 | SS 110/10 Tufanovo | 2,5+2,5 | 0.3044 | 1.0244 |  |  | 1.0244 | 0 | 2.63 | 1.6056 | 1.6056 | open
52 | SS 35/10 Urozhay | 4,0+4,0 | 4 | 4 | 1.58 | 0.65 | 0.93 | 0.346 | 120 | 1.234 | 0 | 4.2 | 2.966 | 2.966 | open | 52 | SS 35/10 Urozhay | 4,0+4,0 | 0.954 | 2.534 | 0.346 | 120 | 2.188 | 0 | 4.2 | 2.012 | 2.012 | open
53 | SS 110/35/10 Khaldeevo | 3,2+6,3 | 3.2 | 6.3 | MVA 4: 2.92; Min 11: 2.83; Min 12: open | 53 | SS 110/35/10 Khaldeevo | 3,2+6,3 |  | 0.8025 |  |  |  | 0 |  |  | 2.8175 | open
| Nom. capacity MV, МVА | 0+6,3 |  |  | MVA 4: 2.13; MVA Т-2: 2.13 |  | Nom. capacity MV, МVА | 0+6,3
| Nom. capacity LV, МVА | 3.2+6.3 |  |  | 0.79 | 0.67 | 0.12 | 0.26 | 120 | 0.53 | 0 | 3.36 | 2.83 |  |  |  | Nom. capacity LV, МVА | 3.2+6.3 | 0.0125 | 0.8025 | 0.26 | 120 | 0.5425 | 0 | 3.36 | 2.8175
54 | SS 110/10 Chayka | 25+25 | 25 | 25 | 19.38 | 9.91 | 9.47 |  |  | 19.38 | 0 | 26.25 | 6.87 | 6.87 | open | 54 | SS 110/10 Chayka | 25+25 | 1.14 | 20.52 |  |  | 20.52 | 0 | 26.25 | 5.73 | 5.73 | open
55 | SS 35/6 Chebakovo | 2,5+2,5 | 2.5 | 2.5 | 1.57 | 0.97 | 0.6 | 0.156 | 120 | 1.414 | 0 | 2.63 | 1.216 | 1.216 | open | 55 | SS 35/6 Chebakovo | 2,5+2,5 | 1.494 | 3.064 | 0.156 | 120 | 2.908 | 0 | 2.63 | -0.278 | -0.278 | closed
56 | SS 35/10 Shchedrino | 4,0+4,0 | 4 | 4 | 1.43 | 0.19 | 1.24 |  |  | 1.43 | 0 | 4.2 | 2.77 | 2.77 | open | 56 | SS 35/10 Shchedrino | 4,0+4,0 | 0.67 | 2.1 |  |  | 2.1 | 0 | 4.2 | 2.1 | 2.1 | open
57 | SS 110/6 /6 Yuzhnaya | 40+40 | 40 | 40 | 31.98 | 12.79 | 19.19 |  |  | 31.98 | 0 | 42 | 10.02 | 10.02 | open | 57 | SS 110/6 /6 Yuzhnaya | 40+40 | 5.0205 | 37.0005 |  |  | 37.0005 | 0 | 42 | 4.9995 | 4.9995 | open
58 | SS 110/10/6 Yartsevo | 25+25 | 25 | 25 | 6.88 | 4.58 | 2.3 |  |  | 6.88 | 0 | 26.25 | 19.37 | 19.37 | open | 58 | SS 110/10/6 Yartsevo | 25+25 | 0.736 | 7.616 |  |  | 7.616 | 0 | 26.25 | 18.634 | 18.634 | open
59 | ПС 110/6/6 Kotorosl | 25+25 | 25 | 25 | 6.04 | 3.72 | 2.32 |  |  | 6.04 | 0 | 26.25 | 20.21 | 20.21 | open | 59 | ПС 110/6/6 Kotorosl | 25+25 | 0.85884 | 6.8988 |  |  | 6.8988 |  | 26.25 | 19.3512 | 19.3512 | open
60 | SS 35/6 Kelnot | 4 | 4 |  | 0.29 | 0.29 |  | 4.2 | 1 day and night | 0.29 | 0 | 4.2 | 3.91 | 3.91 | open | 60 | SS 35/6 Kelnot | 4 | 0 | 0.29 | 4.2 | 1 day and night | 0.29 |  | 4.2 | 3.91 | 3.91 | open
61 | SS 110/10 Altynovo | 6,3+6,3 | 6.3 | 6.3 | 3.3 | 1.51 | 1.79 |  |  | 3.3 | 0 | 6.62 | 3.32 | 3.32 | open | 61 | SS 110/10 Altynovo | 6,3+6,3 | 1.4413 | 4.7413 |  |  | 4.7413 | 0 | 6.62 | 1.8787 | 1.8787 | open
62 | SS 110/35/10 Borisogleb | 16+10 | 16 | 10 | 7.8 |  |  |  |  | 7.8 | 0 | 10.5 | 2.7 | 2.7 | open | 62 | SS 110/35/10 Borisogleb | 16+10 |  | 10.6147 |  |  | 10.6147 | 0 | 10.5 | -0.11475 | -0.11475 | closed
| Nom. capacity MV, МVА | 16+10 |  |  | 3.35 | 1.36 | 1.99 |  |  | 3.35 | 0 | 10.5 | 7.15 |  |  |  | Nom. capacity MV, МVА | 16+10 |  | 4.4285 |  |  | 4.4285 | 0 | 10.5 | 6.0715
| Nom. capacity LV, МVА | 16+10 |  |  | 4.45 | 2.13 | 2.32 |  |  | 4.45 | 0 | 10.5 | 6.05 |  |  |  | Nom. capacity LV, МVА | 16+10 | 1.7362 | 6.1862 |  |  | 6.1862 | 0 | 10.5 | 4.3138
63 | SS 110/35/10 Vasilkovo | 10+10 | 10 | 10 | 3.4 |  |  | 0.537 | 120 | 2.863 | 0 | 10.5 | 7.637 | 7.637 | open | 63 | SS 110/35/10 Vasilkovo | 10+10 |  | 3.577 | 0.537 | 120 | 3.04 | 0 | 10.5 | 7.46 | 7.46 | open
| Nom. capacity MV, МVА | 10+10 |  |  | 2.1 | 0 | 2.1 |  |  | 2.1 | 0 | 10.5 | 8.4 |  |  |  | Nom. capacity MV, МVА | 10+10 |  | 2.236 |  |  | 2.236 | 0 | 10.5 | 8.264
| Nom. capacity LV, МVА | 10+10 |  |  | 1.3 | 0.45 | 0.85 | 0.537 | 120 | 0.763 | 0 | 10.5 | 9.737 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.041 | 1.341 | 0.537 | 120 | 0.804 | 0 | 10.5 | 9.696
64 | SS 110/10 Vakhrushevo | 6,3+6,3 | 6.3 | 6.3 | 0.29 | 0.04 | 0.25 | 0.087 | 120 | 0.203 | 0 | 6.62 | 6.417 | 6.417 | open | 64 | SS 110/10 Vakhrushevo | 6,3+6,3 | 0.015 | 0.305 | 0.087 | 120 | 0.218 | 0 | 6.62 | 6.402 | 6.402 | open
65 | SS 110/6 Gavrilov Yam | 16+16 | 16 | 16 | 12.24 | 5.05 | 7.19 |  |  | 12.24 | 0 | 16.8 | 4.56 | 4.56 | open | 65 | SS 110/6 Gavrilov Yam | 16+16 | 0 | 12.24 |  |  | 12.24 | 0 | 16.8 | 4.56 | 4.56 | open
66 | SS 110/6 Kinoplyonka | 6,3+10 | 6.3 | 10 | 9.9 | 5.64 | 4.26 |  |  | 9.9 | 0 | 6.62 | -3.28 | -3.28 | closed | 66 | SS 110/6 Kinoplyonka | 6,3+10 | 2.854 | 12.754 |  |  | 12.754 | 0 | 6.62 | -6.134 | -6.134 | closed
67 | SS 110/35/10 Klimatino | 6,3+6,3 | 6.3 | 6.3 | 1.7 |  |  |  |  | 1.7 | 0 | 6.62 | 4.92 | 4.92 | open | 67 | SS 110/35/10 Klimatino | 6,3+6,3 |  | 1.762 |  |  | 1.762 | 0 | 6.62 | 4.858 | 4.858 | open
| Nom. capacity MV, МVА | 0+6,3 |  |  | MVA 4: 0.36; MVA Т-2: 0.36; Min 7: 0.36; Min 8: 0; Min 9: 6.62; Min 10: 6.26 |  | Nom. capacity MV, МVА | 0+6,3 |  | 0.391 |  |  | 0.391 | 0 | 6.62 | 6.229
| Nom. capacity LV, МVА | 6,3+6,3 |  |  | 1.34 | 0 | 1.34 |  |  | 1.34 | 0 | 6.62 | 5.28 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 0.031 | 1.371 |  |  | 1.371 | 0 | 6.62 | 5.249
68 | SS 110/35/10 Nila | 6,3+6,3 | 6.3 | 6.3 | 10.35 |  |  | 0.97 | 120 | 9.38 | 0 | 6.62 | -2.76 | -2.76 | closed | 68 | SS 110/35/10 Nila | 6,3+6,3 |  | 25.9482 | 0.97 | 120 | 24.9782 | 0 | 6.62 | -18.3582 | -18.3582 | closed
| Nom. capacity MV, МVА | 6,3+6,3 |  |  | 7.66 | 5.76 | 1.9 |  |  | 7.66 | 0 | 6.62 | -1.04 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 |  | 11.4767 |  |  | 11.4767 | 0 | 6.62 | -4.8567
| Nom. capacity LV, МVА | 6,3+6,3 |  |  | 2.69 | 1.06 | 1.63 | 0.97 | 120 | 1.72 | 0 | 6.62 | 4.9 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 11.7815 | 14.4715 | 0.97 | 120 | 13.5015 | 0 | 6.62 | -6.8815
69 | SS 110/35/6 Pereslavl | 25+25 | 25 | 25 | 24.89 |  |  |  |  | 24.89 | 0 | 26.25 | 1.36 | 1.36 | open | 69 | SS 110/35/6 Pereslavl | 25+25 |  | 34.7305 |  |  | 34.7305 | 0 | 26.25 | -8.4805 | -8.4805 | closed
| Nom. capacity MV, МVА | 25+25 |  |  | 10.56 | 3.77 | 6.79 |  |  | 10.56 | 0 | 26.25 | 15.69 |  |  |  | Nom. capacity MV, МVА | 25+25 |  | 20.1295 |  |  | 20.1295 | 0 | 26.25 | 6.1205
| Nom. capacity LV, МVА | 25+25 |  |  | 14.33 | 4.85 | 9.48 |  |  | 14.33 | 0 | 26.25 | 11.92 |  |  |  | Nom. capacity LV, МVА | 25+25 | 0.271 | 14.601 |  |  | 14.601 | 0 | 26.25 | 11.649
70 | SS 110/10 Ploski | 2,5+2,5 | 2.5 | 2.5 | 1.76 | 1.09 | 0.67 |  |  | 1.76 | 0 | 2.63 | 0.87 | 0.87 | open | 70 | SS 110/10 Ploski | 2,5+2,5 | 0.5945 | 2.3545 |  |  | 2.3545 | 0 | 2.63 | 0.2755 | 0.2755 | open
71 | SS 110/35/10 Rostov | 20+25 | 20 | 25 | 21.21 |  |  |  |  | 21.21 | 0 | 21 | -0.21 | -0.21 | closed | 71 | SS 110/35/10 Rostov | 20+25 |  | 24.236 |  |  | 24.236 | 0 | 21 | -3.236 | -3.236 | closed
| Nom. capacity MV, МVА | 20+25 |  |  | 1.66 | 0 | 1.66 |  |  | 1.66 | 0 | 21 | 19.34 |  |  |  | Nom. capacity MV, МVА | 20+25 |  | 2.128 |  |  | 2.128 | 0 | 21 | 18.872
| Nom. Capacity LV, МVА | 20+25 |  |  | 19.55 | 8.08 | 11.47 |  |  | 19.55 | 0 | 21 | 1.45 |  |  |  | Nom. Capacity LV, МVА | 20+25 | 2.558 | 22.108 |  |  | 22.108 | 0 | 21 | -1.108
72 | SS 110/35/10 Technical school | 6,3+6,3 | 6.3 | 6.3 | 7.62 |  |  |  |  | 7.62 | 0 | 6.62 | -1 | -1 | closed | 72 | SS 110/35/10 Technical school | 6,3+6,3 |  | 13.0243 |  |  | 13.0243 | 0 | 6.62 | -6.4043 | -6.4043 | closed
| Nom. capacity MV, МVА | 6,3+6,3 |  |  | 4.13 | 4.13 | 0 |  |  | 4.13 | 0 | 6.62 | 2.49 |  |  |  | Nom. capacity MV, МVА | 6,3+6,3 |  | 6.7123 |  |  | 6.7123 | 0 | 6.62 | -0.09225
| Nom. capacity LV, МVА | 6,3+6,3 |  |  | 3.49 | 2.2 | 1.29 |  |  | 3.49 | 0 | 6.62 | 3.13 |  |  |  | Nom. capacity LV, МVА | 6,3+6,3 | 2.822 | 6.312 |  |  | 6.312 | 0 | 6.62 | 0.308
73 | SS 110/35/10 Uglich | 25+25 | 25 | 25 | 23.08 |  |  |  |  | 23.08 | 0 | 26.25 | 3.17 | 3.17 | open | 73 | SS 110/35/10 Uglich | 25+25 |  | 31.208 |  |  | 31.208 | 0 | 26.25 | -4.958 | -4.958 | closed
| Nom. capacidty MV, МVА | 25+25 |  |  | 18.49 | 3.59 | 14.9 |  |  | 18.49 | 0 | 26.25 | 7.76 |  |  |  | Nom. capacidty MV, МVА | 25+25 |  | 22.497 |  |  | 22.497 | 0 | 26.25 | 3.753
| Nom. capacity LV, МVА | 25+25 |  |  | 4.59 | 2.47 | 2.12 |  |  | 4.59 | 0 | 26.25 | 21.66 |  |  |  | Nom. capacity LV, МVА | 25+25 | 4.121 | 8.711 |  |  | 8.711 | 0 | 26.25 | 17.539
74 | SS 110/10 Ustye | 10+10 | 10 | 10 | 4.35 | 2.67 | 1.68 | 0.797 | 120 | 3.553 | 0 | 10.5 | 6.947 | 6.947 | open | 74 | SS 110/10 Ustye | 10+10 | 0.302 | 4.652 | 0.797 | 120 | 3.855 | 0 | 10.5 | 6.645 | 6.645 | open
75 | SS 110/10 Shurskol | 10+10 | 10 | 10 | 1.34 | 0.89 | 0.45 | 0.97 | 120 | 0.37 | 0 | 10.5 | 10.13 | 10.13 | open | 75 | SS 110/10 Shurskol | 10+10 | 0.09 | 1.43 | 0.97 | 120 | 0.46 | 0 | 10.5 | 10.04 | 10.04 | open
76 | SS 110/10 Yur.Sloboda | 10+10 | 10 | 10 | 7.17 | 3.94 | 3.23 | 0.866 | 120 | 6.304 | 0 | 10.5 | 4.196 | 4.196 | open | 76 | SS 110/10 Yur.Sloboda | 10+10 | 1.0092 | 8.1792 | 0.866 | 120 | 7.3132 | 0 | 10.5 | 3.1868 | 3.1868 | open
77 | SS 35/10 Aleshkino | 2,5+2,5 | 2.5 | 2.5 | 0.93 | 0.81 | 0.12 |  |  | 0.93 | 0 | 2.63 | 1.7 | 1.7 | open | 77 | SS 35/10 Aleshkino | 2,5+2,5 | 0.114 | 1.044 |  |  | 1.044 | 0 | 2.63 | 1.586 | 1.586 | open
78 | SS 35/6 Batki | 1,6+1,6 | 1.6 | 1.6 | 1.14 | 1.13 | 0.01 |  |  | 1.14 | 0 | 1.68 | 0.54 | 0.54 | open | 78 | SS 35/6 Batki | 1,6+1,6 | 0.526 | 1.666 |  |  | 1.666 | 0 | 1.68 | 0.014 | 0.014 | open
79 | SS 35/10 Beregovaya | 1,6 | 1.6 |  | 0.18 | 0.18 |  | 3.031 | 1 day and night | 0.18 | 0 | 3.031 | 2.851 | 2.851 | open | 79 | SS 35/10 Beregovaya | 1,6 | 0.01 | 0.19 | 3.031 | 1 day and night | 0.19 | 0 | 3.031 | 2.841 | 2.841 | open
80 | SS 35/10 Berendeevo | 2,5+2,5 | 2.5 | 2.5 | 1.76 | 1.11 | 0.65 | 0.225 |  | 1.535 | 0 | 2.63 | 1.095 | 1.095 | open | 80 | SS 35/10 Berendeevo | 2,5+2,5 | 0.065 | 1.825 | 0.225 |  | 1.6 | 0 | 2.63 | 1.03 | 1.03 | open
81 | SS 35/10 Vorzha | 1,8+1,6 | 1.8 | 1.6 | 0.5 | 0.33 | 0.17 | 0.087 | 120 | 0.413 | 0 | 1.68 | 1.267 | 1.267 | open | 81 | SS 35/10 Vorzha | 1,8+1,6 | 0.012 | 0.512 | 0.087 | 120 | 0.425 | 0 | 1.68 | 1.255 | 1.255 | open
82 | SS 35/10 Voshchazhnikovo | 1,6+2,5 | 1.6 | 2.5 | 0.75 | 0.36 | 0.39 | 0.52 | 120 | 0.23 | 0 | 1.68 | 1.45 | 1.45 | open | 82 | SS 35/10 Voshchazhnikovo | 1,6+2,5 | 0.286 | 1.036 | 0.52 | 120 | 0.516 | 0 | 1.68 | 1.164 | 1.164 | open
83 | SS 35/10 Glebovo | 2,5+2,5 | 2.5 | 2.5 | 2.08 | 0.24 | 1.84 |  |  | 2.08 | 0 | 2.63 | 0.55 | 0.55 | open | 83 | SS 35/10 Glebovo | 2,5+2,5 | 3.233 | 5.313 |  |  | 5.313 | 0 | 2.63 | -2.683 | -2.683 | closed
84 | SS 35/10 Gorki | 2,5+2,5 | 2.5 | 2.5 | 0.93 | 0.32 | 0.61 |  |  | 0.93 | 0 | 2.63 | 1.7 | 1.7 | open | 84 | SS 35/10 Gorki | 2,5+2,5 | 0.242 | 1.172 |  |  | 1.172 | 0 | 2.63 | 1.458 | 1.458 | open
85 | SS 35/10 Dmitrianovo | 1,6+1,6 | 1.6 | 1.6 | 1.11 | 0.61 | 0.5 |  |  | 1.11 | 0 | 1.68 | 0.57 | 0.57 | open | 85 | SS 35/10 Dmitrianovo | 1,6+1,6 | 0.094 | 1.204 |  |  | 1.204 | 0 | 1.68 | 0.476 | 0.476 | open
86 | SS 35/10 Zaozerye | 2,5+1,6 | 2.5 | 1.6 | 1.54 | 0.63 | 0.91 |  |  | 1.54 | 0 | 1.68 | 0.14 | 0.14 | open | 86 | SS 35/10 Zaozerye | 2,5+1,6 | 0.093 | 1.633 |  |  | 1.633 | 0 | 1.68 | 0.047 | 0.047 | open
87 | SS 35/10 Ilyinskoe | 2,5+2,5 | 2.5 | 2.5 | 1.49 | 1.07 | 0.42 |  |  | 1.49 | 0 | 2.63 | 1.14 | 1.14 | open | 87 | SS 35/10 Ilyinskoe | 2,5+2,5 | 0.0855 | 1.5755 |  |  | 1.5755 | 0 | 2.63 | 1.0545 | 1.0545 | open
88 | SS 35/10 Kibernetik | 6,3+6,3 | 6.3 | 6.3 | 2.24 | 0.76 | 1.48 |  |  | 2.24 | 0 | 6.62 | 4.38 | 4.38 | open | 88 | SS 35/10 Kibernetik | 6,3+6,3 | 2.517 | 4.757 |  |  | 4.757 | 0 | 6.62 | 1.863 | 1.863 | open
89 | SS 35/10 Klementyevo | 1,6 | 1.6 |  | 0.32 | 0.32 |  | 0.485 | 1 day and night | 0.32 | 0 | 0.485 | 0.165 | 0.165 | open | 89 | SS 35/10 Klementyevo | 1,6 | 0.016 | 0.336 | 0.485 | 1 day and night | 0.336 | 0 | 0.485 | 0.149 | 0.149 | open
90 | SS 35/10 Krasnoe | 4,0+4,0 | 4 | 4 | 1.73 | 0.67 | 1.06 | 0.953 | 120 | 0.777 | 0 | 4.2 | 3.423 | 3.423 | open | 90 | SS 35/10 Krasnoe | 4,0+4,0 | 1.315 | 3.045 | 0.953 | 120 | 2.092 | 0 | 4.2 | 2.108 | 2.108 | open
91 | SS 35/10 Kulakovo | 2,5+2,5 | 2.5 | 2.5 | 1.35 | 0.91 | 0.44 |  |  | 1.35 | 0 | 2.63 | 1.28 | 1.28 | open | 91 | SS 35/10 Kulakovo | 2,5+2,5 | 0.373 | 1.723 |  |  | 1.723 | 0 | 2.63 | 0.907 | 0.907 | open
92 | SS 35/6 Kupan | 2,5+2,5 | 2.5 | 2.5 | 2.58 | 1.55 | 1.03 |  |  | 2.58 | 0 | 2.63 | 0.05 | 0.05 | open | 92 | SS 35/6 Kupan | 2,5+2,5 | 1.1467 | 3.7267 |  |  | 3.7267 | 0 | 2.63 | -1.0967 | -1.0967 | closed
93 | SS 35/10 Markovo | 2,5+2,5 | 2.5 | 2.5 | 0.99 | 0.65 | 0.34 | 0.502 | 120 | 0.488 | 0 | 2.63 | 2.142 | 2.142 | open | 93 | SS 35/10 Markovo | 2,5+2,5 | 0.294 | 1.284 | 0.502 | 120 | 0.782 | 0 | 2.63 | 1.848 | 1.848 | open
94 | SS 35/10 Nagorye | 4,0+4,0 | 4 | 4 | 3.49 | 1.85 | 1.64 |  |  | 3.49 | 0 | 4.2 | 0.71 | 0.71 | open | 94 | SS 35/10 Nagorye | 4,0+4,0 | 1.753 | 5.243 |  |  | 5.243 | 0 | 4.2 | -1.043 | -1.043 | closed
95 | SS 35/10 Porechye | 4,0+4,0 | 4 | 4 | 2.13 | 0.84 | 1.29 | 0.087 | 120 | 2.043 | 0 | 4.2 | 2.157 | 2.157 | open | 95 | SS 35/10 Porechye | 4,0+4,0 | 0.228 | 2.358 | 0.087 | 120 | 2.271 | 0 | 4.2 | 1.929 | 1.929 | open
96 | SS 35/10 Pruzhinino | 2,5+2,5 | 2.5 | 2.5 | 1.11 | 0.88 | 0.23 |  |  | 1.11 | 0 | 2.63 | 1.52 | 1.52 | open | 96 | SS 35/10 Pruzhinino | 2,5+2,5 | 0.5165 | 1.6265 |  |  | 1.6265 | 0 | 2.63 | 1.0035 | 1.0035 | open
97 | SS 35/10 Ramenye | 2,5+2,5 | 2.5 | 2.5 | 0.91 | 0.37 | 0.54 | 0.035 | 120 | 0.875 | 0 | 2.63 | 1.755 | 1.755 | open | 97 | SS 35/10 Ramenye | 2,5+2,5 | 0.05 | 0.96 | 0.035 | 120 | 0.925 | 0 | 2.63 | 1.705 | 1.705 | open
98 | SS 35/10 Ryazantsevo | 2,5+2,5 | 2.5 | 2.5 | 1.28 | 0.86 | 0.42 |  |  | 1.28 | 0 | 2.63 | 1.35 | 1.35 | open | 98 | SS 35/10 Ryazantsevo | 2,5+2,5 | 0.077 | 1.357 |  |  | 1.357 | 0 | 2.63 | 1.273 | 1.273 | open
99 | SS 35/10 Saraevo | 1+1,6 | 1 | 1.6 | 1.32 | 0.37 | 0.95 |  |  | 1.32 | 0 | 1.05 | -0.27 | -0.27 | closed | 99 | SS 35/10 Saraevo | 1+1,6 | 0.818 | 2.138 |  |  | 2.138 | 0 | 1.05 | -1.088 | -1.088 | closed
100 | SS 35/10 Selifontovo | 2,5+2,5 | 2.5 | 2.5 | 1.45 | 0.91 | 0.54 | 0.953 | 120 | 0.497 | 0 | 2.63 | 2.133 | 2.133 | open | 100 | SS 35/10 Selifontovo | 2,5+2,5 | 1.672 | 3.122 | 0.953 | 120 | 2.169 | 0 | 2.63 | 0.461 | 0.461 | open
101 | SS 35/10 Semibratovo | 4,0+4,0 | 4 | 4 | 0.62 | 0.43 | 0.19 | 0.052 | 120 | 0.568 | 0 | 4.2 | 3.632 | 3.632 | open | 101 | SS 35/10 Semibratovo | 4,0+4,0 | 0.25 | 0.87 | 0.052 | 120 | 0.818 | 0 | 4.2 | 3.382 | 3.382 | open
102 | SS 35/10 Skomorokhovo | 1,6+1,6 | 1.6 | 1.6 | 1.1 | 0.04 | 1.06 |  |  | 1.1 | 0 | 1.68 | 0.58 | 0.58 | open | 102 | SS 35/10 Skomorokhovo | 1,6+1,6 | 1.0891 | 2.1891 |  |  | 2.1891 | 0 | 1.68 | -0.5091 | -0.5091 | closed
103 | SS 35/10 Solomidino | 2.5 | 2.5 |  | 1.2 | 1.2 |  | 0.866 | 1 day and night | 1.2 | 0 | 0.866 | -0.334 | -0.334 | closed | 103 | SS 35/10 Solomidino | 2.5 | 1.102 | 2.302 | 0.866 | 1 day and night | 2.302 | 0 | 0.866 | -1.436 | -1.436 | closed
104 | SS 35/10 Stavotino | 4,0+4,0 | 4 | 4 | 1.47 | 0.54 | 0.93 | 0.346 | 120 | 1.124 | 0 | 4.2 | 3.076 | 3.076 | open | 104 | SS 35/10 Stavotino | 4,0+4,0 | 0.97 | 2.44 | 0.346 | 120 | 2.094 | 0 | 4.2 | 2.106 | 2.106 | open
105 | SS 35/10 Urusovo | 2,5+2,5 | 2.5 | 2.5 | 0.4 | 0.31 | 0.09 | 0.052 | 120 | 0.348 | 0 | 2.63 | 2.282 | 2.282 | open | 105 | SS 35/10 Urusovo | 2,5+2,5 | 0.049 | 0.449 | 0.052 | 120 | 0.397 | 0 | 2.63 | 2.233 | 2.233 | open
106 | SS 35/10 Filimonovo | 2,5+2,5 | 2.5 | 2.5 | 0.85 | 0.13 | 0.72 |  |  | 0.85 | 0 | 2.63 | 1.78 | 1.78 | open | 106 | SS 35/10 Filimonovo | 2,5+2,5 | 0.937 | 1.787 |  |  | 1.787 | 0 | 2.63 | 0.843 | 0.843 | open
107 | SS 35/10 Choporovo | 2,5+2,5 | 2.5 | 2.5 | 0.38 | 0.19 | 0.19 |  |  | 0.38 | 0 | 2.63 | 2.25 | 2.25 | open | 107 | SS 35/10 Choporovo | 2,5+2,5 | 0.236 | 0.616 |  |  | 0.616 | 0 | 2.63 | 2.014 | 2.014 | open
108 | SS 35/10 Shchurovo | 2,5+2,5 | 2.5 | 2.5 | 1.11 | 0.57 | 0.54 | 0.242 | 120 | 0.868 | 0 | 2.63 | 1.762 | 1.762 | open | 108 | SS 35/10 Shchurovo | 2,5+2,5 | 0.087 | 1.197 | 0.242 | 120 | 0.955 | 0 | 2.63 | 1.675 | 1.675 | open
109 | SS 35/10 Neksans | 10+10 | 10 | 10 | 1.93 | 0.85 | 1.08 |  |  | 1.93 | 0 | 10.5 | 8.57 | 8.57 | open | 109 | SS 35/10 Neksans | 10+10 | 3.5 | 5.43 |  |  | 5.43 | 0 | 10.5 | 5.07 | 5.07 | open
110 | SS 35/6 Pribrezhnaya | 10+10 | 10 | 10 | 10.7 | 6.51 | 4.19 |  |  | 10.7 | 0 | 10.5 | -0.2 | -0.2 | closed | 110 | SS 35/6 Pribrezhnaya | 10+10 | 0.3125 | 11.0125 |  |  | 11.0125 | 0 | 10.5 | -0.5125 | -0.5125 | closed
111 | SS 110/10 Tishino | 25+25 | 25 | 25 | 18.25 | 11.44 | 6.81 |  |  | 18.25 | 0 | 26.25 | 8 | 8 | open | 111 | SS 110/10 Tishino | 25+25 | 0.173 | 18.423 |  |  | 18.423 | 0 | 26.25 | 7.827 | 7.827 | open
112 | SS 110/10 Product pipeline | 6,3+6,3 | 6.3 | 6.3 | 1.2 | 0.93 | 0.27 |  |  | 1.2 | 0 | 6.62 | 5.42 | 5.42 | open | 112 | SS 110/10 Product pipeline | 6,3+6,3 | 0 | 1.2 |  |  | 1.2 | 0 | 6.62 | 5.42 | 5.42 | open
113 | SS 110/10 Nekouz | 6,3+6,3 | 6.3 | 6.3 | 2.36 | 0.94 | 1.42 | 0.069 | 120 | 2.291 | 0 | 6.62 | 4.329 | 4.329 | open | 113 | SS 110/10 Nekouz | 6,3+6,3 | 0.027 | 2.387 | 0.069 | 120 | 2.318 | 0 | 6.62 | 4.302 | 4.302 | open
114 | SS 110/6 Yuzhnaya | 25+25 | 25 | 25 | 20.03 | 10.89 | 9.14 |  |  | 20.03 | 0 | 26.25 | 6.22 | 6.22 | open | 114 | SS 110/6 Yuzhnaya | 25+25 | 0.1094 | 20.1394 |  |  | 20.1394 | 0 | 26.25 | 6.1106 | 6.1106 | open
115 | SS 110/10 Optika | 10+10 | 10 | 10 | 5.39 | 3.49 | 1.9 | 0.26 | 120 | 5.13 | 0 | 10.5 | 5.37 | 5.37 | open | 115 | SS 110/10 Optika | 10+10 | 0.348 | 5.738 | 0.26 | 120 | 5.478 | 0 | 10.5 | 5.022 | 5.022 | open
116 | SS 110/6 Poligrafmash | 16+16 | 16 | 16 | 7.76 | 3.14 | 4.62 |  |  | 7.76 | 0 | 16.8 | 9.04 | 9.04 | open | 116 | SS 110/6 Poligrafmash | 16+16 | 0.06 | 7.82 |  |  | 7.82 | 0 | 16.8 | 8.98 | 8.98 | open
117 | SS 110/6/6 Zapadnaya | 63+63 | 63 | 63 | 27.9 | 14.65 | 13.25 |  |  | 27.9 | 0 | 66.15 | 38.25 | 38.25 | open | 117 | SS 110/6/6 Zapadnaya | 63+63 | 1.2415 | 29.1415 |  |  | 29.1415 | 0 | 66.15 | 37.0085 | 37.0085 | open
118 | SS 110/35/6 Volzhskaya | 40+40 | 40 | 40 | 10.75 |  |  |  |  | 10.75 | 0 | 42 | 31.25 | 31.25 | open | 118 | SS 110/35/6 Volzhskaya | 40+40 |  | 10.925 |  |  | 10.925 | 0 | 42 | 31.075 | 31.075 | open
| Nom. capacity MV, МVА | 40+40 |  |  | MVA 4: 0; MVA Т-1: 0; MVA Т-2: 0 |  | Nom. capacity MV, МVА | 40+40
| Nom. capacity LV, МVА | 40+40 |  |  | 10.75 | 0 | 10.75 |  |  | 10.75 | 0 | 42 | 31.25 |  |  |  | Nom. capacity LV, МVА | 40+40 | 0.175 | 10.925 |  |  | 10.925 | 0 | 42 | 31.075
119 | SS 110/35/6 Levoberezhnaya | 16+16 | 16 | 16 | 14.06 |  |  |  |  | 14.06 | 0 | 16.8 | 2.74 | 2.74 | open | 119 | SS 110/35/6 Levoberezhnaya | 16+16 |  | 15.2385 |  |  | 15.2385 | 0 | 16.8 | 1.5615 | 1.5615 | open
| Nom. capacity MV, МVА | 16+16 |  |  | 9.1 | 2.68 | 6.42 |  |  | 9.1 | 0 | 16.8 | 7.7 |  |  |  | Nom. capacity MV, МVА | 16+16 |  | 10.2475 |  |  | 10.2475 | 0 | 16.8 | 6.5525
| Nom. capacity LV, МVА | 16+16 |  |  | 4.96 | 3.25 | 1.71 |  |  | 4.96 | 0 | 16.8 | 11.84 |  |  |  | Nom. capacity LV, МVА | 16+16 | 0.031 | 4.991 |  |  | 4.991 | 0 | 16.8 | 11.809
120 | SS 110/35/10 Pishchalkino | 7,5+7,5 | 7.5 | 7.5 | 1.96 |  |  |  |  | 1.96 | 0 | 7.88 | 5.92 | 5.92 | open | 120 | SS 110/35/10 Pishchalkino | 7,5+7,5 |  | 1.96 |  |  | 1.96 | 0 | 7.88 | 5.92 | 5.92 | open
| Nom. capacity MV, МVА | 7,5+7,5 |  |  | 1.18 | 1.18 | 0 |  |  | 1.18 | 0 | 7.88 | 6.7 |  |  |  | Nom. capacity MV, МVА | 7,5+7,5 |  | 1.18 |  |  | 1.18 | 0 | 7.88 | 6.7
| Nom. capacity LV, МVА | 7,5+7,5 |  |  | 0.78 | 0.65 | 0.13 |  |  | 0.78 | 0 | 7.88 | 7.1 |  |  |  | Nom. capacity LV, МVА | 7,5+7,5 | 0 | 0.78 |  |  | 0.78 | 0 | 7.88 | 7.1
121 | SS 110/6 Dock yard | 10+10 | 10 | 10 | 5.32 | 3.71 | 1.61 |  |  | 5.32 | 0 | 10.5 | 5.18 | 5.18 | open | 121 | SS 110/6 Dock yard | 10+10 | 0.154 | 5.474 |  |  | 5.474 | 0 | 10.5 | 5.026 | 5.026 | open
122 | SS 110/6 Selekhovo | 6,3+6,3 | 6.3 | 6.3 | 3.42 | 1.14 | 2.28 |  |  | 3.42 | 0 | 6.62 | 3.2 | 3.2 | open | 122 | SS 110/6 Selekhovo | 6,3+6,3 | 0.61 | 4.03 |  |  | 4.03 | 0 | 6.62 | 2.59 | 2.59 | open
123 | SS 35/6 Kamenniki | 4,0+4,0 | 4 | 4 | 2.3 | 1.19 | 1.11 |  |  | 2.3 | 0 | 4.2 | 1.9 | 1.9 | open | 123 | SS 35/6 Kamenniki | 4,0+4,0 | 0.149 | 2.449 |  |  | 2.449 | 0 | 4.2 | 1.751 | 1.751 | open
124 | SS 35/10 Shashkovo | 1,6+1,6 | 1.6 | 1.6 | 0.68 | 0.52 | 0.16 |  |  | 0.68 | 0 | 1.68 | 1 | 1 | open | 124 | SS 35/10 Shashkovo | 1,6+1,6 | 0.293 | 0.973 |  |  | 0.973 | 0 | 1.68 | 0.707 | 0.707 | open
125 | SS 110/6 Veretye | 25+25 | 25 | 25 | 21.36 | 10.73 | 10.63 |  |  | 21.36 | 0 | 26.25 | 4.89 | 4.89 | open | 125 | SS 110/6 Veretye | 25+25 | 0.997 | 22.357 |  |  | 22.357 | 0 | 26.25 | 3.893 | 3.893 | open
126 | SS 35/10 Nikolo-Korma | 4,0+4,0 | 4 | 4 | 2.8 | 1.8 | 1 | 0.554 | 120 | 2.246 | 0 | 4.2 | 1.954 | 1.954 | open | 126 | SS 35/10 Nikolo-Korma | 4,0+4,0 | 1.3198 | 4.1198 | 0.554 | 120 | 3.5658 | 0 | 4.2 | 0.6342 | 0.6342 | open
127 | SS 35/10 Arefino | 2,5+2,5 | 2.5 | 2.5 | 1.2 | 0.64 | 0.56 | 0.017 | 120 | 1.183 | 0 | 2.63 | 1.447 | 1.447 | open | 127 | SS 35/10 Arefino | 2,5+2,5 | 0.021 | 1.221 | 0.017 | 120 | 1.204 | 0 | 2.63 | 1.426 | 1.426 | open
128 | SS 35/10 Knyazevo | 1,6+2,5 | 1.6 | 2.5 | 0.82 | 0.1 | 0.72 |  |  | 0.82 | 0 | 1.68 | 0.86 | 0.86 | open | 128 | SS 35/10 Knyazevo | 1,6+2,5 | 0.096 | 0.916 |  |  | 0.916 | 0 | 1.68 | 0.764 | 0.764 | open
129 | SS 35/10 Pokrov | 1,6+1,6 | 1.6 | 1.6 | 0.59 | 0.34 | 0.25 | 0.294 | 120 | 0.296 | 0 | 1.68 | 1.384 | 1.384 | open | 129 | SS 35/10 Pokrov | 1,6+1,6 | 0.003 | 0.593 | 0.294 | 120 | 0.299 | 0 | 1.68 | 1.381 | 1.381 | open
130 | SS 35/10 Anikovo | 2,5+2,5 | 2.5 | 2.5 | 0.83 | 0.64 | 0.19 | 0.017 | 120 | 0.813 | 0 | 2.63 | 1.817 | 1.817 | open | 130 | SS 35/10 Anikovo | 2,5+2,5 | 0.035 | 0.865 | 0.017 | 120 | 0.848 | 0 | 2.63 | 1.782 | 1.782 | open
131 | SS 35/10 Novoe selo | 2,5+2,5 | 2.5 | 2.5 | 1.31 | 0.63 | 0.68 |  |  | 1.31 | 0 | 2.63 | 1.32 | 1.32 | open | 131 | SS 35/10 Novoe selo | 2,5+2,5 | 0.553 | 1.863 |  |  | 1.863 | 0 | 2.63 | 0.767 | 0.767 | open
132 | SS 35/10 Bolshoe selo | 6,3+6,3 | 6.3 | 6.3 | 4.31 | 2.38 | 1.93 |  |  | 4.31 | 0 | 6.62 | 2.31 | 2.31 | open | 132 | SS 35/10 Bolshoe selo | 6,3+6,3 | 0.7863 | 5.0963 |  |  | 5.0963 | 0 | 6.62 | 1.5237 | 1.5237 | open
133 | SS 35/10 Breytovo | 6,3+4,0 | 6.3 | 4 | 4.6 | 2.55 | 2.05 |  |  | 4.6 | 0 | 4.2 | -0.4 | -0.4 | closed | 133 | SS 35/10 Breytovo | 6,3+4,0 | 1.325 | 5.925 |  |  | 5.925 | 0 | 4.2 | -1.725 | -1.725 | closed
134 | SS 35/10 Stanilovo | 1,6+1,6 | 1.6 | 1.6 | 1.06 | 0.35 | 0.71 | 0.208 | 120 | 0.852 | 0 | 1.68 | 0.828 | 0.828 | open | 134 | SS 35/10 Stanilovo | 1,6+1,6 | 0.015 | 1.075 | 0.208 | 120 | 0.867 | 0 | 1.68 | 0.813 | 0.813 | open
135 | SS 35/10 Znamovo | 2,5+2,5 | 2.5 | 2.5 | 0.91 | 0.3 | 0.61 | 0.173 | 120 | 0.737 | 0 | 2.63 | 1.893 | 1.893 | open | 135 | SS 35/10 Znamovo | 2,5+2,5 | 0.01 | 0.92 | 0.173 | 120 | 0.747 | 0 | 2.63 | 1.883 | 1.883 | open
136 | SS 35/10 Rozhdestvenno | 2,5+2,5 | 2.5 | 2.5 | 0.96 | 0.47 | 0.49 |  |  | 0.96 | 0 | 2.63 | 1.67 | 1.67 | open | 136 | SS 35/10 Rozhdestvenno | 2,5+2,5 | 0.062 | 1.022 |  |  | 1.022 | 0 | 2.63 | 1.608 | 1.608 | open
137 | SS 35/10 Zapolye | 2,5+2,5 | 2.5 | 2.5 | 0.54 | 0.23 | 0.31 |  |  | 0.54 | 0 | 2.63 | 2.09 | 2.09 | open | 137 | SS 35/10 Zapolye | 2,5+2,5 | 0.16 | 0.7 |  |  | 0.7 | 0 | 2.63 | 1.93 | 1.93 | open
138 | SS 35/10 Tikhmenevo | 1,6+1,6 | 1.6 | 1.6 | 1.4 | 0.68 | 0.72 | 0.364 | 120 | 1.036 | 0 | 1.68 | 0.644 | 0.644 | open | 138 | SS 35/10 Tikhmenevo | 1,6+1,6 | 0.127 | 1.527 | 0.364 | 120 | 1.163 | 0 | 1.68 | 0.517 | 0.517 | open
139 | SS 35/10 Latskoe | 1,6+2,5 | 1.6 | 2.5 | 0.22 | 0.13 | 0.09 | 0.017 | 120 | 0.203 | 0 | 1.68 | 1.477 | 1.477 | open | 139 | SS 35/10 Latskoe | 1,6+2,5 | 0.01 | 0.23 | 0.017 | 120 | 0.213 | 0 | 1.68 | 1.467 | 1.467 | open
140 | SS 35/10 Borok | 2,5+4,0 | 2.5 | 4 | 1.56 | 1.15 | 0.41 | 0.277 | 120 | 1.283 | 0 | 2.63 | 1.347 | 1.347 | open | 140 | SS 35/10 Borok | 2,5+4,0 | 0.212 | 1.772 | 0.277 | 120 | 1.495 | 0 | 2.63 | 1.135 | 1.135 | open
141 | SS 35/10 Myshkin | 6,3+6,3 | 6.3 | 6.3 | 3.76 | 2.47 | 1.29 |  |  | 3.76 | 0 | 6.62 | 2.86 | 2.86 | open | 141 | SS 35/10 Myshkin | 6,3+6,3 | 0.6 | 4.36 |  |  | 4.36 | 0 | 6.62 | 2.26 | 2.26 | open
142 | SS 110/10 Volga | 5,6+6,3 | 5.6 | 6.3 | 2.13 | 0.73 | 1.4 |  |  | 2.13 | 0 | 5.88 | 3.75 | 3.75 | open | 142 | SS 110/10 Volga | 5,6+6,3 | 0 | 2.13 |  |  | 2.13 | 0 | 5.88 | 3.75 | 3.75 | open
143 | SS 35/10 Krasnaya Gorka | 4,0+2,5 | 4 | 2.5 | 2.09 | 1.14 | 0.95 | 0.104 | 120 | 1.986 | 0 | 2.63 | 0.644 | 0.644 | open | 143 | SS 35/10 Krasnaya Gorka | 4,0+2,5 | 0.411 | 2.501 | 0.104 | 120 | 2.397 | 0 | 2.63 | 0.233 | 0.233 | open
144 | SS 110/35/6 Vostochnaya | 25+25 | 25 | 25 | 20.08 |  |  |  |  | 20.08 | 0 | 26.25 | 6.17 | 6.17 | open | 144 | SS 110/35/6 Vostochnaya | 25+25 |  | 21.4093 |  |  | 21.4093 | 0 | 26.25 | 4.8407 | 4.8407 | open
| Nom. capacity MV, МVА | 25+25 |  |  | 3.67 | 3.67 | 0 |  |  | 3.67 | 0 | 26.25 | 22.58 |  |  |  | Nom. capacity MV, МVА | 25+25 |  | 4.9009 |  |  | 4.9009 | 0 | 26.25 | 21.3491
| Nom. capacity LV, МVА | 25+25 |  |  | 16.41 | 8.03 | 8.38 |  |  | 16.41 | 0 | 26.25 | 9.84 |  |  |  | Nom. capacity LV, МVА | 25+25 | 0.09842 | 16.5084 |  |  | 16.5084 | 0 | 26.25 | 9.7416
145 | SS 110/35/10 Zalesye | 10+10 | 10 | 10 | 8.03 |  |  | 1.212 | 120 | 6.818 | 0 | 10.5 | 3.682 | 3.682 | open | 145 | SS 110/35/10 Zalesye | 10+10 |  | 8.118 | 1.212 | 120 | 6.906 | 0 | 10.5 | 3.594 | 3.594 | open
| Nom. capacity MV, МVА | 10+10 |  |  | 0.78 | 0.44 | 0.34 |  |  | 0.78 | 0 | 10.5 | 9.72 |  |  |  | Nom. capacity MV, МVА | 10+10 |  | 0.79 |  |  | 0.79 | 0 | 10.5 | 9.71
| Nom. capacity LV, МVА | 10+10 |  |  | 7.25 | 4.57 | 2.68 | 1.212 | 120 | 6.038 | 0 | 10.5 | 4.462 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.078 | 7.328 | 1.212 | 120 | 6.116 | 0 | 10.5 | 4.384
146 | SS 110/10 Lugovaya | 6,3+6,3 | 6.3 | 6.3 | 2.85 | 1.18 | 1.67 |  |  | 2.85 | 0 | 6.62 | 3.77 | 3.77 | open | 146 | SS 110/10 Lugovaya | 6,3+6,3 | 0.331 | 3.181 |  |  | 3.181 | 0 | 6.62 | 3.439 | 3.439 | open
147 | SS 110/35/10 Lom | 10+10 | 10 | 10 | 7.55 |  |  | 1.368 | 120 | 6.182 | 0 | 10.5 | 4.318 | 4.318 | open | 147 | SS 110/35/10 Lom | 10+10 |  | 9.3959 | 1.368 | 120 | 8.0279 | 0 | 10.5 | 2.4721 | 2.4721 | open
| Nom. capacity MV, МVА | 10+10 |  |  | 6.07 | 4.03 | 2.04 |  |  | 6.07 | 0 | 10.5 | 4.43 |  |  |  | Nom. capacity MV, МVА | 10+10 |  | 7.5293 |  |  | 7.5293 | 0 | 10.5 | 2.9707
| Nom. capacity LV, МVА | 10+10 |  |  | 1.48 | 1.08 | 0.4 | 1.368 | 120 | 0.112 | 0 | 10.5 | 10.388 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.3866 | 1.8666 | 1.368 | 120 | 0.4986 | 0 | 10.5 | 10.0014
148 | SS 35/10 Varegovo | 1,6+2,5 | 1.6 | 2.5 | 0.8 | 0.52 | 0.28 |  |  | 0.8 | 0 | 1.68 | 0.88 | 0.88 | open | 148 | SS 35/10 Varegovo | 1,6+2,5 | 0.12 | 0.92 |  |  | 0.92 | 0 | 1.68 | 0.76 | 0.76 | open
149 | SS 110/35/10 Shestikhino | 10+10 | 10 | 10 | 7.78 |  |  | 0.242 | 120 | 7.538 | 0 | 10.5 | 2.962 | 2.962 | open | 149 | SS 110/35/10 Shestikhino | 10+10 |  | 9.648 | 0.242 | 120 | 9.406 | 0 | 10.5 | 1.094 | 1.094 | open
| Nom. capacity MV, МVА | 10+10 |  |  | 7.16 | 2.2 | 4.96 |  |  | 7.16 | 0 | 10.5 | 3.34 |  |  |  | Nom. capacity MV, МVА | 10+10 |  | 8.834 |  |  | 8.834 | 0 | 10.5 | 1.666
| Nom. capacity LV, МVА | 10+10 |  |  | 0.62 | 0.27 | 0.35 | 0.242 | 120 | 0.378 | 0 | 10.5 | 10.122 |  |  |  | Nom. capacity LV, МVА | 10+10 | 0.194 | 0.814 | 0.242 | 120 | 0.572 | 0 | 10.5 | 9.928
150 | SS 110/35/10 Kryukovo | 6.3 | 6.3 |  | MVA 4: 3.21; Min 11: 1.432; Min 12: open | 150 | SS 110/35/10 Kryukovo | 6.3 |  | 3.51 |  |  |  | 0 |  |  | 1.432 | open
| Nom. capacidty MV, МVА | 6.3 |  |  | MVA 4: 2.91; MVA Т-1: 2.91 |  | Nom. capacidty MV, МVА | 6.3 |  | 3.21 |  |  |  | 0
| Nom. capacity LV, МVА | 6.3 |  |  | 0.3 | 0.3 |  | 1.732 | 1 day and night | 0.3 | 0 | 1.732 | 1.432 |  |  |  | Nom. capacity LV, МVА | 6.3 | 0 | 0.3 | 1.732 | 1 day and night | 0.3 | 0 | 1.732 | 1.432
151 | SS 35/10 Beloe | 2.5 | 2.5 |  | 0.71 | 0.71 |  | 1.472 | 1 day and night | 0.71 | 0 | 1.472 | 0.762 | 0.762 | open | 151 | SS 35/10 Beloe | 2.5 | 0.059 | 0.769 | 1.472 | 1 day and night | 0.769 | 0 | 1.472 | 0.703 | 0.703 | open
152 | SS 110/35/10 Glebovo | 10 | 10 |  | MVA 4: 6.05; Min 11: -2.505; Min 12: closed | 152 | SS 110/35/10 Glebovo | 10 |  | 8.3799 |  |  |  | 0 |  |  | -4.048 | closed
| Nom. capacity MV, МVА | 10 |  |  | MVA 4: 2.87; MVA Т-1: 2.87 |  | Nom. capacity MV, МVА | 10 |  | 3.6569 |  |  |  | 0
| Nom. capacity LV, МVА | 10 |  |  | 3.18 | 3.18 |  | 0.675 | 1 day and night | 3.18 | 0 | 0.675 | -2.505 |  |  |  | Nom. capacity LV, МVА | 10 | 1.543 | 4.723 | 0.675 | 1 day and night | 4.723 | 0 | 0.675 | -4.048
153 | SS 35/6 Pesochnoye | 1,8+1,8 | 1.8 | 1.8 | 1.59 | 0.79 | 0.8 |  |  | 1.59 | 0 | 1.89 | 0.3 | 0.3 | open | 153 | SS 35/6 Pesochnoye | 1,8+1,8 | 0 | 1.59 |  |  | 1.59 |  | 1.89 | 0.3 | 0.3 | open
154 | SS 35/10 Demino | 2,5+2,5 | 2.5 | 2.5 | 0.72 | 0.18 | 0.54 | 0.052 |  | 0.668 | 0 | 2.63 | 1.962 | 1.962 | open | 154 | SS 35/10 Demino | 2,5+2,5 | 0 | 0.72 | 0.052 |  | 0.668 |  | 2.63 | 1.962 | 1.962 | open
155 | SS 110/6 KS-18 | 63+63 | 63 | 63 | 23.71 | 8.29 | 15.42 |  |  | 23.71 | 0 | 66.15 | 42.44 | 42.44 | open | 155 | SS 110/6 KS-18 | 63+63 | 0 | 23.71 |  |  | 23.71 | 0 | 66.15 | 42.44 | 42.44 | open
156 | SS 35/6 Makeikha | 1.6 | 1.6 |  | 0.31 | 0.31 |  | 1.68 | 1 day and night | 0.31 | 0 | 1.68 | 1.37 | 1.37 | open | 156 | SS 35/6 Makeikha | 1.6 | 0 | 0.31 | 1.68 | 1 day and night | 0.31 |  | 1.68 | 1.37 | 1.37 | open
157 | SS 35/10 Ermakovo | 1.6 | 1.6 |  | 1.02 | 1.02 |  | 1.212 | 1 day and night | 1.02 | 0 | 1.212 | 0.192 | 0.192 | open | 157 | SS 35/10 Ermakovo | 1.6 | 0.123 | 1.143 | 1.212 | 1 day and night | 1.143 | 0 | 1.212 | 0.069 | 0.069 | open
158 | SS 35/10 Milyushino | 1.6 | 1.6 |  | 0.84 | 0.84 |  | 0.918 | 1 day and night | 0.84 | 0 | 0.918 | 0.078 | 0.078 | open | 158 | SS 35/10 Milyushino | 1.6 | 0.677 | 1.517 | 0.918 | 1 day and night | 1.517 | 0 | 0.918 | -0.599 | -0.599 | closed
159 | SS 35/10 Sutka | 2.5 | 2.5 |  | 0.74 | 0.74 |  | 0.554 | 1 day and night | 0.74 | 0 | 0.554 | -0.186 | -0.186 | closed | 159 | SS 35/10 Sutka | 2.5 | 0.039 | 0.779 | 0.554 | 1 day and night | 0.779 | 0 | 0.554 | -0.225 | -0.225 | closed
160 | SS 35/10 Sit | 1.6 | 1.6 |  | 0.67 | 0.67 |  | 0.68 | 1 day and night | 0.67 | 0 | 0.68 | 0.01 | 0.01 | open | 160 | SS 35/10 Sit | 1.6 | 0.241 | 0.911 | 0.68 | 1 day and night | 0.911 | 0 | 0.68 | -0.231 | -0.231 | closed
161 | SS 35/10 Gorelovo | 1.6 | 1.6 |  | 1.2 | 1.2 |  | 0.901 | 1 day and night | 1.2 | 0 | 0.901 | -0.299 | -0.299 | closed | 161 | SS 35/10 Gorelovo | 1.6 | 0.461 | 1.661 | 0.901 | 1 day and night | 1.661 | 0 | 0.901 | -0.76 | -0.76 | closed
162 | SS 35/6 Pishchalkino | 1.6 | 1.6 |  | 0.74 | 0.74 |  | 1.68 | 1 day and night | 0.74 | 0 | 1.68 | 0.94 | 0.94 | open | 162 | SS 35/6 Pishchalkino | 1.6 | 0 | 0.74 | 1.68 | 1 day and night | 0.74 | 0 | 1.68 | 0.94 | 0.94 | open
163 | SS 35/6 Varegovo | 1.6 | 1.6 |  | 0.02 | 0.02 |  | 1.68 | 1 day and night | 0.02 | 0 | 1.68 | 1.66 | 1.66 | open | 163 | SS 35/6 Varegovo | 1.6 | 0 | 0.02 | 1.68 | 1 day and night | 0.02 | 0 | 1.68 | 1.66 | 1.66 | open
164 | SS 35/10 Levoberezhnaya | 4 | 4 |  | 1.31 | 1.31 |  | 1.334 | 1 day and night | 1.31 | 0 | 1.334 | 0.024 | 0.024 | open | 164 | SS 35/10 Levoberezhnaya | 4 | 0.4716 | 1.7816 | 1.334 | 1 day and night | 1.7816 |  | 1.334 | -0.4476 | -0.4476 | closed
| Total: | 2858.7 | 1456.3 | 1402.4 | MVA 4: 885.648 |  | Total: | 2857.9 |  | 1019.9998
| deficit |  |  |  | Min 11: -15.784 |  | deficit | [9 empty] | -93.702
| proficit |  |  |  | Min 11: 650.045 |  | proficit | [9 empty] | 539.685
|  | -0.55214 | [15 empty] | -3.2787
|  | 22.7392 | [15 empty] | 18.884
Deputy director for technical policy
[17 empty] | Chief engineer | [8 empty] | E.V. Turapin
Note on G216: Т3
Note on G214: Т3
Note on G194: Т2
Note on H194: Т3